Building Code Act, 1992
Loi de 1992 sur le code du bâtiment

ontario REGULATION 403/97

Amended to O. Reg. 422/06

Building code

Note:  This Regulation was revoked on December 31, 2006.  See:  O. Reg. 350/06, Division C, Part 4, ss. 4.2, 4.3.

This Regulation is made in English only.

Part 1
Scope and Definitions

| Section | 1.1. | General |
| --- | --- | --- |
|  | 1.1.1. | Administration |
|  | 1.1.2. | Scope |
|  | 1.1.3. | Definitions of Words and Phrases |
|  | 1.1.4. | Abbreviations |

Part 1
Scope and Definitions

Section 1.1. General

1.1.1. Administration

1.1.1.1.  Conformance with Administrative Requirements

(1)  This Code shall be administered in conformance with the Building Code Act, 1992.

1.1.2. Scope

1.1.2.1.  Application

(1)  Reserved

1.1.3. Definitions of Words and Phrases

1.1.3.1.  Non-defined Terms

(1)  Definitions of words and phrases used in this Code that are not included in the list of definitions in this Part shall have the meanings which are commonly assigned to them in the context in which they are used in this Code, taking into account the specialized use of terms with the various trades and professions to which the terminology applies.

1.1.3.2.  Defined Terms

(1)  The words and terms in italics in this Code have the following meaning for the purposes of this Code, and where indicated, the following meaning for the purposes of the Act as well.

Absorption trench means an excavation in soil (as defined in Part 8) or leaching bed fill, being part of a leaching bed, in which a distribution pipe is laid and which allows infiltration of the effluent into the soil (as defined in Part 8) or leaching bed fill.

Accessible means when applied to a fixture, connection, plumbing appliance, valve, cleanout or equipment, having access thereto but which first may require the removal of an access panel, door or similar obstruction without the cutting or breaking of materials.

Access to exit means that part of a means of egress within a floor area that provides access to an exit serving the floor area.

Adfreezing means the adhesion of soil to a foundation unit resulting from the freezing of soil water.

Air barrier system means the assembly installed to provide a continuous barrier to the movement of air.

Air break means the unobstructed vertical distance between the lowest point of an indirectly connected waste pipe and the flood level rim of the fixture into which it discharges.

Air-conditioning is the process of treating air to control simultaneously its temperature, humidity, cleanliness, and distribution to meet the comfort requirements of the occupants of the conditioned space.

Air gap means the unobstructed vertical distance through air between the lowest point of a water supply outlet and the flood level rim of the fixture or device into which the outlet discharges.

Air-supported structure means a structure consisting of a pliable membrane which achieves and maintains its shape and support by internal air pressure.

Alarm signal means an audible signal transmitted throughout a zone or zones or throughout a building to advise occupants that a fire emergency exists.

Alert signal means an audible signal to advise designated persons of a fire emergency.

Allowable bearing pressure means the maximum pressure that may be safely applied to a soil or rock by the foundation unit considered in design under expected loading and subsurface conditions.

Allowable load means the maximum load that may be safely applied to a foundation unit considered in design under expected loading and subsurface conditions.

Alternative measure means a substitute for a requirement of Part 3, 4, 5, 6, 7, 8 or 9 of the Code or for a compliance alternative.

Appliance means a device to convert fuel into energy and includes all components, controls, wiring and piping required to be part of the device by the applicable standard referred to in this Code.

Architect means, for the purposes of the Act and this Code, the holder of a licence, a certificate of practice or a temporary licence under the Architects Act.

Artesian groundwater means a confined body of water under pressure in the ground.

As constructed plans means, for the purposes of the Act and this Code, construction plans and specifications that show the building and the location of the building on the property as the building has been constructed.

Assembly occupancy means the occupancy or the use of a building, or part thereof, by a gathering of persons for civic, political, travel, religious social, educational, recreational or like purposes, or for the consumption of food or drink.

Attic or roof space means the space between the roof and the ceiling of the top storey or between a dwarf wall and a sloping roof.

Backflow means a flowing back or reversal of the normal direction of the flow.

Backflow preventer means a device or a method that prevents backflow in a water distribution system.

Back-siphonage means backflow caused by a negative pressure in the supply system.

Back-siphonage preventer means a device or a method that prevents back-siphonage in a water distribution system.

Back vent means a pipe that is installed to vent a trap off the horizontal section of a fixture drain or the vertical leg of a water closet or other fixture that has an integral siphonic flushing action and “back vented” has a corresponding meaning.

Backwater valve means a check valve designed for use in a gravity drainage system.

Barrier-free means that a building and its facilities can be approached, entered, and used by persons with physical or sensory disabilities.

Basement means a storey or storeys of a building located below the first storey.

Bearing surface means the contact surface between a foundation unit and the soil or rock upon which it bears.

Boarding, lodging or rooming house means a building where,

(a)	building height does not exceed 3 storeys and building area does not exceed 600 m2 ,

(b)	lodging is provided for more than 4 persons in return for remuneration or for the provision of services or for both, and

(c)	lodging rooms do not have both bathrooms and kitchen facilities for the exclusive use of individual occupants.

Boiler means an appliance intended to supply hot water or steam for space heating, processing or power purposes.

Bottle trap means a trap that retains water in a closed chamber and that seals the water by submerging the inlet pipe in the liquids or by a partition submerged in the liquids.

Branch means a soil or waste pipe connected at its upstream end to the junction of 2 or more soil or waste pipes or to a soil or waste stack, and connected at its downstream end to another branch, a sump, a soil or waste stack or a building drain.

Branch vent means a vent pipe that is connected at its lower end to the junction of 2 or more vent pipes and is connected at its upper end either to a stack vent, vent stack or header, or is terminated in open air.

Breeching means a flue pipe or chamber for receiving flue gases from 1 or more flue connections and for discharging these gases through a single flue connection.

Building area means the greatest horizontal area of a building above grade within the outside surface of exterior walls or within the outside surface of exterior walls and the centre line of firewalls.

Building Code website means the website at www.obc.mah.gov.on.ca.

Building control valve means the valve on a water system that controls the flow of potable water from the water service pipe to the water distribution system.

Building drain means sanitary building drain or storm building drain.

Building height means the number of storeys contained between the roof and the floor of the first storey.

Building sewer means sanitary building sewer or storm building sewer.

Building trap means a trap that is installed in a sanitary building drain or sanitary building sewer to prevent circulation of air between a sanitary drainage system and a public sewer.

Business and personal services occupancy means the occupancy or use of a building or part thereof for the transaction of business or the rendering or receiving of professional or personal services.

Camp for housing of workers means a camp in which buildings or other structures or premises are used to accommodate 5 or more employees.

Campground means land or premises used as an overnight camping facility other than a recreational camp.

Canopy means a roof-like structure projecting more than 300 mm from the exterior face of the building.

Care and treatment occupancy (Group B, Division 2) means an occupancy in which persons receive special care and treatment.

Care occupancy (Group B, Division 3) means an occupancy in which persons receive special or supervisory care because of cognitive or physical limitations, but does not include a dwelling unit.

Care or detention occupancy means the occupancy or use of a building or part thereof by persons who,

(a)	are dependent on others to release security devices to permit egress,

(b)	receive special care and treatment, or

(c)	receive supervisory care.

Cavity wall means a construction of masonry units laid with a cavity between the wythes.  The wythes are tied together with metal ties or bonding units and are relied on to act together in resisting lateral loads.

Certificate for the occupancy of a building not fully completed means a certificate described in Sentence 2.22.5.3.(5).

Chamber means a structure that is constructed with an open bottom and contains a pressurized distribution pipe.

Check valve means a valve that permits flow in one direction but prevents a return flow.

Chimney means a primarily vertical shaft enclosing at least 1 flue for conducting flue gases to the outdoors.

Chimney liner means a conduit containing a chimney flue used as a lining of a masonry or concrete chimney.

Circuit vent means a vent pipe that functions for two or more traps connecting to a horizontal branch where the lower end of the vent pipe connects to the waste pipe on the downstream side of the highest fixture of the group and the upper end connects to a branch vent, vent stack, stack vent or extends to open air independently and “circuit vented” has a corresponding meaning.

Cleanout means a fitting access in a drainage system or venting system that is installed to provide access for cleaning and inspection and that is provided with a readily replaceable air tight cover.

Clean water means water that has passed through a recirculation system.

Clear water waste means waste water containing no impurities or contaminants that are harmful to a person’s health, plant or animal life or that impair the quality of the natural environment.

Closure means a device or assembly for closing an opening through a fire separation or an exterior wall, such as a door, a shutter, wired glass or glass block, and includes all components such as hardware, closing devices, frames and anchors.

Combustible means that a material fails to meet the acceptance criteria of CAN4-S114, “Standard Method of Test for Determination of Non-Combustibility in Building Materials.”

Combustible construction means that type of construction that does not meet the requirements for noncombustible construction.

Compliance alternative means a substitute for a requirement in another Part of the Code that is listed in Part 10 or 11, and “C.A.” has a corresponding meaning.

Computer room means a room containing electronic computer/data processing equipment such as main frame type, which is separated from the remainder of the building for the purpose of controlling the air quality in the room by a self-contained climate control system and in which the occupant load of the room is not more than one person for each 40 m2 of the room.

Conditioned Space means any space within a building the temperature of which is controlled to limit variation in response to the exterior ambient temperature or interior differential temperatures by the provision, either directly or indirectly, of heating or cooling over substantial portions of the year.

Construction index means a level on a scale of 1 to 8 determined in accordance with Table 11.2.1.1.A. designating the expected performance level of the building structure with respect to the type of construction and fire protection of an existing building, and “C.I.” has a corresponding meaning.

Contained use area means a supervised area containing one or more rooms in which occupant movement is restricted to a single room by security measures not under the control of the occupant.

Continuous waste and vent means a vent pipe that is a vertical extension of a vertical waste pipe and includes the vertical waste pipe.

Critical level means the level of submergence at which the back-siphonage preventer ceases to prevent back-siphonage.

Day camp means a camp or resort that admits persons for a continuous period not exceeding twenty-four hours.

Day nursery means a day nursery as defined in the Day Nurseries Act.

Dead end means a pipe that terminates with a closed fitting.

Dead load means the weight of all permanent structural and nonstructural components of a building.

Deep foundation means a foundation unit that provides support for a building by transferring loads either by end-bearing to a soil or rock at considerable depth below the building, or by adhesion or friction, or both, in the soil or rock in which it is placed.  Piles are the most common type of deep foundation.

Design activities means the activities described in Subsection 15.11 (5) of the Act.

Design bearing pressure means the pressure applied by a foundation unit to a soil or rock and which is not greater than the allowable bearing pressure.

Design capacity, when used in the definition of the term sewage system, means total daily design sanitary sewage flow determined in accordance with Article 8.2.1.3.

Designer means the person responsible for the design.

Design load means the load applied to a foundation unit and which is not greater than the allowable load.

Detention occupancy (Group B, Division 1) means an occupancy in which persons are under restraint or are incapable of self preservation because of security measures not under their control.

Developed length means the length along the centre line of the pipe and fittings.

Directly connected means physically connected in such a way that water or gas cannot escape from the connection.

Distributing pipe means a pipe or piping in a water distribution system.

Distribution box means a device for ensuring that effluent from a treatment unit is distributed in equal amounts to each line of distribution pipe in a leaching bed.

Distribution pipe means a line or lines of perforated or open jointed pipe or tile installed in a leaching bed for the purpose of distributing effluent from a treatment unit to the soil (as defined in Part 8) or leaching bed fill in the leaching bed.

Diving board means a flexible board.

Diving platform means a rigid platform that is not a starting platform.

Drainage system means an assembly of pipes, fittings, fixtures and appurtenances on the property that is used to convey sewage and clear water waste to a main sewer or a private sewage disposal system, and includes a private sewer but does not include subsoil drainage piping.

Drinking-water system has the same meaning as in Subsection 2 (1) of the Safe Drinking Water Act, 2002.

Drum trap means a trap that has the inlet and outlet ends in the sides of the cylindrical body of the trap.

Dwelling unit means a suite operated as a housekeeping unit, used or intended to be used as a domicile by 1 or more persons and usually containing cooking, eating, living, sleeping and sanitary facilities.

Earth pit privy means a latrine consisting of an excavation in the ground surmounted by a superstructure.

Effluent means sanitary sewage that has passed through a treatment unit.

Electric space heating means an electric energy source that provides more than 10% of the heating capacity provided for the building and includes the following types:

(a)	electric resistance unitary baseboard heating,

(b)	electric resistance unitary cabinet heating,

(c)	electric resistance ceiling cable or floor cable heating,

(d)	electric resistance central furnace heating,

(e)	electric hot water space heating, or

(f)	air source heat pumps in combination with electric resistance backup heating.

Excavation means the space created by the removal of soil, rock or fill for the purposes of construction.

Exhaust duct means a duct through which air is conveyed from a room or space to the outdoors.

Exit means that part of a means of egress, including doorways, that leads from the floor area it serves, to a separate building, an open public thoroughfare, or an exterior open space protected from fire exposure from the building and having access to an open public thoroughfare.

Exit level means the level of an enclosed exit stair in a building governed by Subsection 3.2.6. at which an exterior exit door or exit corridor leads to the exterior.

Exit storey means a storey having an exterior exit door in a building governed by Subsection 3.2.6.

Exposing building face means that part of the exterior wall of a building which faces one direction and is located between ground level and the ceiling of its top storey, or where a building is divided into fire compartments, the exterior wall of a fire compartment which faces one direction.

Exterior cladding means those components of a building which are exposed to the outdoor environment and are intended to provide protection against wind, water or vapour.

Factory-built chimney means a chimney consisting entirely of factory-made parts, each designed to be assembled with the other without requiring fabrication on site.

Farm building means a building or part thereof which does not contain a residential occupancy and which is associated with and located on land devoted to the practice of farming and used essentially for the housing of equipment or livestock, or the production, storage or processing of agricultural and horticultural produce or feeds.

Fill means soil, rock, rubble, industrial waste such as slag, organic material or a combination of these that is transported and placed on the natural surface of a soil or rock or organic terrain.  It may or may not be compacted.

Fire compartment means an enclosed space in a building that is separated from all other parts of the building by enclosing construction providing a fire separation that may be required to have a fire-resistance rating.

Fire damper means a closure which consists of a normally held open damper installed in an air distribution system or in a wall or floor assembly, and designed to close automatically in the event of a fire in order to maintain the integrity of the fire separation.

Fire detector means a device which detects a fire condition and automatically initiates an electrical signal to actuate an alert signal or alarm signal and includes heat detectors and smoke detectors.

Fire load means the combustible contents of a room or floor area expressed in terms of the average weight of combustible materials per unit area, from which the potential heat liberation may be calculated based on the calorific value of the materials, and includes the furnishings, finished floor, wall and ceiling finishes, trim and temporary and movable partitions.

Fire-protection rating means the time in hours or fraction thereof that a closure will withstand the passage of flame when exposed to fire under specified conditions of test and performance criteria, or as otherwise prescribed in this Code.

Fire-resistance rating means the time in hours or fraction thereof that a material or assembly of materials will withstand the passage of flame and the transmission of heat when exposed to fire under specified conditions of test and performance criteria, or as determined by extension or interpretation of information derived therefrom as prescribed in this Code.

Fire-retardant treated wood means wood or a wood product that has had its surface-burning characteristics, such as flame spread, rate of fuel contribution and density of smoke developed, reduced by impregnation with fire-retardant chemicals.

Fire separation means a construction assembly that acts as a barrier against the spread of fire.

Fire service main means a pipe and its appurtenances which are connected to a source of water and that are located on the property:

(a)	between the source of water and the base of the riser of a water-based fire protection system,

(b)	between the source of water and inlets to foam making systems,

(c)	between the source of water and the base elbow of private hydrants or monitor nozzles,

(d)	used as fire pump suction and discharge piping not within a building, or

(e)	beginning at the inlet side of the check valve on a gravity or pressure tank.

Fire stop flap means a device intended for use in horizontal assemblies required to have a fire-resistance rating and incorporating protective ceiling membranes, which operates to close off a duct opening through the membrane in the event of a fire.

Firewall means a type of fire separation of noncombustible construction which subdivides a building or separates adjoining buildings to resist the spread of fire and which has a fire-resistance rating as prescribed in this Code and has structural stability to remain intact under fire conditions for the required fire-rated time.

First storey means the storey with its floor closest to grade and having its ceiling more than 1.8 m above grade.

Fixture means a receptacle, plumbing appliance, apparatus or other device that discharges sewage or clear water waste, and includes a floor drain.

Fixture drain means the pipe that connects a trap serving a fixture to another part of a drainage system.

Fixture outlet pipe means a pipe that connects the waste opening of a fixture to the trap serving the fixture.

Fixture unit (as applying to drainage systems) means the unit of measure based on the rate of discharge, time of operation and frequency of use of a fixture that expresses the hydraulic load that is imposed by that fixture on the drainage system.

Fixture unit (as applying to water distribution systems) means the unit of measure based on the rate of supply, time of operation and frequency of use of a fixture or outlet that expresses the hydraulic load that is imposed by that fixture or outlet on the supply system.

Flame-spread rating means an index or classification indicating the extent of spread-of-flame on the surface of a material or an assembly of materials as determined in a standard fire test as prescribed in this Code.

Flood level rim means the top edge at which water can overflow from a fixture or device.

Floor area means the space on any storey of a building between exterior walls and required firewalls including the space occupied by interior walls and partitions, but not including exits, vertical service spaces, and their enclosing assemblies.

Flow control roof drain means a roof drain that restricts the flow of water that is discharged from a surface as a result of rainfall or snowfall into the storm drainage system.

Flue means an enclosed passageway for conveying flue gases.

Flue collar means the portion of a fuel-fired appliance designed for the attachment of the flue pipe or breeching.

Flue pipe means the pipe connecting the flue collar of an appliance to a chimney.

Food premise means a floor area where food or drink for human consumption, or an ingredient of food or drink for human consumption, is manufactured, processed, prepared, stored, displayed, handled, served, distributed, sold or offered for sale, but does not include,

(a)	a private residence,

(b)	a boarding house that provides meals for fewer than ten boarders,

(c)	a building to which Regulation 554 or 568 of the Revised Regulations of Ontario, 1990 applies,

(d)	a plant, as defined in the Milk Act, that is required to be operated under the authority of a licence issued under that Act,

(e)	a plant, as defined in the Meat Inspection Act, that is required to be operated under the authority of a licence issued under that Act,

(f)	an egg-grading station or a processed egg station that is required to be operated under the authority of a licence issued under the Livestock and Livestock Products Act,

(g)	a floor area occupied by a church, service club or fraternal organization for the purpose of,

(i)	preparing meals for special events for its members and personally invited guests, or

(ii)	conducting bake sales, or

(h)	a farm building.

Forced-air furnace means a furnace equipped with a fan that provides the primary means for the circulation of air.

Force main means a sanitary drainage pipe through which sanitary sewage is conveyed by mechanical or pneumatic propulsion.

Foundation means a system or arrangement of foundation units through which the loads from a building are transferred to supporting soil or rock.

Foundation unit means one of the structural members of the foundation of a building such as a footing, raft or pile.

Fresh air inlet means a vent pipe that is installed in conjunction with a building trap and terminates in open air.

Frost action means the phenomenon that occurs when water in soil is subjected to freezing which, because of the water ice phase change or ice lens growth, results in a total volume increase or the build-up of expansive forces under confined conditions or both, and the subsequent thawing that leads to loss of soil strength and increased compressibility.

Furnace means a space-heating appliance using warm air as the heating medium and usually having provision for the attachment of ducts.

Gaming premise means a gaming premises as defined in the Ontario Lottery and Gaming Corporation Act, 1999.

Gas vent means that portion of a venting system designed to convey vent gases to the outdoors from the vent connector of a gas-fired appliance or directly from the appliance when a vent connector is not used.

Grade means the average level of proposed or finished ground adjoining a building at all exterior walls.

Graded lumber means lumber which has been graded and stamped to indicate its grade as determined by the NLGA “Standard Grading Rules for Canadian Lumber”.

Greywater means sanitary sewage of domestic origin which is derived from fixtures other than sanitary units.

Gross area means the total area of all floors above grade measured between the outside surfaces of exterior walls or between the outside surfaces of exterior walls and the centre line of firewalls except that, in any other occupancy than a residential occupancy, where an access or a building service penetrates a firewall, measurements shall not be taken to the centre line of such firewall.

Groundwater means a free standing body of water in the ground.

Groundwater level means the top surface of a free standing body of water in the ground.

Ground water means water below the surface of the ground occupying a zone of the earth’s mantle that is saturated with water.

Ground water table means the elevation of the upper surface of the ground water existing in the area of the sewage system.

Guard means a protective barrier around openings in floors or at the open sides of stairs, landings, balconies, mezzanines, galleries, raised walkways or other locations to prevent accidental falls from one level to another.  Such barrier may or may not have openings through it.

Hauled sewage means sanitary sewage that,

(a)	is not finally disposed of at the site where it is produced and is not conveyed by a sewer to a sewage works, and

(b)	is stored or retained at the site where it is produced for periodic collection, handling, treatment, transportation, storage or processing prior to final disposal at a place other than where it was produced,

and includes sanitary sewage that is removed from a sewage system for purposes of cleaning or maintaining the system.

Hauled sewage system means works, installations, equipment, operations and land used in connection with the collection, handling, treatment, transportation, storage, processing and disposal of hauled sewage as regulated under the Environmental Protection Act.

Hazard index means a level on a scale of 1 to 8 determined in accordance with Tables 11.2.1.1.B. to 11.2.1.1.N. designating the life safety hazard to occupants of the building based on,

(a)	use and occupancy,

(b)	occupant load,

(c)	the use and function of floor spaces,

(d)	the difficulty of egress,

(e)	the fire load of contents, finishes and furnishings,

(f)	the configuration or compartmentation of floor spaces, and

(g)	the size of building,

and “H.I.” has a corresponding meaning.

Hazardous classroom means a classroom supplied with flammable gas, containing hazardous substances such as chemicals or explosive dusts, containing large quantities of combustible materials or where cooking equipment is used.

Hazardous room means a room containing sufficient quantities of a substance which because of its chemical nature may create an atmosphere or condition of imminent hazard to health.

Header means a vent pipe that connects two or more vent stacks or stack vents to open air.

Header line means a line of pipe with watertight joints installed in a sewage system for the purpose of distributing effluent from a treatment unit to the distribution pipe in a leaching bed.

Heat detector means a fire detector designed to operate at a predetermined temperature or rate of temperature rise.

Heavy timber construction means that type of combustible construction in which a degree of fire safety is attained by placing limitations on the sizes of wood structural members and on thickness and composition of wood floors and roofs and by the avoidance of concealed spaces under floors and roofs.

Heritage building means a building designated under the Ontario Heritage Act, or a building that is certified to be of significant architectural or historical value by a recognized, non-profit public organization whose primary object is the preservation of structures of architectural or historical significance and which certification is accepted by the chief building official.

High ground water table means the highest elevation at which there is physical evidence that the soil (as defined in Part 8) or leaching bed fill has been saturated with water.

High hazard industrial occupancy (Group F, Division 1) means an industrial occupancy containing sufficient quantities of highly combustible and flammable or explosive materials which, because of their inherent characteristics, constitute a special fire hazard.

Holding tank means a tank designed for the total retention of all sanitary sewage discharged into it and requiring periodic emptying.

Home for special care means a home for the care of persons requiring nursing, residential or sheltered care.

Horizontal branch means that part of a waste pipe that is horizontal and installed to convey the discharge from more than one fixture.

Horizontal exit means an exit from one building to another by means of a doorway, vestibule, walkway, bridge or balcony.

Horizontal service space means a space such as an attic, duct, ceiling, roof or crawl space oriented essentially in a horizontal plane, concealed and generally inaccessible, through which building service facilities such as pipes, ducts and wiring may pass.

Hotel means floor areas, a floor area or part of a floor area containing 4 or more suites which provide sleeping accommodation for the travelling public or for recreational purposes.

Hub drain means a drain opening for indirect liquid wastes that does not serve as a floor drain, that has the same pipe size, material and venting requirements as a floor drain and that has a flood level rim above the floor in which it is installed and receives wastes that are discharged directly into the drain opening.

Impeded egress zone means a supervised area in which occupants have free movement but require the release, by security personnel, of security doors at the boundary before they are able to leave the area, but does not include a contained use area.

Indirect service water heater means a service water heater that derives its heat from a heating medium such as warm air, steam or hot water.

Indirectly connected means not directly connected.

Indoor pool means a public pool where the pool and pool deck are totally or partially covered by a roof.

Industrial occupancy means the occupancy or use of a building or part thereof for the assembling, fabricating, manufacturing, processing, repairing or storing of goods and materials.

Interceptor means a receptacle that is designed and installed to prevent oil, grease, sand or other materials from passing into a drainage system.

Interconnected floor space means superimposed floor areas or parts of floor areas in which floor assemblies that are required to be fire separations are penetrated by openings that are not provided with closures.

Leaching means dispersal of liquid by downward or lateral drainage or both into permeable soil (as defined in Part 8) or leaching bed fill.

Leaching bed means an absorption system constructed as absorption trenches or as a filter bed, located wholly in ground or raised or partly raised above ground as required by local conditions, to which effluent from a treatment unit is applied for treatment and disposal and that is composed of,

(a)	the soil (as defined in Part 8), leaching bed fill or other filter media that is contained between the surface to which the sanitary sewage is applied and the bottom of the bed,

(b)	the distribution pipe and the stone or gravel layer in which such pipe is located, and

(c)	the backfill above the distribution pipe, including the topsoil and sodding or other anti-erosion measure, and the side slopes of any portion elevated above the natural ground elevation.

Leaching bed fill means unconsolidated material suitable for the construction of a leaching bed placed in the area of the leaching bed in order to obtain the required unsaturated zone below the distribution pipes, and the required lateral extent such that the effluent is absorbed.

Leader means a pipe that is installed to carry storm water from a roof to a storm building drain or sewer or other place of disposal.

Limiting distance means the distance from an exposing building face to a property line, the centre line of a street, lane or public thoroughfare, or to an imaginary line between 2 buildings or fire compartments on the same property, measured at right angles to the exposing building face.

Listed means equipment or materials included in a list published by a certification organization accredited by the Standards Council of Canada.

Live load means the load other than dead load to be assumed in the design of the structural members of a building.  It includes loads resulting from snow, rain, wind, earthquake and those due to occupancy.

Live/work unit means a dwelling unit that contains a subsidiary business and personal services occupancy or a subsidiary low hazard industrial occupancy, has an area of not more than 150 m2, and is used and operated by one or more persons of a single household.

Loadbearing as applying to a building element means subjected to or designed to carry loads in addition to its own dead load, excepting a wall element subjected only to wind or earthquake loads in addition to its own dead load.

Loading rate means the volume, in litres, of effluent per square metre applied in a single day to the soil (as defined in Part 8) or leaching bed fill.

Low hazard industrial occupancy (Group F, Division 3) means an industrial occupancy in which the combustible content is not more than 50 kg/m2 or 1200 MJ/m2 of floor area.

Low human occupancy (as applying to farm buildings) means an occupancy having an occupant load of not more than one person per 40 m2 of floor area during normal use.

Major occupancy means the principal occupancy for which a building or part thereof is used or intended to be used, and shall be deemed to include the subsidiary occupancies which are an integral part of the principal occupancy.

Make-up water means water added to a public pool from an external source.

Marquee means a canopy over an entrance to a building.

Masonry or concrete chimney means a chimney of brick, stone, concrete or masonry units constructed on site.

Means of egress means a continuous path of travel provided for the escape of persons from any point in a building or contained open space to a separate building, an open public thoroughfare, or an exterior open space protected from fire exposure from the building and having access to an open public thoroughfare.  Means of egress includes exits and access to exits.

Medium hazard industrial occupancy (Group F, Division 2) means an industrial occupancy in which the combustible content is more than 50 kg/m2 or 1200 MJ/m2 of floor area and not classified as high hazard industrial occupancy.

Mercantile occupancy means the occupancy or use of a building or part thereof for the displaying or selling of retail goods, wares or merchandise.

Mezzanine means an intermediate floor assembly between the floor and ceiling of any room or storey and includes an interior balcony.

Modified pool means a public pool that has a basin-shaped floor sloping downward and inward toward the interior from the rim.

Modified stack venting means a stack venting arrangement where the stack vent above the connection of the highest stack vented fixture is reduced in diameter.

Municipal drinking-water system has the same meaning as in Subsection 2 (1) of the Safe Drinking Water Act, 2002.

Nominally horizontal means at an angle of less than 45° with the horizontal.

Nominally vertical means at an angle of not more than 45° with the vertical.

Noncombustible means that a material meets the acceptance criteria of CAN4-S114, “Standard Method of Test for Determination of Non-Combustibility in Building Materials”.

Noncombustible construction means that type of construction in which a degree of fire safety is attained by the use of noncombustible materials for structural members and other building assemblies.

Occupancy means the use or intended use of a building or part thereof for the shelter or support of persons, animals or property.

Occupant load means the number of persons for which building or part thereof is designed.

Offset means the piping that connects the ends of 2 pipes that are parallel.

Open air means the atmosphere outside a building.

Open-air storey means a storey in which at least 25% of the total area of its perimeter walls is open to the outdoors in a manner that will provide cross ventilation to the entire storey.

Outdoor pool means a public pool that is not an indoor pool.

Pail privy means a latrine in which the receptacle for human waste consists of a removable container surmounted by a superstructure.

Partition means an interior wall 1 storey or part-storey in height that is not loadbearing.

Party wall means a wall jointly owned and jointly used by 2 parties under easement agreement or by right in law, and erected at or upon a line separating 2 parcels of land each of which is, or is capable of being, a separate real-estate entity.

Perched groundwater means a free standing body of water in the ground extending to a limited depth.

Percolation time means the average time in minutes that is required for water to drop one centimetre during a percolation test or as determined by a soil evaluation or analysis.

Performance level means that level of performance under which all or part of an existing building functions with respect to its building systems.

Pharmacy means a premises or the part of a premises in which prescriptions are compounded and dispensed for the public or in which drugs are sold by retail.

Pile means a slender deep foundation unit, made of materials such as wood, steel or concrete or combination thereof, which is either premanufactured and placed by driving, jacking, jetting or screwing, or cast-in-place in a hole formed by driving, excavating or boring.

Plenum means a chamber forming part of an air duct system.

Plumbing appliance means a receptacle or equipment that receives or collects water, liquids or sewage and discharges water, liquid or sewage directly or indirectly to a plumbing system.

Plumbing system means a system of connected piping, fittings, valves, equipment, fixtures and appurtenances contained in plumbing.

Point of entry treatment unit has the same meaning as in Subsection 1 (1) of Ontario Regulation 170/03 made under the Safe Drinking Water Act, 2002.

Pool deck means the area immediately surrounding a public pool.

Portable privy means a portable latrine in which the receptacle for human body waste and the superstructure are combined structurally into one unit.

Post-disaster building means a building essential to provide services in the event of a disaster, and includes hospitals, fire stations, police stations, radio stations, telephone exchanges, power stations, electrical substations, water and sewage pumping stations and fuel depot buildings.

Potable means fit for human consumption.

Potable water system means the plumbing that conveys potable water.

Pressurized distribution system means a leaching bed in which the effluent is distributed through the use of pressurized distribution pipes.

Private sewage disposal system means a sewage system or a sewage works which is not owned and operated by the Crown, a municipality or an organisation acceptable to the Director responsible for issuing a Certificate of Approval under the Ontario Water Resources Act.

Private sewer means a sewer other than a building sewer that,

(a)	is not owned or operated by a municipality, the Ministry of Environment or other public agency,

(b)	receives drainage from more than one sanitary building drain either directly or through more than one sanitary building sewer or receives drainage from more than one storm building drain either directly or through one or more storm building sewers, and connects to a main sewer, or

(c)	serves as a place of disposal on the property,

but does not include:

(d)	a sewer that carries only the sanitary waste or storm sewage from two semi-detached dwelling units,

(e)	a sewer that carries only the sanitary waste or storm sewage from one main building that is of industrial, commercial or care or detention occupancy and one ancillary building, or

(f)	a sewer that carries only the sanitary waste or storm sewage from a row housing complex having five or fewer single family residences.

Private water supply means piping on the property that conveys potable water from a drinking-water system to more than one water service pipe.

Privy vault means a latrine in which the receptacle for the human waste consists of a constructed vault from which the waste is periodically removed.

Professional engineer means, for the purposes of the Act and this Code, a person who holds a licence or a temporary licence under the Professional Engineers Act.

Public corridor means a corridor that provides access to exit from more than 1 suite.

Public heritage building means a heritage building where occupancy in whole or in part includes viewing thereof by the public provided that displays therein are limited to those relevant to the heritage significance of the building.

Public pool means a structure, basin, chamber or tank containing or intended to contain an artificial body of water for swimming, water sport, water recreation or entertainment but does not include,

(a)	pools operated in conjunction with less than six dwelling units, suites or single family residences or any combination thereof,

(b)	pools that are used only for commercial display and demonstration purposes,

(c)	wading pools,

(d)	hydro-massage pools, or

(e)	pools that serve only as receiving basins for persons at the bottom of water slides.

Public spa means a hydro-massage pool containing an artificial body of water that is intended primarily for therapeutic or recreational use, that is not drained, cleaned or refilled before use by each individual and that utilizes hydrojet circulation, air induction bubbles, current flow or a combination of them over the majority of the pool area, but does not include,

(a)	wading pools, or

(b)	spas operated in conjunction with less than six dwelling units, suites or single family residences, or any combination of them, for the use of occupants or residents and their visitors.

Public use (as applying to the classification of plumbing fixtures) means fixtures in general washrooms of schools, gymnasiums, hotels, bars, public comfort stations and other installations where fixtures are installed so that their use is unrestricted.

Public way means a sidewalk, street, highway, square or other open space to which the public has access, as of right or by invitation, expressed or implied.

Range means a cooking appliance equipped with a cooking surface and 1 or more ovens.

Recirculation system means a system that maintains circulation of water through a public pool by pumps, and that provides continuous treatment that includes filtration and chlorination or bromination and any other process that may be necessary for the treatment of the water.

Recreational camp means a camp for recreational activities consisting of 1 or more buildings or other structures, established or maintained as living quarters with or without charge for 10 or more persons, for temporary occupancy of 5 or more days.

Relief vent means a vent pipe that connects at the upper end to a vent stack and connects at the lower end to a horizontal branch between the first fixture connection and the soil stack or waste stack.

Repair for the purposes of clause 15 (5) (b) of the Act includes taking any actions that the chief building official considers necessary for the protection of the public.

Repair garage means a building or part thereof where facilities are provided for the repair or servicing of motor vehicles.

Residential occupancy means the occupancy or use of a building or part thereof by persons for whom sleeping accommodation is provided but who are not harboured or detained to receive medical care or treatment or are not involuntarily detained.

Return duct means a duct for conveying air from a space being heated, ventilated or air-conditioned back to the heating, ventilating or air-conditioning appliance.

Riser means a water distributing pipe that extends through at least one full storey (as defined in Part 7 of this Code).

Rock means that portion of the earth’s crust which is consolidated, coherent and relatively hard and is a naturally formed, solidly bonded, mass of mineral matter which cannot readily be broken by hand.

Roof drain means a fitting or device that is installed in the roof to permit storm sewage to discharge into a leader.

Roof gutter means an exterior channel installed at the base of a sloped roof to convey storm sewage.

Sanitary building drain means a building drain that conducts sewage and connects to the sanitary building sewer.

Sanitary building sewer means a pipe that is connected to a sanitary building drain 1 000 mm outside a wall of a building and that conducts sewage to a public sewer or private sewage disposal system.

Sanitary drainage pipe means all piping that conveys sanitary sewage to a place of disposal, including the sanitary building drain, sanitary building sewer, soil pipe, soil stack, waste stack and waste pipe but not the main sewer or piping in a sewage treatment plant.

Sanitary drainage system means a drainage system that conducts sanitary sewage.

Sanitary sewage means liquid or water borne waste,

(a)	of industrial or commercial origin, or

(b)	of domestic origin, including human body waste, toilet or other bathroom waste, and shower, tub, culinary, sink and laundry waste.

Sanitary sewer means a sewer that conducts sewage.

Sanitary unit means a water closet, urinal, bidet or bedpan washer.

Self-service storage building means a building that is used to provide individual storage spaces to the public and that is open to the public only for those purposes.

Septic tank means a watertight vault in which sanitary sewage is collected for the purpose of removing scum, grease and solids from the liquid without the addition of air and where solids settling and anaerobic digestion of the sanitary sewage takes place.

Service room means a room provided in a building to contain equipment associated with building services.

Service space means space provided in a building to facilitate or conceal the installation of building service facilities such as chutes, ducts, pipes, shafts or wires.

Service water heater means a device for heating water for plumbing services.

Sewage means sanitary sewage or storm sewage.

Sewage system means,

(a)	a chemical toilet, an incinerating toilet, a recirculating toilet, a self-contained portable toilet and all forms of privy including a portable privy, an earth pit privy, a pail privy, a privy vault and a composting toilet system,

(b)	a greywater system,

(c)	a cesspool,

(d)	a leaching bed system, or

(e)	a system which requires or uses a holding tank for the retention of hauled sewage at the site where it is produced prior to its collection by a hauled sewage system,

where these,

(f)	have a design capacity of 10,000 litres per day or less,

(g)	have, in total, a design capacity of 10,000 litres per day or less where more than one of these are located on a lot or parcel of land, and

(h)	are located wholly within the boundaries of the lot or parcel of land on which is located the building or buildings they serve.

Sewage works means a sewage works as defined in the Ontario Water Resources Act.

Shallow buried trench means an absorption trench that contains a chamber.

Shallow foundation means a foundation unit which derives its support from soil or rock located close to the lowest part of the building which it supports.

Size means the nominal diameter by which a pipe, fitting, trap or other similar item is commercially designated.

Smoke alarm means a combined smoke detector and audible alarm device designed to sound an alarm within the room or suite in which it is located upon the detection of smoke within that room or suite.

Smoke detector means a fire detector designed to operate when the concentration of airborne combustion products exceeds a pre-determined level.

Soil means that portion of the earth’s crust which is fragmentary, or such that some individual particles of a dried sample may be readily separated by agitation in water; it includes boulders, cobbles, gravel, sand, silt, clay and organic matter.

Soil pipe means a sanitary drainage pipe that carries the discharge of a sanitary unit with or without the discharge from any other fixture.

Soil stack means a vertical soil pipe that passes through one or more storeys and includes any offset that is part of the stack.

Space heater means a space-heating appliance for heating the room or space within which it is located, without the use of ducts.

Space-heating appliance means an appliance intended for the supplying of heat to a room or space directly, such as a space heater, fireplace or unit heater, or to rooms or spaces of a building through a heating system such as a central furnace or boiler.

Sprinklered means equipped with a system of automatic sprinklers.

Stack vent means a vent pipe that connects the top of a soil or waste stack to a header or open air and “stack vented” has a corresponding meaning.

Stack venting when used with reference to fixtures means an arrangement such that the connections of the drainage piping from the stack vented fixtures to the stack provide venting to the fixture traps so that no additional vent pipe is required.

Stage means a space designed primarily for theatrical performances with provision for quick change scenery and overhead lighting, including environmental control for a wide range of lighting and sound effects and which is traditionally, but not necessarily, separated from the audience by a proscenium wall and curtain opening.

Starting platform means a rigid platform located entirely on the pool deck consisting of a top which, if projected horizontally over the water surface, would be less than 1 000 mm in vertical height above the surface and that is designed to be used by a swimmer to dive from at the start of a swimming race.

Storage garage means a building or part thereof intended for the storage or parking of motor vehicles and which contains no provision for the repair or servicing of such vehicles.

Storage-type service water heater means a service water heater with an integral hot water storage tank.

Storey means that portion of a building which is situated between the top of any floor and the top of the floor next above it, and if there is no floor above it, that portion between the top of such floor and the ceiling above it.

Storm building drain means a building drain that conveys storm sewage to a storm building sewer.

Storm building sewer means a building sewer that conveys storm sewage to a place of disposal and commences 1 000 mm from the building.

Storm drainage pipe means all the connected piping that conveys storm sewage to a place of disposal and includes the storm building drain, storm building sewer, rain water leader, catch basin and area drain installed to collect water from the property and the piping that drains water from a swimming pool or from water cooled air conditioning equipment, but does not include,

(a)	a main storm sewer,

(b)	a subsoil drainage pipe, or

(c)	a private sewage treatment and disposal facility designed for the treatment or retention of storm sewage prior to discharge to the natural environment.

Storm drainage system means a drainage system that conveys storm sewage.

Storm sewage means water that is discharged from a surface as a result of rainfall, snow melt or snowfall.

Storm sewer means a sewer that conveys storm sewage.

Stove means an appliance intended for cooking and space heating.

Street means any highway, road, boulevard, square or other improved thoroughfare 9 m or more in width, which has been dedicated or deeded for public use, and is accessible to fire department vehicles and equipment.

Subsoil drainage pipe means a pipe that is installed underground to intercept and convey subsurface water, and includes foundation drain pipes.

Subsurface investigation means the appraisal of the general subsurface conditions at a building site by analysis of information gained by such methods as geological surveys, in situ testing, sampling, visual inspection, laboratory testing of samples of the subsurface materials and groundwater observations and measurements.

Suite means a single room or series of rooms of complementary use, operated under a single tenancy, and includes dwelling units, individual guest rooms in motels, hotels, boarding houses, rooming houses and dormitories as well as individual stores and individual or complementary rooms for business and personal services occupancies.

Supply duct means a duct for conveying air from a heating, ventilating or air-conditioning appliance to a space to be heated, ventilated or air-conditioned.

Surface water means water on the surface of the ground.

Theatre means a place of public assembly intended for the production and viewing of the performing arts or the screening and viewing of motion pictures, and consisting of an auditorium with permanently fixed seats intended solely for a viewing audience.

Trap means a fitting or device that is designed to hold a liquid seal that will prevent the passage of gas but will not materially affect the flow of a liquid.

Trap dip means the lowest part of the upper interior surface of a trap.

Trap seal depth means the vertical distance between the trap dip and the trap weir.

Trap standard means the trap for a fixture that is integral with the support for the fixture.

Trap weir means the highest part of the lower interior surface of a trap.

Treatment unit means a device which when designed, installed and operated in accordance with its design specifications provides a specific degree of sanitary sewage treatment reducing the contaminant load from that of sanitary sewage to given effluent quality.

Tribunal means the License Appeal Tribunal established under the Licence Appeal Tribunal Act, 1999.

Ungraded lumber means lumber which has not been grade stamped to indicate its grade as determined by the NLGA “Standard Grading Rules for Canadian Lumber” but which meets the following visual attributes:

(a)	it is rough sawn to full nominal size,

(b)	it has no evidence of decay,

(c)	it has no tight knots which exceed 25% of the cross section and which are spaced closer than 150 mm on centres,

(d)	it has no loose knots or holes which exceed 25% of the cross section and which are spaced closer than 600 mm on centres,

(e)	it has the slope of grain not exceeding 1 (vertical) in 4 (horizontal), and

(f)	it is free of excessive warp.

Unit heater means a suspended space heater with an integral air circulating fan.

Unprotected opening as applying to exposing building face means a doorway, window or opening other than one equipped with a closure having the required fire-protection rating, or any part of a wall forming part of the exposing building face that has a fire-resistance rating less than required for the exposing building face.

Vacuum breaker means back-siphonage preventer.

Vapour barrier means the elements installed to control the diffusion of water vapour.

Vent connector as applying to heating or cooling systems means the part of a venting system that conducts the flue gases or vent gases from the flue collar of a gas appliance to the chimney or gas vent, and may include a draft control device.

Vent pipe means a pipe that is part of a venting system.

Vent stack means a vent pipe that is connected at its upper end to a header or is terminated in open air and that is used to limit pressure differential in a soil or waste stack.

Venting system means an assembly of pipes and fittings that connects a drainage system with open air for circulation of air and the protection of trap seals in the drainage system.

Vertical leg means the vertical portion of a fixture drain and includes the portion of a drain from the outlet of a water closet bowl to the point where the connecting piping changes to horizontal.

Vertical service space means a shaft oriented essentially vertically that is provided in a building to facilitate the installation of building services including mechanical, electrical and plumbing installations and facilities such as elevators, refuse chutes and linen chutes.

Walkway means a covered or roofed pedestrian thoroughfare used to connect 2 or more buildings.

Waste pipe means a sanitary drainage pipe that carries the discharge from a fixture directly to a waste stack, soil stack, sanitary building drain, branch or sewage system.

Waste stack means a vertical waste pipe that passes through one or more storeys and includes any offset that is part of the stack that conducts liquid waste from fixtures other than sanitary units.

Water distribution system means an assembly of pipes, fittings, valves and appurtenances that conveys potable water to water supply outlets, fixtures, plumbing appliances and devices from the water service pipe or from a point of entry treatment unit located in the building.

Water purveyor means the owner or operator of a drinking-water system.

Water service pipe means a pipe on the property that conveys potable water from a drinking-water system or a private water supply to the inside of the building.

Water system means a water service pipe, a private water supply, a water distribution system, a fire service main or parts of any of them.

Wave action pool means a public pool equipped with a means for inducing wave motion in the water.

Wet vent means a waste pipe that also serves as a vent pipe.

Working capacity means the volume of liquid that a treatment unit or holding tank is capable of holding without overflowing while it is in its working position, but does not include the volume of liquid contained in a compartment in which a pump or siphon is installed.

X-ray equipment includes x-ray imaging systems, processing equipment and equipment directly related to the production of images for diagnosis or directly related to irradiation with x-rays for therapy.

X-ray machine means an electrically-powered device producing x-rays for the irradiation of a human being or an animal for a therapeutic or diagnostic purpose or for industrial use.

Yoke vent means a vent pipe that is connected at its lower end to a soil or waste stack and at its upper end to a vent stack or a branch vent that is connected to a vent stack.

1.1.3.3.  Applicable Law

(1)  For the purposes of Section 8 of the Act, applicable law means:

(a)	the statutory requirements in the following provisions with respect to the following matters:

(i)	Revoked:  O. Reg. 389/05, s. 1 (1).

(ii)	Section 5 of the Charitable Institutions Act, with respect to the approval by the Minister of the site and plans for a new building or an addition to an existing building used or to be used as a charitable institution,

(iii)	Section 5 of Regulation 262 of the Revised Regulations of Ontario, 1990, made under the Day Nurseries Act, with respect to the approval of plans for a new building to be erected or an existing building to be used, altered or renovated for use as a day nursery or for alterations or renovations to be made to premises used by a day nursery,

(iv)	Revoked:  O. Reg. 389/05, s. 1 (1).

(v)	Section 194 of the Education Act, with respect to the approval of the Minister for the demolition of a building,

(vi)	Revoked:  O. Reg. 389/05, s. 1 (1).

(vii)	Revoked:  O. Reg. 389/05, s. 1 (1).

(viii)	Section 6 of Regulation 314 of the Revised Regulations of Ontario, 1990, made under the Elderly Persons Centres Act, with respect to the approval of the Minister for the construction of a building project,

(ix)	Section 5 of the Environmental Assessment Act with respect to the approval of the Minister or the Environmental Review Tribunal to proceed with an undertaking,

(x)	Revoked:  O. Reg. 349/06, s. 2 (1).

(xi)	Section 46 of the Environmental Protection Act with respect to the approval of the Minister to use land or land covered by water that has been used for the disposal of waste,

(xi.1)	Section 168.3.1 of the Environmental Protection Act with respect to the construction of a building to be used in connection with a change of use of a property,

(xi.2)	Paragraph 2 of Subsection 168.6 (1) of the Environmental Protection Act if a certificate of property use has been issued in respect of the property under subsection 168.6 (1) of that Act,

(xii)	Section 9 of Regulation 469 of the Revised Regulations of Ontario, 1990, made under the Funeral Directors and Establishments Act, with respect to the provision to the Registrar of architectural plans or drawings of the proposed construction or alteration of a funeral establishment,

(xiii)	Section 14 of the Homes for the Aged and Rest Homes Act with respect to the approval of the Minister for the erection or alteration of a building for use as a home or a joint home,

(xiv)	Section 14 of the Milk Act with respect to the permit from the Director for the construction or alteration of any building intended for use as a plant,

(xv)	Section 4 of Regulation 832 of the Revised Regulations of Ontario, 1990, made under the Nursing Homes Act, with respect to the provision to the Director of plans and specifications and such information and other material as may be required by the Director in respect of the construction, alteration, addition to or renovation of a nursing home or conversion of an existing building into a nursing home,

(xv.1)	Section 11.1 of Ontario Regulation 267/03 (General) made under the Nutrient Management Act, 2002 with respect to a proposed building or structure to house farm animals or store nutrients if that regulation requires the preparation and approval of a nutrient management strategy before construction of the proposed building or structure,

(xv.2)	Subsection 30 (2) of the Ontario Heritage Act with respect to a consent of the council of a municipality to the alteration or demolition of a building where the council of the municipality has given a notice of intent to designate the building under subsection 29 (3) of that Act,

(xvi)	Section 33 of the Ontario Heritage Act with respect to the consent of the council of a municipality for the alteration of property,

(xvii)	Section 34 of the Ontario Heritage Act with respect to the consent of the council of a municipality for the demolition of a building,

(xvii.1)	Section 34.5 of the Ontario Heritage Act with respect to a consent of the Minister to the alteration or demolition of a designated building,

(xvii.2)	Subsection 34.7 (2) of the Ontario Heritage Act with respect to a consent of the Minister to the alteration or demolition of a building where the Minister has given a notice of intent to designate the building under section 34.6 of that Act,

(xviii)	Section 42 of the Ontario Heritage Act with respect to the permit given by the council of a municipality for the erection, alteration or demolition of a building,

(xviii.1)	Section 14 of the Ontario Planning and Development Act, 1994 with respect to any conflict between a development plan made under that Act and a zoning by-law that affects the proposed building or structure,

(xix)	Section 41 of the Planning Act with respect to the approval by the council of the municipality or the Municipal Board of plans and drawings,

(xx)	Revoked:  O. Reg. 349/06, s. 2 (3).

(xxi)	Revoked:  O. Reg. 349/06, s. 2 (3).

(xxii)	Section 2 of Ontario Regulation 453/96, made under the Public Lands Act, with respect to the work permit authorizing the construction or placement of a building on public land,

(xxiii)	Section 34 or 38 of the Public Transportation and Highway Improvement Act with respect to the permit from the Minister for the placement, erection or alteration of any building or other structure or the use of land,

(b)	the following provisions of Acts and regulations:

(i)	Sections 28 and 53 of the Development Charges Act, 1997,

(ii)	Sections 257.83 and 257.93 of the Education Act,

(iii)	Subsection 5 (4) of the Environmental Assessment Act,

(iv)	Subsection 133 (4) of the Municipal Act, 2001,

(v)	Subsection 24 (3) of the Niagara Escarpment Planning and Development Act,

(vi)	Subsections 4 (3) and (5) of Regulation 832 of the Revised Regulations of Ontario, 1990, made under the Nursing Homes Act,

(vii)	Revoked:  O. Reg. 389/05, s. 1 (5).

(viii)	Subsection 27 (3) of the Ontario Heritage Act,

(ix)	Section 46 of the Planning Act,

(x)	Section 33 of the Planning Act except where, in the case of the demolition of a residential property, a permit to demolish the property is obtained under that Section,

(xi)	Revoked:  O. Reg. 389/05, s. 1 (7).

(xii)	Revoked:  O. Reg. 422/06, s. 1 (4).

(c)	regulations made by a conservation authority under Clause 28 (1) (c) of the Conservation Authorities Act with respect to permission of the authority for the construction of a building or structure if, in the opinion of the authority, the control of flooding, erosion, dynamic beaches or pollution or the conservation of land may be affected by the development,

(d)	by-laws made under Section 34 or 38 of the Planning Act or under Section 3 of Ontario Regulation 246/01 made under that Act,

(d.1)	by-laws made under Section 40.1 of the Ontario Heritage Act,

(e)	orders made by the Minister under section 47 of the Planning Act or subsection 17 (1) of the Ontario Planning and Development Act, 1994, and

(f)	by-laws made under any private Act that prohibit the proposed construction or demolition of the building unless the by-law is complied with.

(2)  For the purposes of Clause 10 (2) (a) of the Act, applicable law means any general or special Act, and all regulations and by-laws enacted under them that prohibit the proposed use of the building unless the Act, regulation or by-law is complied with.

1.1.4. Abbreviations

1.1.4.1.  Abbreviations of Proper Names

(1)  The abbreviations of proper names in this Code shall have the meanings assigned to them in this Article.  The appropriate addresses are shown in brackets following the name.

| ACI | American Concrete Institute (38800 Country Club Drive, Farmington Hills, Michigan 48331 U.S.A.) |
| --- | --- |
| ACNBC | Associate Committee on the National Building Code (National Research Council of Canada, Ottawa, Ontario K1A 0R6) |
| ANSI | American National Standards Institute (11 W. 42nd St., New York, New York 10036 U.S.A.) |
| ASHRAE | American Society of Heating, Refrigerating and Air-Conditioning Engineers (1791 Tullie Circle N.E., Atlanta, Georgia 30329-2305 U.S.A.) |
| ASPE | American Society of Plumbing Engineers (3617 Thousand Oaks Blvd., Suite 210, Westlake, California 91362 U.S.A.) |
| ASTM | American Society for Testing and Materials (1916 Race Street, Philadelphia, Pennsylvania 19103-1187 U.S.A.) |
| AWWA | American Water Works Association (45 23rd. Street, Toronto, Ontario M8V 3M6) |
| BRMD | Bureau of Radiation and Medical Devices (Department of National Health and Welfare 775 Brookefield Road, Ottawa, Ontario K1A 1C1) |
| CAN | National Standard of Canada designation (The number or name following the CAN designation represents the agency under whose auspices the standard is issued. CAN1 designates CGA, CAN2 designates CGSB, CAN3 designates CSA, and CAN4 designates ULC.) |
| CGA | Canadian Gas Association (178 Rexdale Boulevard, Rexdale, Ontario M9W 1R3) |
| CGSB | Canadian General Standards Board (11 Laurier St. Hull, Ottawa, Ontario K1A 0S5) |
| CLA | Canadian Lumbermen’s Association (27 Goulburn Avenue, Ottawa, Ontario K1N 8C7) |
| CSA | Canadian Standards Association (178 Rexdale Boulevard, Rexdale, Ontario M9W 1R3) |
| DBR | Division of Building Research (now called the Institute for Research in Construction) National Research Council of Canada, Ottawa, Ontario K1A 0R6 |
| FINA | Federation Internationale de Natation Amateur (208-3540 West 41st Avenue, Vancouver, British Columbia V6N 2G8) |
| HI | Hydronics Institute (35 Russo Place, P.O. Box 218, Berkeley Heights, New Jersey 07922 U.S.A.) |
| HRAI | Heating, Refrigerating and Air-Conditioning Institute of Canada (5045 Orbitor Drive, Building 11, Suite 300, Mississauga, Ontario L4W 4Y4) |
| HUD | U.S. Department of Housing and Urban Development (Office of the Assistant Secretary for Policy Development and Research, Washington, D.C. 20410 U.S.A.) |
| MOEE | Ontario Ministry of the Environment and Energy (135 St Clair Avenue West, Toronto, Ontario M4V 1P5) |
| NBC | National Building Code of Canada (National Research Council of Canada, Ottawa, Ontario K1A 0R6) |
| NFPA | National Fire Protection Association (1 Batterymarch Park, P.O. Box 9101, Quincy, Massachusetts 02269-9101 U.S.A.) |
| NLGA | National Lumber Grades Authority (103-4400 Dominion Street, Burnaby, British Columbia V5G 4G3) |
| SMACNA | Sheet Metal and Air Conditioning Contractors National Association Inc. (4201 Lafayette Centre Drive, Chantilly, Virginia 20151 U.S.A.) |
| ULC | Underwriters’ Laboratories of Canada (7 Crouse Road, Scarborough, Ontario M1R 3A9) |
| WCLIB | West Coast Lumber Inspection Bureau (6980 Southwest Varns Street, P.O. Box 23145, Portland, Oregon 97223 U.S.A.) |
| WH | Warnock Hersey Professional Services Ltd. (3210 American Drive, Mississauga, Ontario L4V 1B3) |
| WWPA | Western Wood Products Association (1500 Yeon Building, Portland, Oregon 97204 U.S.A.) |

1.1.4.2.  Symbols and Other Abbreviations

(1)  The symbols and other abbreviations in this Code shall have the meanings assigned to them in this Article.

| 1 in 2 | slope of 1 vertical to 2 horizontal |
| --- | --- |
| ABS | acrylonitrile-butadiene-styrene |
| BOD5 | the five-day biochemical oxygen demand |
| CBOD5 | the five-day carbonaceous biochemical oxygen demand |
| Cm | centimetre(s) |
| cm2 | square centimetre(s) |
| CPVC | chlorinated poly (vinyl chloride) |
| dB(A) | decibel-weighted sound level |
| ° | degree(s) |
| °C | degree(s) Celsius |
| Diam | Diameter |
| DWV | drain, waste and vent |
| G | gram(s) |
| Ga | Gauge |
| Gal | imperial gallon(s) |
| gal/min | imperial gallon(s) per minute |
| H | hour(s) |
| HVAC | Heating, Ventilating and Air-conditioning |
| Hz | Hertz |
| In | inch(es) |
| Inc. | Incorporated |
| J | joule(s) |
| Kg | kilogram(s) |
| kg/m2 | kilograms per square metre |
| KN | kilonewton(s) |
| kPa | kilopascal(s) |
| KW | kilowatt(s) |
| L | litre(s) |
| L/s | litre(s) per second |
| Lx | Lux |
| M | metre(s) |
| M2 | square metre(s) |
| M/s | metre(s) per second |
| Max. | Maximum |
| mg/L | milligram(s) per litre |
| Min. | Minimum |
| Min | minute(s) |
| MJ | megajoule(s) |
| Mm | millimetre(s) |
| Mpa | megapascal(s) |
| N | Newton |
| N/A | not applicable |
| Ng | nanogram(s) |
| No. | number(s) |
| Nom. | Nominal |
| o.c. | On centre |
| OSB | oriented strandboard |
| Pa | pascal(s) |
| PB | Polybutylene |
| PE | Polyethylene |
| PE/AL/PE | Polyethylene/Aluminum/Polyethylene |
| PEX | cross-linked polyethylene |
| PEX/AL/ PEX | Crosslinked Polyethylene/Aluminum/ Crosslinked Polyethylene |
| PVC | poly (vinyl chloride) |
| RSI | thermal resistance, International System of Units |
| S | second(s) |
| SDR | standard dimension ratio |
| temp. | Temperature |
| T&G | tongue and groove |
| W | watt(s) |
| Wt | Weight |
| % | per cent |

O. Reg. 403/97, Part 1; O. Reg. 22/98, s. 1; O. Reg. 278/99, s. 1; O. Reg. 593/99, s. 1; O. Reg. 205/00, s. 1; O. Reg. 220/02, s. 1; O. Reg. 304/03, s. 1; O. Reg. 305/03, ss. 1, 2; O. Reg. 389/05, s. 1; O. Reg. 349/06, ss. 1, 2; O. Reg. 422/06, s. 1.

Part 2
General Requirements

| Section | 2.1. | Application |
| --- | --- | --- |
|  | 2.1.1. | Buildings |
|  | 2.1.2. | Designated Structures |
|  | 2.1.3. | Building Size Determination |
| Section | 2.2. | Materials, Appliances, Systems and Equipment |
|  | 2.2.1. | General |
|  | 2.2.2. | Building Materials Evaluation Commission |
| Section | 2.3. | Design and General Review |
|  | 2.3.1. | Design |
|  | 2.3.2. | General Review |
| Section | 2.4. | Permits & Inspections |
|  | 2.4.1. | Permits |
|  | 2.4.2. | Site Documents |
|  | 2.4.3. | Occupancy of Unfinished Building |
|  | 2.4.4. | Fire Department Inspection |
|  | 2.4.5. | Notices and Inspections |
|  | 2.4.6. | As Constructed Plans |
| Section | 2.5. | Climatic Data |
|  | 2.5.1. | Climatic and Seismic Values |
| Section | 2.6. | Referenced Documents |
|  | 2.6.1. | Application |
|  | 2.6.2. | Conflicting Requirements |
|  | 2.6.3. | Effective Date |
|  | 2.6.4. | Alternate Test Standards |
| Section | 2.7. | Equivalents |
|  | 2.7.1. | Application |
|  | 2.7.2. | Acceptance of Equivalents |
| Section | 2.8. | Rulings and Interpretations |
|  | 2.8.1. | Designated Materials Evaluation Bodies |
|  | 2.8.2. | Minister’s Ruling |
|  | 2.8.3. | Interpretations By Minister |
| Section | 2.9. | Search Warrant |
|  | 2.9.1. | Forms |
| Section | 2.10. | Building Code Commission |
|  | 2.10.1. | Hearings |
| Section | 2.13. | Designated Persons and Powers |
|  | 2.13.1. | General |
| Section | 2.14. | Prescribed Person |
|  | 2.14.1. | General |
| Section | 2.15. | Enforcement of Provisions of the Act and Building Code Related to Sewage Systems |
|  | 2.15.1. | General |
| Section | 2.16. | Qualifications for Chief Building Officials and Inspectors |
|  | 2.16.1. | Scope |
|  | 2.16.2. | Chief Building Officials |
|  | 2.16.3. | Supervisors and Managers |
|  | 2.16.4. | Inspectors |
|  | 2.16.5. | Updating of Qualifications |
|  | 2.16.6. | Information |
|  | 2.16.7. | Fees |
|  | 2.16.8. | Public Register |
|  | 2.16.9. | Categories of Qualifications |
| Section | 2.17. | Qualifications for Designers |
|  | 2.17.1. | Scope |
|  | 2.17.2. | General |
|  | 2.17.3. | Definition |
|  | 2.17.4. | Qualifications — Persons Engaged in the Business of Providing Design Activities to the Public |
|  | 2.17.5. | Qualifications — Other Designers |
|  | 2.17.6. | Public Register |
|  | 2.17.7. | Classes of Registration and Categories of Qualifications |
| Section | 2.18. | Qualifications for Persons Engaged in the Business of Constructing On Site, Installing, Repairing, Servicing, Cleaning or Emptying Sewage Systems |
|  | 2.18.1. | Scope |
|  | 2.18.2. | Definition |
|  | 2.18.3. | Qualifications |
|  | 2.18.4. | Public Register |
| Section | 2.19. | Qualifications for Registered Code Agencies |
|  | 2.19.1. | Scope |
|  | 2.19.2. | Definition |
|  | 2.19.3. | Qualifications |
|  | 2.19.4. | Public Register |
|  | 2.19.5. | Classes of Registration and Categories of Qualifications |
| Section | 2.20. | Classes of Registration and Categories of Qualifications |
|  | 2.20.1. | Scope |
|  | 2.20.2. | Classes of Registration and Categories of Qualifications |
| Section | 2.21. | Insurance |
|  | 2.21.1. | Scope |
|  | 2.21.2. | Insurance for Registered Code Agencies and Persons Referred to in Subsection 15.11 (5) of the Act |
| Section | 2.22. | Registered Code Agencies |
|  | 2.22.1. | Appointment of Registered Code Agency under Section 4.1 of the Act |
|  | 2.22.3. | When a Registered Code Agency may not be Appointed or Continue to Act under an Appointment |
|  | 2.22.4. | Additional Functions that Registered Code Agencies may be Appointed To Perform |
|  | 2.22.5. | Manner in which Registered Code Agency shall Perform Functions |
|  | 2.22.6. | Termination of Appointment of a Registered Code Agency |
|  | 2.22.7. | Information to be Provided |
|  | 2.22.8. | Referral of Stop Work Order |
| Section | 2.23. | Fees |
|  | 2.23.1. | Fees |

Part 2
General Requirement

Section 2.1. Application

2.1.1. Buildings

2.1.1.1.  Parts 1, 2, 7 and 12

(1)  Parts 1, 2, 7 and 12 apply to all buildings.

2.1.1.2.  Parts 3, 4, 5 and 6

(1)  Except as provided in Article 2.1.1.5., Sentence 2.1.1.6.(1) and Subsection 2.1.2., Parts 3, 4, 5 and 6 apply to all buildings occupying an area greater than ten square meters and

(a)	used for

(i)	Group A, assembly occupancies,

(ii)	Group B, care or detention occupancies, or

(iii)	Group F, Division 1, high hazard industrial occupancies, and

(b)	exceeding 600 m2 in building area or exceeding 3 storeys in building height used for major occupancies classified as

(i)	Group C, residential occupancies,

(ii)	Group D, business and personal services occupancies,

(iii)	Group E, mercantile occupancies, or

(iv)	Group F, Division 2 and 3, medium and low hazard industrial occupancies.

2.1.1.3.  Part 9

(1)  Except as provided in Sentences 2.1.1.4.(2), 2.1.1.6.(1) and Article 2.1.1.5., Part 9 applies to buildings occupying an area greater than ten square metres

(a)	of 3 storeys or less in building height,

(b)	having a building area not exceeding 600 m2, and

(c)	used for

(i)	Group C, residential occupancies,

(ii)	Group D, business and personal services occupancies,

(iii)	Group E, mercantile occupancies, or

(iv)	Group F, Division 2 and 3, medium and low hazard industrial occupancies.

2.1.1.4.  Site Assembled and Factory-Built Buildings

(1)  Except as provided in Sentence (2) and Article 2.1.1.7., this Code applies to the design and construction of site assembled buildings and manufactured buildings.

(2)  Except as provided in Sentence (3), a manufactured building intended for residential occupancy is deemed to comply with this Code if it is designed and constructed in compliance with

(a)	CAN/CSA-Z240.2.1, “Structural Requirements for Mobile Homes”, CAN/CSA-Z240.8.1., “Light Duty Windows” and CAN/CSA-Z240.3.1., “Plumbing Requirements for Mobile Homes”, if the building is constructed in Sections not wider than 4.88 m, or

(b)	CSA A-277 “Procedure for Certification of Factory-Built Houses”.

(3)  The requirements of this Code shall apply to

(a)	building components designed and constructed outside the place of manufacture, and

(b)	site installation of such buildings.

2.1.1.5.  Farm Buildings

(1)  Except as provided in Sentences (2) and (3), farm buildings shall conform to the requirements in the CCBFC National Farm Building Code of Canada 1995.

(2)  Articles 1.1.1.2. and 3.1.8.1. and Subsections 3.1.4. and 4.1.4. in the National Farm Building Code of Canada do not apply to farm buildings.

(3)  In the National Farm Building Code of Canada, references in Articles 1.1.1.3., 1.2.1.2., 2.2.2.1., 2.2.2.2., 2.3.1.1., 2.3.2.1., 3.1.1.1., 3.1.1.2., 3.1.2.1. and 3.1.6.1. to the National Building Code of Canada are deemed to refer to this Code.

2.1.1.6.  Renovation of Existing Buildings

(1)  Except as provided in Sentence (2), Part 11 applies to the design and construction of existing buildings, or parts of existing buildings, that have been in existence for at least five years.

(2)  Where a building has been in existence for at least five years but includes an addition that has been in existence for less than five years, Part 11 applies to the entire building.

2.1.1.7.  Existing Buildings

(1)  Except as provided in Section 3.15., Article 7.1.2.2., Section 9.41. and Part 11, where an existing building is extended or subject to material alteration or repair, the Code is applicable only to the design and construction of the extensions and those parts of the building that are subject to the material alteration or repair.

(2)  Where an existing previously occupied building is moved from the original location to be installed elsewhere, or is dismantled at the original location and moved to be reconstituted elsewhere, the Code applies only to changes to the design and construction of the building required as a result of moving the building.

2.1.1.8.  Radon

(1)  In addition to all other requirements, a building in the following designated areas shall be designed and constructed so that the annual average concentration of radon 222 does not exceed 250 millibecquerels per litre of air and the annual average concentration of the short lived daughters of radon 222 does not exceed 0.02 working levels inside the building

(a)	The Town of Elliot Lake in the Territorial District of Algoma,

(b)	The Township of Faraday in the County of Hastings, and

(c)	The geographic Township of Hyman in the Territorial District of Sudbury.

2.1.1.9.  Durability of Parking Structures

(1)  Parking structures shall be designed in conformance with CAN/CSA-S413, “Parking Structures”.

2.1.1.10.  Language Used on Required Signs

(1)  All required signs in this Code shall be displayed in the English language or in the English and French languages, including operational material on all life safety equipment and devices.

2.1.1.11.  Energy Efficiency

(1)  Except for buildings of residential occupancy within the scope of Part 9, farm buildings and areas of buildings intended primarily for manufacturing or commercial or industrial processing, the energy efficiency of all buildings shall be designed to good engineering practice such as described in

(a)	the ASHRAE/IES 90.1-1989, “Energy Efficient Design of New Buildings Except Lowrise Residential Buildings” and the Supplementary Guidelines to the 1997 OBC, or

(b)	the Model National Energy Code for Buildings, 1997.

2.1.1.12.  Change of Use

(1)  Part 10 applies to existing buildings requiring a permit under Section 10 of the Act.

2.1.1.13.  Building in Flood Plains

(1)  Buildings constructed on flood plains shall

(a)	be designed and constructed in accordance with good engineering practice to withstand anticipated vertical and horizontal hydrostatic pressures acting on the structure, and

(b)	incorporate floodproofing measures that will preserve the integrity of exits and means of egress during times of flooding.

2.1.1.14.  Sewage Systems

(1)  Part 8 applies to the construction, operation and maintenance of all sewage systems and to the construction of buildings in the vicinity of sewage systems.

2.1.2. Designated Structures

2.1.2.1.  Part 4

(1)  Part 4 applies to the following designated structures:

(a)	a retaining wall exceeding 1 000 mm in exposed height adjacent to

(i)	public property,

(ii)	access to a building, or

(iii)	private property to which the public is admitted,

(b)	the structural requirements for signs regulated by Section 3.14.,

(c)	a communication tower exceeding 16.6 m above ground level,

(d)	a pedestrian bridge appurtenant to a building,

(e)	a crane runway,

(f)	an exterior storage tank and its supporting structure which is not regulated by the Gasoline Handling Act or the Energy Act,

(g)	a dish antenna or a solar collector that is mounted on a building and has a face area equal to or greater than 5 m2, and

(h)	an outdoor pool that has a water depth greater than 3.5 m at any point.

(2)  Public pools are designated structures to which Section 3.11. applies.

(3)  Public spas are designated structures to which Section 3.11A. applies.

2.1.3. Building Size Determination

2.1.3.1.  Building Divided by Firewalls

(1)  Where a firewall divides a building, each portion of the building so divided shall be considered as a separate building, except for the purpose of

(a)	gross area determination in Section 2.3.,

(b)	a fire alarm and detection system in Sentence 3.2.4.2.(1) or Article 9.10.17.1., or

(c)	a plumbing system interconnected through a firewall.

2.1.3.2.  Building Divided by Vertical Fire Separations

(1)  Except as permitted in Sentence (2), where portions of a building are completely separated by a vertical fire separation that has a fire-resistance rating of at least 1 h and extends through all storeys and service spaces of the separate portions, each separated portion is permitted to be considered as a separate building for the purpose of determining building height provided

(a)	each separated portion is not more than 3 storeys in building height and is used only for residential occupancies, and

(b)	the unobstructed path of travel for the firefighter from the nearest street to one entrance of each separated portion is not more than 45 m.

(2)  The vertical fire separation in Sentence (1) may terminate at the floor assembly immediately above a basement provided the basement conforms to Article 3.2.1.2.

Section 2.2. Materials, Appliances, Systems and Equipment

2.2.1. General

2.2.1.1.  Characteristics of Materials, Appliances, Systems and Equipment

(1)  All materials, appliances, systems and equipment installed to meet the requirements of this Code shall possess the necessary characteristics to perform their intended functions when installed in a building.

2.2.1.2.  Recycled Materials, Used Materials, Appliances and Equipment

(1)  Unless otherwise specified, recycled materials in building products may be used and used materials, appliances and equipment may be reused when they meet the requirements of this Code for new materials and are satisfactory for the intended use.

2.2.2. Building Materials Evaluation Commission

2.2.2.1.  Application Fee

(1)  The fee on an application to the Building Materials Evaluation Commission is $950.00.

Section 2.3. Design and General Review

2.3.1. Design

2.3.1.1.  Design by Architect or Professional Engineer

(1)  Except as permitted in Sentences (2) and (3), the construction, including, for greater certainty, enlargement or alteration, of every building or part thereof described in Table 2.3.1.1. and this Article shall be designed and reviewed by an architect, professional engineer or both.

(2)  An architect may provide the services within the practice of professional engineering in any building described in Table 2.3.1.1., or a professional engineer may provide the services within the practice of architecture in any building described in Table 2.3.1.1. where to do so does not constitute a substantial part of the services provided by the other profession related to the construction of the building and is necessary

(a)	for the construction of the building and is incidental to the other services provided by the architect or professional engineer, or

(b)	for coordination purposes.

Table 2.3.1.1.(4)

Design and General Review

Forming Part of Sentence 2.3.1.1.(1)

| Building Classification by Major Occupancy | Building Description | Design and General Review by: |
| --- | --- | --- |
| Assembly occupancy only | Every building | Architect and professional engineer(1) |
| Assembly occupancy and any other major occupancy except industrial | Every building | Architect and professional engineer(1) |
| Care or detention occupancy only | Every building | Architect and professional engineer(1) |
| Care or detention occupancy and any other major occupancy except industrial | Every building | Architect and professional engineer(1) |
| Residential occupancy only | Every building that exceeds 3 storeys in building height | Architect and professional engineer(1) |
|  | Every building that exceeds 600 m2 in gross area and that contains a residential occupancy other than a dwelling unit or dwelling units | Architect(2) |
| Residential occupancy only | Every building that exceeds 600 m2 in gross area and contains a dwelling unit above another dwelling unit | Architect(2) |
|  | Every building that exceeds 600 m2 in building area contains 3 or more dwelling units and has no dwelling unit above another dwelling unit | Architect(2) |
| Residential occupancy and any other major occupancy except industrial, assembly or care or detention occupancy | Every building that exceeds 600 m2 in gross area or 3 storeys in building height | Architect and professional engineer(1) |
| Business and personal services occupancy only | Every building that exceeds 600 m2 in gross area or 3 storeys in building height | Architect and professional engineer(1) |
| Business and personal services occupancy and any other major occupancy except industrial, assembly or care or detention occupancy | Every building that exceeds 600 m2 in gross area or 3 storeys in building height | Architect and professional engineer(1) |
| Mercantile occupancy only | Every building that exceeds 600 m2 in gross area or 3 storeys in building height | Architect and professional engineer(1) |
| Mercantile occupancy and any other major occupancy except industrial, assembly or care or detention occupancy | Every building that exceeds 600 m2 in gross area or 3 storeys in building height | Architect and professional engineer(1) |
| Industrial occupancy only and where there are no subsidiary occupancies | Every building that exceeds 600 m2 in gross area or 3 storeys in building height | Architect or professional engineer(3) |
| Industrial occupancy and one or more other major occupancies where the portion of the area occupied by one of the other major or subsidiary occupancies exceeds 600 m2 | The non-industrial portion of every building | Architect and professional engineer(1) |
|  | The industrial portion of every building | Architect or professional engineer(3) |
| Industrial occupancy and one or more other major occupancies where no portion of the area occupied by one of the other major or subsidiary occupancies exceeds 600 m2 | Every building that exceeds 600 m2 in gross area or 3 storeys in building height | Architect or professional engineer(3) |
| Column 1 | 2 | 3 |

Notes To Table 2.3.1.1.

(1) An architect shall provide services within the practice of architecture and a professional engineer shall provide the services within the practice of professional engineering.

(2) An architect may engage a professional engineer to provide services within the practices of professional engineering.

(3) Only a professional engineer may provide services within the practice of professional engineering.

(4) Requirements for design and general review by an architect or professional engineer or a combination of both for the construction, enlargement or alteration of a building are set out in the Architects Act and the Professional Engineers Act.

(3)  The requirement for an architect does not apply to the preparation or provision of a design for interior space for a building, including finishes, fixed or loose furnishings, equipment, fixtures and partitioning of space, and related exterior elements such as signs, finishes and glazed openings used for display purposes, that does not affect or is not likely to affect

(a)	the structural integrity,

(b)	a fire safety system or fire separation,

(c)	a main entrance or public corridor on a floor,

(d)	an exit to a public thoroughfare or to the exterior,

(e)	the construction or location of an exterior wall, or

(f)	the usable floor space through the addition of a mezzanine, infill or other similar element,

of the building.

(4)  Where a building or part of it described in Table 2.3.1.1. is designed by an architect or a professional engineer or a combination of both as required by this Article, all plans, sketches, drawings, graphic representations, specifications and other documents that are prepared by an architect, professional engineer or both and that form the basis for the issuance of a permit under Section 8 of the Act or any changes to it authorized by the chief building official shall bear the signature and seal of the architect, professional engineer or both, as applicable.

(5)  Where the foundations of a building are to be constructed below the level of the footings of an adjacent building and within the angle of repose of the soil, as drawn from the bottom of the footings, the foundations shall be designed by a professional engineer.

(6)  The thermal design of a building in accordance with Section 9.38. shall be prepared and provided by an architect or professional engineer or a combination of both.

2.3.2. General Review

2.3.2.1.  General Review by Architect or Professional Engineer

(1)  Except as permitted in Sentence (2), a person who intends to construct or have constructed a building required to be designed by an architect, professional engineer or both, shall ensure that an architect, professional engineer or both are retained to undertake the general review of the construction of the building in accordance with the performance standards of the Ontario Association of Architects or the Association of Professional Engineers of Ontario, as applicable, to determine whether the construction is in general conformity with the plans, sketches, drawings, graphic representations, specifications and other documents that are prepared by an architect, professional engineer or both and that form the basis for the issuance of a permit under Section 8 of the Act or any changes to it authorized by the chief building official, copies of written reports arising out of the general review shall be forwarded to the chief building official or registered code agency, as the case may be, by the architect, professional engineer or both who have been retained to undertake the general review of the construction of the building.

(2)  An architect or a professional engineer need not be retained to undertake the general review of construction of a building where the building is designed in accordance with Section 9.38.

2.3.2.2.  Restriction for General Review

(1)  Only an architect may carry out or provide the general review of the construction of a building

(a)	that is constructed in accordance with a design prepared or provided by an architect, or

(b)	in relation to services that are provided by an architect in connection with the design in accordance with which the building is constructed.

(2)  Only a professional engineer may carry out or provide the general review of the construction of a building

(a)	that is constructed in accordance with a design prepared or provided by a professional engineer, or

(b)	in relation to services that are provided by a professional engineer in connection with the design in accordance with which the building is constructed.

2.3.2.3.  Demolition of a Building

(1)  The applicant for a permit respecting the demolition of a building shall retain a professional engineer to undertake the general review of the project during demolition, where

(a)	the building exceeds 3 storeys in building height or 600 m2 in building area,

(b)	the building structure includes pre-tensioned or post-tensioned members,

(c)	it is proposed that the demolition will extend below the level of the footings of any adjacent building and occur within the angle of repose of the soil, drawn from the bottom of such footings, or

(d)	explosives or a laser are to be used during the course of demolition.

Section 2.4. Permits and Inspections

2.4.1. Permits

2.4.1.1.  Requirement for Permits

(1)  A person is exempt from the requirement to obtain a permit under Section 8 of the Act

(a)	for the demolition of a building located on a farm,

(b)	subject to Sentence (1.1), for the construction or demolition of a building in territory without municipal organization, or

(c)	for the construction of a Class 1 sewage system.

(1.1)  The exemption in Clause (1) (b) from the requirement to obtain a permit does not apply to the construction of a sewage system in territory without municipal organization.

(2)  Where a permit is required for the demolition of a building in Sentence 2.3.2.3.(1), descriptions of the structural design characteristics of the building and the method of demolition shall be included in the application for a permit to demolish the building.

(3)  No person shall commence demolition of a building or any part of a building before the building has been vacated by the occupants except where the safety of the occupants is not affected.

(4)  Reserved.

(5)  A tent or group of tents is exempt from the requirement to obtain a permit under Section 8 of the Act and is exempt from compliance with the Code provided that the tent or group of tents are

(a)	not more than 60 m2 in aggregate ground area,

(b)	not attached to a building, and

(c)	constructed more than 3 m from other structures.

2.4.1.1A.  Applications for Permits under Section 8 of the Act

(1)  An application for a permit under Section 8 of the Act to construct or demolish a building shall be made after June 30, 2005 by

(a)	the owner of the property on which the proposed construction or demolition is to take place, or

(b)	the authorized agent of the owner referred to in Clause (a).

(2)  An application referred to in Sentence (1) that is made after June 30, 2005 shall be in a form approved by the Minister.

(3)  In Sentence (1),

owner includes, in respect of the property on which the construction or demolition will take place, the registered owner, a lessee and a mortgagee in possession.

2.4.1.1B.  Period Within Which a Permit is Issued or Refused

(1)  Subject to Sentences (2) and (3), if an application for a permit under Subsection 8 (1) of the Act that meets the requirements of Sentence (5) is submitted after December 31, 2005 to a chief building official, the chief building official shall, within the time period set out in Column 3 of Table 2.4.1.1B. corresponding to the class of building described in Column 2 of Table 2.4.1.1B. for which the application is made:

(a)	issue the permit, or

(b)	refuse to issue the permit and provide in writing all of the reasons for the refusal.

(2)  If an application made after December 31, 2005 for a permit under Subsection 8 (1) of the Act proposes construction or demolition of two or more buildings of different classes described in Column 2 of Table 2.4.1.1B. that have different time periods in Column 3 of Table 2.4.1.1B., the longer of the time periods shall be the time period for the purposes of Sentence (1).

(3)  If an application for a permit under Subsection 8 (1) of the Act proposes construction or demolition of a building described in Sentence (4), the time period for the purposes of Sentence (1) shall be the longer of

(a)	10 days, and

(b)	the time period corresponding to the class of the building described in Column 2 of Table 2.4.1.1B. that the building in Sentence (4) serves, if any.

(4)  A building referred to in Sentence (3) is:

(a)	a structure occupying an area of 10 m2 or less that contains plumbing, including the plumbing appurtenant to it,

(b)	plumbing not located in a structure,

(c)	a sewage system, or

(d)	a structure described in Article 2.1.2.1.

(5)  The requirements for an application referred to in Sentence (1) for a permit under Subsection 8 (1) of the Act are:

(a)	that the application be made in the form described in Sentence 2.4.1.1A.(2),

(b)	that the application be signed by a person described in Clause 2.4.1.1A.(1)(a) or (b),

(c)	that all applicable fields on the application form and required schedules are completed,

(d)	that all attachments indicated as being attached to the application are submitted with the application, and

(e)	that the application be accompanied by the types and quantities of plans and specifications that are prescribed by the applicable by-law, resolution or regulation made under Clause 7 (1) (b) of the Act.

(6)  The time period described in Sentences (1) to (3) shall begin on the day following the later of

(a)	the day on which an application meeting the requirements of Sentence (5) is submitted to the chief building official, and

(b)	the day on which payment is made of all fees that are required, under a by-law, regulation or resolution made under Clause 7 (1) (c) of the Act, to be paid when the application is made.

(7)  Subject to Sentences (8) and (9), the time periods described in Column 3 of Table 2.4.1.1B. shall not include Saturdays, holidays and all other days when the offices of the principal authority are not open for the transaction of business with the public.

(8)  The time period in Sentence (9) applies where

(a)	an application is made for the construction of a building that is served by a sewage system,

(b)	construction is proposed in respect of the sewage system that serves the building, and

(c)	a board of health, conservation authority, planning board or the council of an upper-tier municipality is responsible for the enforcement of the provisions of the Act and this Code related to the sewage system under Section 3.1 of the Act or pursuant to an agreement under Section 6.2 of the Act.

(9)  The time period described in Sentences (1) to (3) for an application referred to in Clause (8)(a) shall begin on the day following the latest of

(a)	the day on which an application meeting the requirements of Sentence (5) is submitted to the chief building official,

(b)	the day on which payment is made of all fees that are required, under a by-law, regulation or resolution made under Clause 7 (1) (c) of the Act, to be paid when the application is made, and

(c)	the day on which a permit for the construction of the sewage system referred to in Clause (8)(b) is issued.

Table 2.4.1.1B.

Period Within Which Permit Shall be Issued or Refused Forming Part of Article 2.4.1.1B.

| Row Number | Class of Building | Time period |
| --- | --- | --- |
| 1 | (a) A detached house, semi-detached house, townhouse, or row house where no dwelling unit is located above another dwelling unit. | 10 days |
|  | (b) A detached structure that serves a building described in Clause (a) and does not exceed 50 m2 in building area. |  |
|  | (c) A tent to which Section 3.13. applies. |  |
|  | (d) A sign to which Section 3.14. applies. |  |
| 2 | (a) Buildings described in Clauses 2.1.1.3.(1)(a), (b) and (c), other than buildings described in Column 2 of any of Rows 1 and 4 of this Table. | 15 days |
|  | (b) Farm buildings that do not exceed 600 m2 in building area. |  |
| 3 | (a) Buildings described in Clause 2.1.1.2.(1)(a) or (b), other than buildings described in Column 2 of any of Rows 1 and 4 of this Table. | 20 days |
|  | (b) Farm buildings exceeding 600 m2 in building area. |  |
| 4 | (a) Post-disaster buildings. | 30 days |
|  | (b) Buildings to which Subsection 3.2.6. or any provision in Articles 3.2.8.3. to 3.2.8.11. applies. |  |
| Column 1 | Column 2 | Column 3 |

2.4.1.2. Permits under Section 10 of the Act

(1)  Except as provided in Sentence (2), the following changes in use of a building or part of a building constitute an increase in hazard for the purposes of Section 10 of the Act and require a permit under Section 10 of the Act:

(a)	a change of the major occupancy of all or part of a building that is designated with a “Y” in Table 2.4.1.2. takes place,

(b)	a suite of a Group C major occupancy is converted into more than one suite of Group C major occupancy,

(b.1)	a suite or part of a suite of a Group A, Division 2 or a Group A, Division 4 major occupancy is converted to a gaming premise,

(c)	a farm building or part of a farm building is changed to a major occupancy, or

(d)	the use of a building or part of a building is changed and the previous major occupancy of the building or part of the building cannot be determined.

(2)  A person is exempt from the requirement to obtain a permit under Section 10 of the Act where the change in use of the building or part of the building will result from proposed construction and a permit under Section 8 of the Act has been issued in respect of such construction.

(3)  A person is exempt from the requirement to obtain a permit under Section 10 of the Act for the change of use of a building in unorganized territory.

Table 2.4.1.2.

Permit Required for Change of Use

Forming Part of Sentence 2.4.1.2.(1)(1)

|  |  | FROM(2) |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | A-1 | A-2 | A-3 | A-4 | B-1 | B-2 | B-3 | C | D | E | F-1 | F-2 | F-3 |
| TO(3) | A-1 | N(5) | Y | Y | N(5) | Y | Y | Y | Y | Y | Y | Y | Y | Y |
|  | A-2 | Y | N(5) | Y | N(5) | Y | Y | Y | Y | Y | Y | Y | Y | Y |
|  | A-3 | Y | Y | N(5) | N(5) | Y | Y | Y | Y | Y | Y | Y | Y | Y |
|  | A-4 | Y | Y | Y | N(5) | Y | Y | Y | Y | Y | Y | Y | Y | Y |
|  | B-1 | Y | Y | Y | N(5) | N(5) | Y | Y | Y | Y | Y | Y | Y | Y |
|  | B-2 | Y | Y | Y | N(5) | Y | N(5) | Y | Y | Y | Y | Y | Y | Y |
|  | B-3 | Y | Y | Y | N(5) | Y | N(5) | N(5) | Y | Y | Y | Y | Y | Y |
|  | C | Y | Y | Y | N(5) | Y | N(5) | N(5) | (4) | Y | Y | Y | Y | Y |
|  | D | N(5) | N(5) | Y | N(5) | Y | N(5) | N(5) | Y | N(5) | Y | Y | N(5) | N(5) |
|  | E | Y | Y | Y | N(5) | Y | Y | Y | Y | Y | N(5) | Y | Y | Y |
|  | F-1 | Y | Y | Y | N(5) | Y | Y | Y | Y | Y | Y | N(5) | Y | Y |
|  | F-2 | Y | Y | Y | N(5) | Y | Y | Y | Y | Y | Y | N(5) | N(5) | Y |
|  | F-3 | Y | N(5) | Y | N(5) | Y | Y | Y | Y | N(5) | N(5) | N(5) | N(5) | N(5) |

Notes to Table 2.4.1.2.:

(1) See Clauses 2.4.1.2.(1)(a), 3.15.1.1.(1)(a) and 9.41.1.1.(1)(a).

(2) Major occupancy of all or part of a building before change of use.

(3) Major occupancy of all or part of a building after change of use.

(4) See Clauses 2.4.1.2.(1)(b), 3.15.1.1.(1)(b), 9.41.1.1.(1)(b) and 11.4.2.3.(1)(b).

(5) “N” is only applicable where the major occupancy of the entire suite is changed.

2.4.1.3.  Conditional Permits

(1)  The chief building official shall not issue a conditional permit for any stage of construction under Subsection 8 (3) of the Act unless compliance with the following applicable laws has been achieved in respect of the construction of the proposed building:

(a)	regulations made under Clause 28 (1) (e) of the Conservation Authorities Act,

(b)	Subsection 5 (3) of the Environmental Assessment Act,

(c)	Reserved

(d)	Subsection 24 (3) of the Niagara Escarpment Planning and Development Act,

(e)	Subsection 27 (3), subsection 30 (2), sections 33, 34 and 34.5, subsection 34.7 (2) and sections 40.1 and 42 of the Ontario Heritage Act.

(f)	Revoked:  O. Reg. 305/03, s. 7 (1).

(2)  For the purposes of issuing a conditional permit under Subsection 8 (3) of the Act, a person is exempt from the requirement in Clause 8 (3) (a) of the Act of compliance with by-laws passed under Sections 34 and 38 of the Planning Act where

(a)	a committee of adjustment has made a decision under Section 45 of the Planning Act authorizing one or more minor variances from the provisions of any by-laws made under Sections 34 and 38 of that Act,

(b)	such minor variance or variances result in the achievement of full compliance with such by-laws, and

(c)	no person informed the committee of adjustment of objections to the minor variances either in writing or in person at the hearing of the application.

(3)  For the purposes of issuing a conditional permit under Subsection 8 (3) of the Act, a person is exempt from the requirement in Clause 8 (3) (a) of the Act of compliance with by-laws passed under Sections 34 and 38 of the Planning Act where the construction in respect of which the conditional permit is issued is required in order to comply with an order issued under Subsection 21 (1) of the Fire Protection and Prevention Act, 1997 or under Subsection 15.9 (4) of the Building Code Act, 1992.

(4)  A permit issued under Subsection 8 (3) of the Act shall indicate its conditional nature.

2.4.2. Site Documents

2.4.2.1.  Permit Posting

(1)  Where a permit has been issued pursuant to the Act, the person to whom it is issued shall have the permit or a copy thereof posted at all times during construction or demolition in a conspicuous place on the property in respect of which the permit was issued.

2.4.2.2.  Documentation on Site

(1)  The person in charge of the construction of the building shall keep and maintain on the site of the construction

(a)	at least one copy of drawings and specifications certified by the chief building official or a person designated by the chief building official to be a copy of those submitted with the application for the permit to construct the building, together with changes that are authorized by the chief building official or a person designated by the chief building official, and

(b)	authorization or facsimiles thereof received from the Building Materials Evaluation Commission, including specified terms and conditions.

2.4.3. Occupancy of Unfinished Building

2.4.3.1.  Occupancy Permit

(1)  Except as permitted in Sentence 2.4.3.2.(1), a person may occupy or permit to be occupied any building or part thereof that has not been fully completed at the date of occupation where the chief building official or a person designated by the chief building official has issued a permit authorizing occupation of the building or part thereof prior to its completion in accordance with Sentence (2).

(2)  The chief building official or a person designated by the chief building official shall issue a permit authorizing occupation of a building, where

(a)	the structure of the building or part thereof is completed to the roof,

(b)	the enclosing walls of the building or part thereof are completed to the roof,

(c)	the walls enclosing the space to be occupied are completed, including balcony guards,

(d)	all required fire separations and closures are completed on all storeys to be occupied,

(e)	all required exits are completed and fire separated including all doors, door hardware, self-closing devices, balustrades and handrails from the uppermost floor to be occupied down to grade level and below if an exit connects with lower storeys,

(f)	all shafts including closures are completed to the floor-ceiling assembly above the storey to be occupied and have a temporary fire separation at such assembly,

(g)	measures have been taken to prevent access to parts of the building and site that are incomplete or still under construction,

(h)	floors, halls, lobbies and required means of egress are kept free of loose materials and other hazards,

(i)	if service rooms should be in operation, required fire separations are completed and all closures installed,

(j)	all building drains, building sewers, water systems, drainage systems and venting systems are complete and tested as operational for the storeys to be occupied,

(k)	required lighting, heating and electrical supply are provided for the suites, rooms and common areas to be occupied,

(l)	required lighting in corridors, stairways and exits is completed and operational up to and including all storeys to be occupied,

(m)	required standpipe, sprinkler and fire alarm systems are complete and operational up to and including all storeys to be occupied, together with required pumper connections for such standpipes and sprinklers,

(n)	required fire extinguishers have been installed on all storeys to be occupied,

(o)	main garbage rooms, chutes and ancillary services thereto are completed to storeys to be occupied,

(p)	required fire fighting access routes have been provided and are accessible, and

(q)	the sewage system has been completed and is operational.

(3)  Where a registered code agency has been appointed to perform the functions described in Clause 4.1 (4) (b) or (c) of the Act in respect of the construction of the building, the chief building official or a person designated by the chief building official shall issue the permit referred to in Sentence (2) after receipt of a certificate for the occupancy of a building not fully completed issued by the registered code agency in respect of the building.

2.4.3.2.  Conditions for Residential Occupancy

(1)  A person may occupy or permit to be occupied a building intended for residential occupancy that has not been fully completed at the date of occupation provided that

(a)	the building

(i)	is not more than 3 storeys in building height and 600 m2 in building area,

(ii)	has not more than 1 dwelling unit above another dwelling unit,

(iii)	has not more than 2 dwelling units sharing a common means of egress, and

(iv)	has no accommodation for tourists,

(b)	the following building components and systems are complete, operational and inspected:

(i)	required exits, handrails and guards, fire alarm and detection systems, and fire separations,

(ii)	required exhaust fume barriers and self-closing devices on doors between an attached or built-in garage and a dwelling unit, and

(iii)	water supply, sewage disposal, lighting and heating systems,

(c)	the following building components and systems are complete, operational, inspected and tested:

(i)	water systems,

(ii)	building drains and building sewers, and

(iii)	drainage systems and venting systems, and

(d)	where applicable, the building conforms to Article 2.1.1.8.

2.4.3.3.  Notification

(1)  Where a person has occupied or permitted the occupancy of a building under this Subsection, such person shall notify the chief building official forthwith upon completion of the building.

2.4.4. Fire Department Inspection

2.4.4.1.  Fire Department Approval

(1)  Subject to Sentence (2), if the council of a municipality assigns specific responsibility for the enforcement of any portion of this Code respecting fire safety matters to an inspector who is the chief of the fire department of the municipality, the chief building official shall not issue a permit to construct a building unless the inspector approves the drawings submitted with the application for the permit as complying with that portion of this Code.

(2)  If a registered code agency has been appointed under Clause 4.1 (4) (a) or (c) of the Act

(a)	a municipality shall not assign responsibility under Sentence (1) to the chief of the fire department with respect to a building for which the registered code agency has been appointed, and

(b)	any assignment of responsibility under Sentence (1) with respect to a building for which the registered code agency is appointed shall be cancelled as of the date of the appointment.

2.4.5. Notices and Inspections

2.4.5.1.  Prescribed Notices

(1)  This Article sets out the notices that are required under Section 10.2 of the Act.

(2)  The person to whom a permit under Section 8 of the Act is issued shall notify the chief building official or, where a registered code agency is appointed under the Act in respect of the construction to which the notice relates, the registered code agency of:

(a)	readiness to construct footings,

(b)	substantial completion of footings and foundations prior to commencement of backfilling,

(c)	substantial completion of structural framing and ductwork and piping for heating and air-conditioning systems, if the building is within the scope of Part 9,

(d)	substantial completion of structural framing and roughing-in of heating, ventilation, air-conditioning and air-contaminant extraction equipment, if the building is not a building to which Clause (c) applies,

(e)	substantial completion of insulation, vapour barriers and air barriers,

(f)	substantial completion of all required fire separations and closures and all fire protection systems including standpipe, sprinkler, fire alarm and emergency lighting systems,

(g)	substantial completion of fire access routes,

(h)	readiness for inspection and testing of:

(i)	building sewers and building drains,

(ii)	water service pipes,

(iii)	fire service mains,

(iv)	drainage systems and venting systems,

(v)	the water distribution system, and

(vi)	plumbing fixtures and plumbing appliances,

(i)	readiness for inspection of suction and gravity outlets, covers and suction piping serving outlets of an outdoor pool described in Clause 2.1.2.1.(1)(h), a public pool or a public spa,

(j)	substantial completion of the circulation/recirculation system of an outdoor pool described in Clause 2.1.2.1.(1)(h), a public pool or public spa and substantial completion of the pool before it is first filled with water,

(k)	readiness to construct the sewage system,

(l)	substantial completion of the installation of the sewage system before the commencement of backfilling,

(m)	substantial completion of installation of plumbing not located in a structure, before the commencement of backfilling, and

(n)	completion of construction and installation of components required to permit the issue of an occupancy permit under Sentence 2.4.3.1.(2) or to permit occupancy under Sentence 2.4.3.2.(1), if the building or part of the building to be occupied is not fully completed.

2.4.5.2.  Additional Notices

(1)  A principal authority may pass a by-law or resolution or make a regulation under Clause 7 (1) (e) of the Act, as part of its responsibility for the enforcement of the Act, in order to establish time periods within which notice of one or more of the following stages of construction must be given:

(a)	commencement of construction of the building,

(b)	substantial completion of structural framing for each storey, if the building is a type of building that is within the scope of Parts of this Code other than Part 9,

(c)	commencement of construction of:

(i)	masonry fireplaces and masonry chimneys,

(ii)	factory-built fireplaces and allied chimneys,

(iii)	stoves, ranges, space heaters and add-on furnaces using solid fuels and allied chimneys,

(d)	substantial completion of interior finishes,

(e)	substantial completion of heating, ventilating, air-conditioning and air-contaminant extraction equipment,

(f)	substantial completion of exterior cladding,

(g)	substantial completion of site grading,

(h)	substantial completion of the pool deck and dressing rooms for a public pool or public spa and readiness for inspection of the emergency stop system for a public pool or public spa, and

(i)	completion and availability of drawings of the building as constructed.

(2)  The person to whom a permit under Section 8 of the Act is issued shall notify the chief building official or, if a registered code agency is appointed under the Act in respect of the construction to which the notice relates, the registered code agency of the stages of construction for which a time period for giving notice is required under Sentence (1).

2.4.5.3.  Prescribed Inspections

(1)  Except as provided in Sentence (2), an inspector or registered code agency, as the case may be, shall, not later than two days after receipt of a notice given under Sentence 2.4.5.1.(2), undertake a site inspection of the building to which the notice relates.

(2)  Where a notice given under Sentence 2.4.5.1.(2) relates to matters described in Clause 2.4.5.1.(2)(k) or (l), an inspector or registered code agency, as the case may be, shall, not later than five days after receipt of the notice, undertake a site inspection of the sewage system to which the notice relates.

(3)  When undertaking an inspection required under Sentence (1) or (2), the inspector or registered code agency, as the case may be, may consider reports concerning whether the building or a part of the building complies with the Act or this Code.

(4)  The time periods referred to in Sentences (1) and (2) shall begin on the day following the day on which the notice is given.

(5)  The time periods referred to in Sentences (1) and (2) shall not include Saturdays, holidays and all other days when the offices of the principal authority are not open for the transaction of business with the public.

2.4.5.4.  Exemption

(1)  A person is exempt from the requirement in Sentences 2.4.5.1.(2) and 2.4.5.2.(2) to give notice to the chief building official in respect of construction if

(a)	a permit in respect of the construction was issued to the person under Section 8 of the Act before July 1, 2005, and

(b)	the person notifies the chief building official in accordance with

(i)	Sentence 2.4.5.1.(1) as it read on June 30, 2005, and

(ii)	the by-law passed by the municipality under Clause 7 (e) of the Act, as the by-law read on June 30, 2005.

(2)  Article 2.4.5.3. does not apply to construction to which Sentence (1) relates.

2.4.5.5.  Construction of Sewage Systems

(1)  The following information is prescribed for the purposes of Subsection 15.12 (3) of the Act and must be provided to the chief building official before the commencement of the construction of a sewage system:

(a)	the information described in Sentence 2.18.4.1.(2) as it relates to:

(i)	the person registered under Article 2.18.3.2., and

(ii)	the person with the qualifications described in Clause 2.18.3.2.(1)(a) who will supervise construction on-site of the sewage system, and

(b)	the name and telephone number of the representative of the person described in Subclause (a)(i) who may be contacted by the chief building official in respect of the construction of the sewage system.

2.4.5.6.  Orders

(1)  An order issued after June 30, 2005 under Subsection 12 (2), 13 (1), 13 (6) or 14 (1) or Clause 18 (1) (f) of the Act shall be in a form approved by the Minister.

2.4.6. As Constructed Plans

2.4.6.1.  Application

(1)  Where the council of a municipality has passed a by-law pursuant to Subsection 7 (g) of the Act, the chief building official may require that as constructed plans for the whole of, or any part or system of, a building or any class of buildings be provided by the persons responsible for the construction.

Section 2.5. Climatic Data

2.5.1. Climatic and Seismic Values

2.5.1.1.  Design Values

(1)  The climatic and seismic values required for the design of buildings under this Code shall be in conformance with the values provided in Table 2.5.1.1.

Table 2.5.1.1.

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251au.tif

Table 2.5.1.1. (Cont’d)

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251bu.tif

Table 2.5.1.1. (Cont’d)

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251cu.tif

Table 2.5.1.1. (Cont’d)

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251du.tif

Table 2.5.1.1. (Cont’d)

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251eu.tif

Table 2.5.1.1. (Cont’d)

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251fu.tif

Table 2.5.1.1. (Cont’d)

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251gu.tif

Table 2.5.1.1. (Cont’d)

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251hu.tif

Table 2.5.1.1. (Cont’d)

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251iu.tif

Table 2.5.1.1. (Cont’d)

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251ju.tif

Table 2.5.1.1. (Cont’d)

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251ku.tif

Table 2.5.1.1. (Cont’d)

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251lu.tif

Table 2.5.1.1. (Cont’d)

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251mu.tif

Table 2.5.1.1. (Cont’d)

Design Data For Selected Locations in Ontario

Forming part of Sentence 2.5.1.1.(1)

Insert regs\graphics\1997\403\403251nu.tif

Section 2.6. Referenced Documents

2.6.1. Application

2.6.1.1.  Limitation

(1)  The provisions of referenced documents in this Code apply only to the extent that they relate to buildings or to structures designated in Subsection 2.1.2.

2.6.2. Conflicting Requirements

2.6.2.1.  Governing Documents

(1)  In the case of conflict between the provisions of this Code and those of a referenced document, the provisions of this Code shall govern.

2.6.3. Effective Date

2.6.3.1. Edition of Standard

(1)  Unless otherwise specified herein, the documents referenced in this Code shall include all amendments, revisions and supplements effective to September 1, 1997.

2.6.3.2.  Designated Editions

(1)  Where documents are referenced in this Code, they shall be in the editions designated in Column 2 of Table 2.6.3.2.

Table 2.6.3.2.

Documents Referenced in the Ontario Building Code

Forming Part of Sentence 2.6.3.2.(1)

| Issuing Agency | Document Number | Title of Document | Code Reference |
| --- | --- | --- | --- |
| ANSI/ ASME | A112.19.8M-1987 | Suction Fittings for Use in Swimming Pools, Wading Pools, Spas, Hot Tubs, and Whirlpool Bathtub Appliances | 3.11A.4.1.(9) |
| ANSI/ ASME | B16.3-1992 | Malleable Iron Threaded Fittings (Classes 150 and 300) | 7.2.6.6.(1) |
| ANSI/ ASME | B16.4-1992 | Cast Iron Threaded Fittings (Classes 125 and 250) | 7.2.6.5.(1) Table 7.2.11.2. |
| ANSI/ ASME | B16.12-1991 | Cast Iron Threaded Drainage Fittings | 7.2.6.3.(1) |
| ANSI/ ASME | B16.15-1985 | Cast Bronze Threaded Fittings (Classes 125 and 250) | 7.2.7.3.(1) |
| ANSI | B16.18-1984 | Cast Copper Alloy Solder Joint Pressure Fittings | 7.2.7.6.(1) 7.2.7.6.(2) Table 7.2.11.2. |
| ANSI/ ASME | B16.22-1989 | Wrought Copper and Copper Alloy Solder Joint Pressure Fittings | 7.2.7.6.(1) |
| ANSI/ ASME | B16.24-1991 | Bronze Pipe Flanges and Flanged Fittings (Class 150 and 300) | 7.2.7.2.(1) |
| ANSI/ ASME | B16.26-1988 | Cast Copper Alloy Fittings for Flared Copper Tubes | 7.2.7.7.(1) 7.2.7.7.(2) Table 7.2.11.2. |
| ANSI/ ASME | B16.29-1986 | Wrought Copper and Wrought Copper Alloy Solder Joint Drainage Fittings — DWV | 7.2.7.5.(1) |
| ANSI | B18.6.1-1981 | Slotted and Recessed Wood Screws (Inch Series) | 9.23.3.1.(2) |
| ANSI | Z21.22-1986 | Relief Valves and Automatic Shut-off Devices for Hot Water Supply Systems | 7.2.10.11.(1) |
| ANSI/ ASHRAE | 62-1989 | Ventilation for Acceptable Indoor Air Quality | 6.2.2.1.(2) |
| ANSI/ AWWA | C104/A21.4-90 | Cement-Mortar Lining for Ductile-Iron and Gray-Iron Pipe and Fittings for Water | 7.2.6.4.(2) |
| ANSI/ AWWA | C110/A21.10-93 | Ductile-Iron and Gray-Iron Fittings, 3 in. Through 48 in., for Water and Other Liquids | 7.2.6.4.(3) Table 7.2.11.2. |
| ANSI/ AWWA | C111/A21.11- 90 | Rubber-Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings | 7.2.6.4.(4) Table 7.2.11.2. |
| ANSI/ AWWA | C151/A21.51- 91 | Ductile-Iron Pipe, Centrifugally Cast in Metal Molds or Sand-Lined Molds, for Water or Other Liquids | 7.2.6.4.(1) Table 7.2.11.2. |
| ASTM | A53-93a | Pipe, Steel, Black and Hot-Dipped, Zinc-Coated Welded and Seamless | 7.2.6.7.(4) |
| ASTM | A123-89A | Zinc (Hot Dip Galvanized) Coatings on Iron and Steel Products | Table 9.20.16.1. |
| ASTM | A153-82 (1987) | Specification for Zinc Coating (Hot-Dip) on Iron and Steel Hardware | Table 9.20.16.1. |
| ASTM | A252-93 | Welded and Seamless Steel Pipe Piles | 4.2.3.8.(1) |
| ASTM | A283/A283M-93a | Low and Intermediate Tensile Strength Carbon Steel Plates, Shapes, and Bars | 4.2.3.8.(1) |
| ASTM | A518M-92 | Specification for Corrosion-Resistant High-Silicon Iron Castings | 7.2.8.1.(1) |
| ASTM | A570/A570M-93 | Hot-Rolled Carbon Steel Sheet and Strip, Structural Quality | 4.2.3.8.(1) |
| ASTM | A611-94 | Steel, Cold-Rolled Sheet, Carbon Structural | 4.2.3.8.(1) |
| ASTM | A653-94 | Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvanealed) by the Hot-Dip Process | 9.3.3.2.(1) |
| ASTM | A924-94 | Steel Sheet, Metallic-Coated by the Hot-Dip Process | 9.3.3.2.(1) |
| ASTM | B32-94 | Solder Metal | 7.2.9.2.(2) |
| ASTM | B42-93 | Seamless Copper Pipe, Standard Sizes | 7.2.7.1.(1) |
| ASTM | B43-94 | Seamless Red Brass Pipe, Standard Sizes | 7.2.7.1.(2) |
| ASTM | B68-92 | Seamless Copper Tube, Bright, Annealed | 7.2.7.4.(3) |
| ASTM | B88-93a | Seamless Copper Water Tube | 7.2.7.4.(1) Table 7.2.11.2. |
| ASTM | B306-92 | Copper Drainage Tube (DWV) | 7.2.7.4.(1) |
| ASTM | C4-62 (1991) | Clay Drain Tile | 9.14.3.1.(1) |
| ASTM | C5-79 (1992) | Quicklime for Structural Purposes | 9.20.3.1.(1) |
| ASTM | C27-93 | Classification for Fire Clay and High Alumina Refractory Brick | 9.21.3.4.(1) |
| ASTM | C36 | Gypsum Wallboard | 3.1.5.11.(4) 9.29.5.2.(1) |
| ASTM | C37 | Gypsum Lath | 9.29.5.2.(1) |
| ASTM | C126-94 | Ceramic Glazed Structural Clay Facing Tile, Facing Brick, and Solid Masonry Units | 9.20.2.1.(1) |
| ASTM | C207-91 (1992) | Hydrated Lime for Masonry Purposes | 9.20.3.1.(1) |
| ASTM | C212-93 | Structural Clay Facing Tile | 9.20.2.1.(1) |
| ASTM | C411-82 (1992) | Hot-Surface Performance of High-Temperature Thermal Insulation | 6.2.3.4.(3) 6.2.9.2.(2) |
| ASTM | C412M-94 | Concrete Drain Tile | 9.14.3.1.(1) |
| ASTM | C442 | Gypsum Backing Board and Coreboard | 3.1.5.11.(4) 9.29.5.2.(1) |
| ASTM | C444M-94 | Perforated Concrete Pipe (Metric) | 9.14.3.1.(1) |
| ASTM | C588 | Gypsum Base for Veneer Plaster | 9.29.5.2.(1) 3.1.5.11.(4) |
| ASTM | C630 | Water Resistant Gypsum Board Backing | 3.1.5.11.(4) 9.29.5.2.(1) |
| ASTM | C700-91 | Vitrified Clay Pipe, Extra Strength, Standard Strength and Perforated | 9.14.3.1.(1) |
| ASTM | C931 | Exterior Gypsum Soffirt Board | 3.1.5.11.(4) 9.29.5.2.(1) |
| ASTM | C960 | Predocorated Gypsum Board | 3.1.5.11.(4) 9.29.5.2.(1) |
| ASTM | C1002-93 | Steel Drill Screws for the Application of Gypsum Board or Metal Plaster Bases | 9.24.1.4. 9.29.5.7. |
| ASTM | C1053-90 | Borosilicate Glass Pipe and Fittings for Drain, Waste and Vent (DWV) Applications | 7.2.8.1.(1) |
| ASTM | D374-94 | Thickness of Solid Electrical Insulation | 3.14.4.1.(1)(c) |
| ASTM | D568-77 | Rate of Burning and/or Extent and Time of Burning of Flexible Plastics in a Vertical Position | 3.14.4.1.(1)(b) 3.3.4.6.(1) 9.11.1.1.(1) |
| ASTM | D635-91 | Rate of Burning and/or Extent and Time of Burning of Self- Supporting Plastics in a Horizontal Position | 3.14.4.1.(1)(a) |
| ASTM | D2178-89 | Asphalt Glass Felt Used in Roofing and Waterproofing | 5.6.1.2.(1) |
| ASTM | D2898-94 | Test Method for Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing | 3.1.5.5.(4) 3.1.5.5.(5) |
| ASTM | D3261-93 | Butt Heat Fusion Polyethylene (PE) Plastic Fittings for Polyethylene (PE) Plastic Pipe and Tubing | 7.2.5.5.(3) |
| ASTM | E90-90 | Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions | 3.3.4.6.(1) 9.11.1.1.(1) |
| ASTM | E96-94 | Test Methods for Water Vapour Transmission of Materials | 5.5.1.2.(4) |
| ASTM | E283-91 | Standard Test Method for Rate of Air Leakage through Exterior Windows, Curtain Walls and Doors | 9.6.5.4.(1) 9.6.5.5.(1) 9.7.1.7.(1) 9.38.6.1.(1) |
| ASTM | E336-90 | Measurement of Airborne Sound Insulation in Buildings | 3.3.4.6.(1) 9.11.1.1.(1) |
| ASTM | E413-1994 | Classification for Rating Sound Insulation | 3.3.4.6.(1) 9.11.1.1.(1) |
| ASTM | F476-1991 | Standard Test Methods For Security of Swinging Door Assemblies | 9.6.8.10.(1) |
| AWPA | M4-91 | Care of Preservative-Treated Wood Products | 4.2.3.2.(2) |
| BNQ | NQ3624-115-1991 | Thermo-Plastic Pipe-Flexible Corrugated Tubing and Fitting for Soil Drainage | 9.14.3.1.(1) |
| CGA | CAN1-4.4-M80 | Temperature, Pressure, Temperature and Pressure Relief Valves and Vacuum Relief Valves | 7.2.10.11.(1) |
| CSA | CAN/CGA-6.19-M93 (R1999) | Residential Carbon Monoxide Detectors | 6.2.5A.3.(1) 9.33.4.3.(1) |
| CGSB | CAN/CGSB-1.501-M89 | Method of Permeance of Coated Wallboard | 5.5.1.2.(3) 9.25.4.2.(5) |
| CGSB | CAN/CGSB-7.1-86 | Cold Formed Steel Framing Components | 9.24.1.2.(1) |
| CGSB | CAN/CGSB-7.2-94 | Adjustable Steel Columns | 9.17.3.4.(1) |
| CGSB | CAN/CGSB-10.3-92 | Air Setting Refractory Mortar | 9.21.3.4.(2) 9.21.3.9.(1) 9.22.2.2.(2) |
| CGSB | CAN/CGSB-11.3-M87 | Hardboard | 9.27.10.1.(2) 9.29.7.1.(1) 9.30.2.2.(1) |
| CGSB | CAN/CGSB-11.5-M87 | Hardboard, Precoated, Factory Finished, for Exterior Cladding | 9.27.10.1.(1) |
| CGSB | CAN/CGSB-12.1-M90 | Tempered or Laminated Safety Glass | 3.3.1.18.(2) 3.4.6.14.(3) 9.6.6.2.(2) 9.7.3.1.(1) 9.8.8.7.(1) |
| CGSB | CAN/CGSB-12.2-M91 | Flat, Clear, Sheet Glass | 9.7.3.1.(1) |
| CGSB | CAN/CGSB-12.3-M91 | Flat, Clear, Float Glass | 9.7.3.1.(1) |
| CGSB | CAN/CGSB-12.4-M91 | Heat Absorbing Glass | 9.7.3.1.(1) |
| CGSB | CAN/CGSB-12.5-M86 | Mirrors, Silvered | 9.6.6.3.(2) |
| CGSB | CAN/CGSB-12.8-M90 | Insulating Glass Units | 9.7.3.1.(1) |
| CGSB | CAN/CGSB-12.10-M76 | Glass, Light and Heat Reflecting | 9.7.3.1.(1) |
| CGSB | CAN/CGSB-12.11-M90 | Wired Safety Glass | 3.4.6.14.(3) 9.6.6.2.(2) 9.7.3.1.(1) 9.8.8.7.(1) 4.3.6.1.(1) |
| CGSB | CAN/CGSB-12.20-M89 | Structural Design of Glass for Buildings | 3.3.1.18.(2) 9.7.3.2.(1) |
| CGSB | 19-GP-5M-1976 | Sealing Compound, One Component, Acrylic Base, Solvent Curing | 9.27.4.2.(2) |
| CGSB | CAN/CGSB-19.13-M87 | Sealing Compound, One Component, Elastomeric, Chemical Curing | 9.27.4.2.(2) |
| CGSB | 19-GP-14M-1976 | Sealing Compound, One Component, Butyl-Polyisobutylene Polymer Base, Solvent Curing | 9.27.4.2.(2) |
| CGSB | CAN/CGSB-19.22-M89 | Mildew Resistant Sealing Compound for Tubs and Tile | 9.29.10.5.(1) |
| CGSB | CAN/CGSB-19.24-M90 | Multi-Component, Chemical Curing Sealing Compound | 9.27.4.2.(2) |
| CGSB | CAN/CGSB-34.4-M89 | Siding, Asbestos-Cement, Shingles and Clapboards | 9.27.8.1.(1) |
| CGSB | CAN/CGSB-34.5-M89 | Sheets, Asbestos-Cement, Corrugated | 9.27.8.1.(1) |
| CGSB | CAN/CGSB-34.9-M87 | Pipe, Asbestos-Cement, Sewer | 7.2.5.1.(2) |
| CGSB | CAN/CGSB-34.14-M89 | Sheets, Asbestos-Cement, Decorative | 9.27.8.1.(1) |
| CGSB | CAN/CGSB-34.16-M89 | Sheets, Asbestos-Cement, Flat, Fully Compressed | 9.27.8.1.(1) |
| CGSB | CAN/CGSB-34.17-M89 | Sheets, Asbestos-Cement, Flat, Semicompressed | 9.27.8.1.(1) |
| CGSB | CAN/CGSB-34.21-M89 | Panels, Sandwich, Asbestos-Cement with Insulating Cores | 9.27.8.1.(1) |
| CGSB | CAN/CGSB-34.22-M87 | Pipe, Asbestos-Cement, Drain | 7.2.5.1.(1) 9.14.3.1.(1) |
| CGSB | CAN/CGSB-34.23-M87 | Pipe, Asbestos-Cement, Sewer, House Connection | 7.2.5.1.(2) |
| CGSB | CAN/CGSB-37.1-M89 | Chemical Emulsified Type, Emulsified Asphalts for Dampproofing | 9.13.2.1.(1) |
| CGSB | CAN/CGSB-37.2-M88 | Emulsified Asphalt, Mineral Colloid Type, Unfilled, for Dampproofing and Waterproofing and for Roof Coatings | 9.13.2.1.(1) |
| CGSB | CAN/CGSB-37.3-M89 | Application of Emulsified Asphalts for Dampproofing or Waterproofing | 9.13.1.4.(1) |
| CGSB | CAN/CGSB-37.4-M89 | Fibrated, Cutback Asphalt, Lap Cement for Asphalt Roofing | 9.26.2.1.(1) |
| CGSB | CAN/CGSB-37.5-M89 | Cutback Asphalt Plastic Cement | 9.26.2.1.(1) |
| CGSB | 37-GP-6Ma-1983 | Asphalt, Cutback, Unfilled, for Dampproofing | 9.13.2.1.(1) |
| CGSB | CAN/CGSB-37.8-M88 | Asphalt, Cutback, Filled, for Roof Coating | 9.26.2.1.(1) |
| CGSB | 37-GP-9Ma-1983 | Primer, Asphalt, Unfilled, for Asphalt Roofing, Dampproofing and Waterproofing | 5.6.1.2.(1) 9.26.2.1.(1) |
| CGSB | 37-GP-12Ma-1984 | Application of Unfilled Cutback Asphalt for Dampproofing | 9.13.1.4.(1) |
| CGSB | CAN/CGSB-37.16-M89 | Filled Cutback Asphalt for Dampproofing and Waterproofing | 9.13.2.1.(1) |
| CGSB | 37-GP-18Ma-1985 | Tar, Cutback, Unfilled, for Dampproofing | 9.13.2.1.(1) |
| CGSB | 37-GP-18Ma-1985 | Tar, Cutback, Fibrated, For Roof Coating | 9.26.2.1.(1) |
| CGSB | CAN/CGSB-37.22-M89 | Application of Unfilled Cutback Tar Foundation Coating for Dampproofing | 9.13.1.4.(1) |
| CGSB | 37-GP-36M-1976 | Application of Filled Cutback Asphalt for Dampproofing or Waterproofing | 5.8.2.3 (1) |
| CGSB | 37-GP-37M-1977 | Application of Hot Asphalt for Dampproofing or Waterproofing | 5.8.2.3 (1) |
| CGSB | CAN/CGSB-37.50-M89 | Hot Applied, Rubberized Asphalt for Roofing and Waterproofing | 9.26.2.1.(1) |
| CGSB | CAN/CGSB-37.51-M90 | Application for Hot Applied Rubberized Asphalt for Roofing and Waterproofing | 5.8.2.3.(1) 9.26.15.1. (1) |
| CGSB | 37-GP-52M-1984 | Roofing and Waterproofing Membrane, Sheet Applied, Elastomeric | 9.26.2.1.(1) |
| CGSB | 37-GP-54M-1979 | Roofing and Waterproofing Membrane, Sheet Applied, Flexible, Polyvinyl Chloride | 9.26.2.1.(1) |
| CGSB | 37-GP-55M-1979 | Application of Sheet Applied Flexible Polyvinyl Chloride Roofing Membrane | 9.26.16.1.(1) |
| CGSB | 37-GP-56M-1980 | Membrane, Modified, Bituminous, Prefabricated, and Reinforced for Roofing | 9.13.2.1.(1) 9.26.2.1.(1) |
| CGSB | 37-GP-64M-1977 | Mat Reinforcing, Fibrous Glass, for Membrane Waterproofing Systems and Built-up Roofing | 5.6.1.2.(1) |
| CGSB | 41-GP-6M-1983 | Sheets, Thermosetting Polyester Plastics, Glass Fiber Reinforced | 9.26.2.1.(1) |
| CGSB | 41-GP-24Ma-1983 | Siding, Soffits and Fascia, Rigid Vinyl | 9.27.13.1.(1) |
| CGSB | CAN/CGSB-51.20-M87 | Thermal Insulation, Polystyrene Boards and Pipe Covering | Table 9.23.16.2.A. 9.25.2.3.(1) |
| CGSB | 51-GP-21M-1978 | Thermal Insulation, Urethane and Isocyanurate, Unfaced | Table 9.23.16.2.A. 9.25.2.3.(1) |
| CGSB | CAN/CGSB-51.23-M92 | Spray Applied Rigid Polyurethane Cellular Plastic Thermal Insulation | 5.3.1.2.(2) 9.25.2.3.(1) |
| CGSB | CAN/CGSB-51.25-M87 | Thermal Insulation, Phenolic, Faced | 9.25.2.3.(1) |
| CGSB | CAN/CGSB-51.26-M87 | Thermal Insulation, Urethane and Isocyanurate, Boards, Faced | Table 9.23.16.2.A. 9.25.2.3.(1) |
| CGSB | 51-GP-27M-1979 | Thermal Insulation, Polystyrene, Loose Fill | 9.25.2.3.(1) |
| CGSB | CAN2-51.32-M77 | Sheathing, Membrane, Breather Type | 9.20.13.9.(1) 9.23.17.1.(1) 9.26.2.1.(1) |
| CGSB | CAN/CGSB-51.33-M89 | Vapour Barrier, Sheet, Excluding Polyethylene, for Use in Building Construction | 9.25.4.2.(4) |
| CGSB | CAN/CGSB-51.34-M86 | Vapour Barrier, Polyethylene Sheet for Use in Building Construction | 9.13.2.1.(1) 9.13.2.1.(2) 9.18.6.2.(1) 9.25.3.2.(2) 9.25.4.2.(3) |
| CGSB | CAN/CGSB-51.39-M92 | Spray Application of Rigid Polyurethane Cellular Plastic Insulation for Building Construction | 5.3.1.3.(3) 9.25.2.5.(1) |
| CGSB | CAN/CGSB-51.60-M90 | Cellulose Fibre Loose Fill Thermal Insulation | 9.25.2.3.(1) |
| CGSB | CAN/CGSB-63.14-M89 | Plastic Skylights | 9.7.7.1.(1) 9.7.7.2.(1) |
| CGSB | CAN/CGSB-82.1-M89 | Sliding Doors | 9.6.5.2.(1) |
| CGSB | CAN/CGSB-82.5-M88 | Insulated Steel Doors | 9.6.5.3.(1) |
| CGSB | CAN/CGSB-82.6-M86 | Doors, Mirrored Glass, Sliding or Folding, Wardrobe | 9.6.6.3.(1) |
| CGSB | CAN/CGSB-93.1-M85 | Sheet, Aluminum Alloy, Prefinished Residential | 9.27.12.1.(4) |
| CGSB | CAN/CGSB-93.2-M91 | Prefinished, Aluminum, Siding, Soffits and Facsia for Residential Use | 9.27.12.1.(3) |
| CGSB | CAN/CGSB-93.3-M91 | Prefinished Galvanized and Aluminum-Zinc Alloy Steel Sheet for Residential Use | 5.6.1.2.(3) 9.27.12.1.(2) |
| CGSB | CAN/CGSB-93.4-M92 | Galvanized Steel and Aluminum-Zinc Alloy Coated Steel Siding and Fascia, Residential, Prefinished | 5.6.1.2.(3) 9.27.12.1.(1) |
| CSA | CAN/CSA-A5-M93 | Portland Cement | 9.3.1.2.(1) 9.20.3.1.(1) 9.28.2.1.(1) |
| CSA | CAN/CSA-A8-M93 | Masonry Cement | 9.20.3.1.(1) |
| CSA | CAN/CSA-A23.1-94 | Concrete Materials and Methods of Concrete Construction | 4.2.3.6.(1) 4.2.3.9.(1) 9.3.1.3.(1) 9.3.1.4.(1) |
| CSA | CAN/CSA-A23.3-94 | Design of Concrete Structures | Table 4.1.9.1.B. 4.3.3.1.(1) |
| CSA | A60.1-M1976 | Vitrified Clay Pipe | 7.2.5.4.(1) |
| CSA | A60.3-M1976 | Vitrified Clay Pipe Joints | 7.2.5.4.(2) |
| CSA | CAN/CSA-A82.1-M87 | Burned Clay Brick (Solid Masonry Units Made From Clay or Shale) | 9.20.2.1.(1) |
| CSA | A82.3-M1978 | Calcium Silicate (Sand-Lime) Building Brick | 9.20.2.1.(1) |
| CSA | A82.4-M1978 | Structural Clay Load-Bearing Wall Tile | 9.20.2.1.(1) |
| CSA | A82.5-M1978 | Structural Clay Non-Load-Bearing Tile | 9.20.2.1.(1) |
| CSA | A82.8-M78 | Hollow Clay Brick | 9.20.2.1.(1) |
| CSA | CAN/CSA-A82.27-M91 | Gypsum Board | 3.1.5.11.(4) Table 9.23.16.2.A. 9.29.5.2.(1) |
| CSA | A82.30-M1980 | Interior Furring, Lathing and Gypsum Plastering | 9.29.4.1.(1) |
| CSA | A82.31-M1980 | Gypsum Board Application | 9.10.12.5.(1) 9.29.5.1.(2) |
| CSA | A82.56-M1976 | Aggregate for Masonry Mortar | 9.20.3.1.(1) |
| CSA | CAN3-A93-M82 | Natural Airflow Ventilators for Buildings | 9.19.1.2.(4) |
| CSA | A101-M1983 | Thermal Insulation, Mineral Fibre, for Buildings | 9.25.2.3.(1) Table 9.23.16.2.A. |
| CSA | A123.1-M1979 | Asphalt Shingles Surfaced with Mineral Granules | 9.26.2.1.(1) |
| CSA | A123.2-M1979 | Asphalt Coated Roofing Sheets | 9.26.2.1.(1) |
| CSA | A123.3-M1979 | Asphalt or Tar Saturated Roofing Felt | 9.26.2.1.(1) |
| CSA | A123.4-M1979 | Bitumen for Use in Construction of Built-Up Roof Coverings and Dampproofing and Waterproofing Systems | 9.13.2.1.(1) 9.26.2.1.(1) |
| CSA | CAN/CSA-A123.5-M90 | Asphalt Shingle Made from Glass Felt and Surfaced with Mineral Granules | 5.6.1.2.(1) 9.26.2.1.(1) |
| CSA | A123.17-M1963 | Asphalt-Saturated Felted Glass-Fibre Mat for Use in Construction of Built-Up Roofs | 9.26.2.1.(1) |
| CSA | CAN3-A123.51-M85 | Asphalt Shingle Application on Roof Slopes 1:3 and Steeper | 9.26.1.2.(1) |
| CSA | CAN3-A123.52-M85 | Asphalt Shingle Application on Roof Slopes 1:6 to Less than 1:3 | 9.26.1.2.(1) |
| CSA | A165.1-94 | Concrete Masonry Units | 9.15.2.2.(1) 9.17.5.1.(1) 9.20.2.1.(1) 9.20.2.6.(1) |
| CSA | A165.2-94 | Concrete Brick Masonry Units | 9.20.2.1.(1) |
| CSA | A165.3-94 | Prefaced Concrete Masonry Units | 9.20.2.1.(1) |
| CSA | A165.4-94 | Autoclaved Cellular Units | 9.20.2.1.(1) |
| CSA | CAN/CSA-A220.0-M91 | Performance of Concrete Roof Tiles | 5.6.1.2.(1) 9.26.2.1.(1) |
| CSA | CAN/CSA-A220.1-M91 | Installation of Concrete Roof Tiles | 9.26.17.1.(1) |
| CSA | CAN/CSA-A247-M86 | Insulating Fibreboard | 9.23.15.6.(3) Table 9.23.16.2.A. 9.25.2.3.(1) 9.25.3.1.(1) 9.29.8.1.(1) |
| CSA | A257 Series-M92 | Standards for Circular Concrete Pipe and Manholes | 7.2.5.3.(1) |
| CSA | CAN/CSA-A257.4-M92 | Precast Reinforced Circular Concrete Manhole Sections, Catch Basins, and Fittings | 7.2.5.3.(6) |
| CSA | CAN3-A266.1-M78 | Air-Entraining Admixtures for Concrete | 9.3.1.8.(1) |
| CSA | CAN3-A266.2-M78 | Chemical Admixtures for Concrete | 9.3.1.8.(1) |
| CSA | CSA B66-00 | Prefabricated Septic Tanks and Sewage Holding Tanks | 8.2.2.2.(1) 8.2.2.2.(2) 8.2.2.2.(2.1) 8.2.2.3.(7) |
| CSA | CAN/CSA-A277-M90 | Procedures for Certification of Factory-Built Houses | 2.1.1.4.(2) |
| CSA | CAN/CSA-A324-M88 | Clay Flue Liners | 9.21.3.3.(1) |
| CSA | A371-94 | Masonry Construction for Buildings | 5.6.1.2.(3) 5.6.1.3.(3) 9.20.15.2.(1) |
| CSA | CAN/CSA-A405-M87 | Design and Construction of Masonry Chimneys and Fireplaces | 9.21.3.5.(1) 9.22.1.4.(1) 9.22.5.2.(2) |
| CSA | CAN3-A438-M84 | Concrete Construction for Housing and Small Buildings | 9.3.1.1.(1) 9.3.1.7.(1) |
| CSA | CAN/CSA-A440-M90 | Windows | 3.7.2.2.(3) 9.7.2.1.(1) 9.7.6.1.(1) |
| CSA | CAN/CSA-A440.2-M92 | Energy Performance Evaluation of Windows and Sliding Glass Doors | 9.25.2.1.(12) 9.38.5.4.(4) |
| CSA | CAN/CSA-B44-M94 | Safety Code for Elevators, Escalators, Dumbwaiters, Moving Walks and Freight Platform Lifts | 3.3.3.9.(1) 3.8.3.5.(1) Table 4.1.10.5. |
| CSA | CAN/CSA-B45.O Series-94 | General Requirements for Plumbing Fixtures | 7.6.4.2.(1) |
| CSA | CAN/CSA-B52-92 | Mechanical Refrigeration Code | 6.2.2.4.(4) |
| CSA | CAN/CSA-B64 Series-M94 | Backflow Preventers and Vacuum Breakers | 7.6.2.3.(4) |
| CSA | CAN/CSA-B64.0-M94 | Definitions, General Requirements, and Test Methods for Vacuum Breakers and Backflow Preventers | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.1.1-M94 | Vacuum Breakers, Atmospheric Type (AVB) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.1.2-M94 | Vacuum Breakers, Pressure Type (PVB) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.2-M94 | Vacuum Breakers, Hose Connection Type | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.2.1-M94 | Vacuum Breakers, Hose Connection Type (HCVB) with Manual Draining Feature | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.2.2-M94 | Vacuum Breakers, Hose Connection Type (HCVB) with Automatic Draining Feature | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.3-M94 | Backflow Preventers, Dual Check Valve Type Atmospheric Port (DACP) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.4-M94 | Backflow Preventers, Reduced Pressure Principle Type (RP) | 7.2.10.10.(1) 7.6.2.3.(4) |
| CSA | CAN/CSA-B64.5-M94 | Backflow Preventers, Double Check Valve Type (DCVA) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.6-M94 | Backflow Preventers, Dual Check Valve Type (DuC) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.7-M94 | Vacuum Breakers, Laboratory Faucet Type (LFVP) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.8-M94 | Backflow Preventers, Dual Check Valve Type with Intermediate Vent (DuCV) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.10-M94 | Backflow Prevention Devices - Selection, Installation, Maintenance and Field Testing | 7.2.10.10.(1) |
| CSA | B67-1972 | Lead Service Pipe, Waste Pipe, Traps, Bends and Accessories | 7.2.7.8.(1) 7.2.9.2.(1) |
| CSA | CAN/CSA-B70-M91 | Cast Iron Soil Pipe, Fittings and Means of Joining | 7.2.6.1.(1) |
| CSA | B111-1974 | Wire Nails, Spikes and Staples | 9.23.3.1.(1) 9.26.2.2.(1) 9.29.5.6.(1) |
| CSA | CAN/CSA-B125-93 | Plumbing Fittings | 7.2.3.3.(1) 7.2.10.6.(1) 7.2.10.7.(1) 7.2.10.7.(2) 7.2.10.10.(2) |
| CSA | B127.1-M1977 | Components for Use in Asbestos Cement Drain, Waste and Vent Systems | 7.2.5.1.(1) |
| CSA | B127.2-M1977 | Components for Use in Asbestos Cement Building Sewer Systems | 7.2.5.1.(2) |
| CSA | CAN/CSA-B137.1-M89 | Polyethylene Pipe, Tubing and Fittings for Cold Water Pressure Services | 7.2.5.5.(1) Table 7.2.11.2. |
| CSA | CAN/CSA-B137.2-M93 | PVC Injection-Moulded Gasketed Fittings for Pressure Applications | 7.2.5.6.(1) 7.2.5.9.(1) |
| CSA | CAN/CSA-B137.3-M93 | Rigid Poly (Vinyl Chloride) (PVC) Pipe for Pressure Applications | 7.2.5.6.(1) 7.2.5.9.(1) Table 7.2.11.2. |
| CSA | CAN/CSA-B137.5-M89 | Cross-Linked Polyethylene (PEX) Tubing Systems for Pressure Applications | 7.2.5.5.(4) Table 7.2.11.2. |
| CSA | B137.6-M1983 | CPVC Pipe, Tubing and Fittings for Hot and Cold Water Distribution Systems | 7.2.5.7.(1) Table 7.2.11.2. |
| CSA | B137.7-M1983 | Polybutylene (PB) Pipe for Cold Water Distribution Systems | Table 7.2.11.2. |
| CSA | CAN/CSA-B137.8-M92 | Polybutylene (PB) Piping for Pressure Applications | 7.2.5.8.(1) |
| CSA | CAN/CSA-B137.9-M91 | Polyethylene/Aluminum/Polyethylene Composite Pressure Pipe Systems | 7.2.5.12.(1) Table 7.2.11.2. |
| CSA | CAN/CSA-B137.10-M91 | Crosslinked Polyethylene/Aluminum Crosslinked Polyethylene Composite Pressure Pipe Systems | 7.2.5.13.(1) Table 7.2.11.2. |
| CSA | CAN/CSA-B137.11-M93 | Polypropylene (PP-R) Pipe and Fittings for Pressure Applications | 7.2.5.14.(1) |
| CSA | B158.1-M1976 | Cast Brass Solder Joint Drainage, Waste and Vent Fittings | 7.2.7.5.(1) 7.2.10.1.(1) |
| CSA | CAN/CSA-B181.1-M90 | ABS Drain, Waste, and Vent Pipe and Pipe Fittings | 7.2.5.9.(1) 7.2.5.10.(1) 7.2.5.10.(2) 7.2.10.1.(2) |
| CSA | CAN/CSA-B181.2-M90 | PVC Drain, Waste, and Vent Pipe and Pipe Fittings | 7.2.5.9.(1) 7.2.5.10.(1) 7.2.5.10.(2) 7.2.10.1.(3) |
| CSA | CAN/CSA-B181.3-M86 | Polyolefin Laboratory Drainage Systems | 7.2.8.1.(1) |
| CSA | CAN/CSA-B182.1-M92 | Plastic Drain and Sewer Pipe and Pipe Fittings | 7.2.5.9.(1) 7.2.5.10.(2) 9.14.3.1.(1) |
| CSA | CAN/CSA-B182.2-M90 | PVC Sewer Pipe and Fittings (PSM Type) | 7.2.5.9.(1) 7.2.5.10.(2) |
| CSA | CAN/CSA-B182.4-M92 | Profile (Ribbed) PVC Sewer Pipe and Fittings | 7.2.5.9.(1) |
| CSA | CAN/CSA-B182.6-M92 | Profile Polyethylene Sewer Pipe and Fittings | 7.2.5.9.(1) |
| CSA | B242-M1980 | Groove and Shoulder Type Mechanical Pipe Couplings | 7.2.10.4.(1) |
| CSA | CAN/CSA-B272-M1993 | Prefabricated Self-Sealing Vent Flashings | 7.2.10.14.(2) |
| CSA | CAN/CSA-B281-M90 | Aluminum Drain, Waste, and Vent Pipe and Components | 7.2.7.9.(1) 7.2.7.9.(3) |
| CSA | CAN/CSA-B355-94 | Lifts for Persons with Physical Disabilities | 3.8.3.5.(2) |
| CSA | CAN/CSA-B356-94 | Water Pressure Reducing Valves Water Pressure Reducing Valves for Domestic Water Supply Systems | 7.2.10.12.(1) |
| CSA | CAN/CSA-B365-M91 | Installation Code for Solid-Fuel Burning Appliances and Equipment | 6.2.1.5.(1) 9.21.1.3.(2) 9.33.1.2.(1) |
| CSA | CAN/CSA-B366.1-M87 | Solid Fuel-Fired Central Heating Appliances | 6.2.1.5.(2) |
| CSA | CAN/CSA-B602-M90 | Mechanical Couplings for Drain, Waste, and Vent Pipe and Sewer Pipe | 7.2.5.3.(3) 7.2.10.4.(2) |
| CSA | CAN/CSA-C22.2 No.0.3-92 | Test Methods for Electrical Wires and Cables | 3.1.4.3.(1) 3.1.5.17.(1) 3.1.5.20.(1) 3.6.4.3.(1) |
| CSA | C22.2 No.113-M1984 | Fans and Ventilators | 9.32.3.9.(5) |
| CSA | C22.2 No.141-M1985 | Unit Equipment for Emergency Lighting | 3.2.7.4.(2) 9.9.11.3.(6) |
| CSA | C22.2 No.211.0-M84 | General Requirements and Methods of Testing Nonmetallic Conduit | 3.1.5.19.(1) |
| CSA | CAN/CSA-C22.3 No.1-M87 | Overhead Systems | 3.1.18.1.(2) |
| CSA | CAN/CSA-C88-M90 (R1994) | Power Transformers and Reactors | 3.6.2.8.(10) |
| CSA | CAN/CSA-C260-M90 | Rating for the Performance of Residential Mechanical Ventilating Equipment | 9.32.3.9.(1) |
| CSA | C282-05 | Emergency Electrical Power Supply for Buildings | 3.2.7.5.(1) |
| CSA | CAN/CSA-C439-M88 | Standard Methods of Test for Rating the Performance of Heat Recovery Ventilators | 6.2.1.7.(2) 9.32.3.11.(2) |
| CSA | CAN/CSA-C445-M92 | Design and Installation of Earth Energy Heat Pump Systems for Residential and Other Small Buildings | 6.2.1.5.(3) |
| CSA | C447-94 | Design and Installation of Earth Energy Heat Pump Systems for Commercial and Institutional Buildings | 6.2.1.5.(4) |
| CSA | CAN/CSA-F280-M90 | Determining the Required Capacity of Residential Space Heating and Cooling Appliances | 6.2.1.1.(1) |
| CSA | CAN/CSA-F379.1-88 | Solar Domestic Hot Water Systems (Liquid to Liquid Heat Transfer) | 7.2.10.13.(1) |
| CSA | CAN/CSA-F383-87 | Installation Code for Solar Domestic Hot Water Systems | 7.6.1.15.(1) |
| CSA | CAN/CSA-G40.21-M92 | Structural Quality Steels | 4.2.3.8.(1) 9.23.4.3.(2) |
| CSA | G164-M81 | Hot Dip Galvanising of Irregularly Shaped Articles | 4.1.10.8.(4) |
| CSA | G401-93 | Corrugated Steel Pipe Products | 7.2.6.8.(1) 9.14.3.1.(1) |
| CSA | CAN/CSA-O80-M89 | Wood Preservation | 3.1.4.4.(1) 4.2.3.2.(1) |
| CSA | CAN/CSA-O80.1-M89 | Preservative Treatment of All Timber Products by Pressure Processes | 9.3.2.9.(1) |
| CSA | CAN/CSA-O80.2-M89 | Preservative Treatment of Lumber, Timber, Bridge Ties and Mine Ties by Pressure Processes | 4.2.3.2.(1) 9.3.2.9.(1) |
| CSA | CAN/CSA-O80.3-M89 | Preservative Treatment of Piles by Pressure Processes | 4.2.3.2.(1) |
| CSA | CAN/CSA-O80.9-M89 | Preservative Treatment of Plywood by Pressure Processes | 9.3.2.9.(1) |
| CSA | CAN/CSA-O80.15-M89 | Preservative Treatment of Wood for Building Foundation Systems, Basements and Crawl Spaces by Pressure Processes | 4.2.3.2.(1) 9.3.2.9.(1) |
| CSA | O86.1-94 | Engineering Design in Wood (Limit States Design) | 4.3.1.1.(1) Table 4.1.9.1.B. |
| CSA | O115-M1982 | Hardwood and Decorative Plywood | 9.27.9.1.(1) 9.30.2.2.(1) |
| CSA | O118.1-M88 | Western Red Cedar Shingles and Shakes | 9.26.2.1.(1) 9.27.7.1.(1) |
| CSA | O118.2-M88 | Eastern White Cedar Shingles | 5.6.1.2.(1) 5.6.1.2.(3) 9.26.2.1.(1) 9.27.7.1.(1) |
| CSA | O121-M1978 | Douglas Fir Plywood | 9.23.14.2.(1) 9.23.15.1.(1) Table 9.23.16.2.A. 9.27.9.1. 9.30.2.2.(1) |
| CSA | O132.2-M1977 | Wood Doors | 9.6.5.1.(1) |
| CSA | CAN/CSA-O132.2 Series-M90 | Wood Flush Doors | 9.6.5.1.(1) |
| CSA | O141-1991 | Softwood Lumber | 3.1.4.6.(2) 9.3.2.6.(1) |
| CSA | O151-M1978 | Canadian Softwood Plywood | 9.23.14.2.(1) 9.23.15.1.(1) Table 9.23.16.2.A. 9.27.9.1.(1) 9.30.2.2.(1) |
| CSA | O153-M1980 | Poplar Plywood | 9.23.14.2.(1) 9.23.15.1.(1) Table 9.23.16.2.A. 9.27.9.1.(1) 9.30.2.2.(1) |
| CSA | CAN/CSA-O177-M89 | Qualification Code for Manufacturers of Structural Glued-Laminated Timber | 4.3.1.2.(1) |
| CSA | CAN3-O188.1-M78 | Interior Mat-Formed Wood Particleboard | 9.23.14.2.(3) 9.29.9.1.(1) 9.30.2.2.(1) |
| CSA | CAN/CSA-O325.0-92 | Construction Sheathing | 5.6.1.2.(3) 9.23.14.2.(1) 9.23.15.1.(1) |
| CSA | O437.0-93 | OSB and Waferboard | 5.6.1.2.(3) 9.23.14.2.(1) 9.23.14.4.(2) 9.23.15.1.(1) 9.23.15.2.(2) Table 9.23.16.2.A. 9.27.11.1.(1) 9.29.9.1.(2) 9.30.2.2.(1) |
| CSA | CAN/CSA-S16.1-94 | Limit States Design of Steel Structures | Table 4.1.9.1.B. 4.3.4.1.(1) |
| CSA | CAN/CSA-S37-M86 | Antennas, Towers and Antenna Supporting Structures | 4.1.1.4.(2) |
| CSA | S136-94 | Cold Formed Steel Structural Members | 4.3.4.2.(1) |
| CSA | CAN3-S157-M83 | Strength Design in Aluminum | 4.3.5.1.(1) |
| CSA | CAN3-S304-M84 | Masonry Design for Buildings | Table 4.1.9.1.B. 4.3.2.1.(1) 9.21.4.5.(1) |
| CSA | S304.1-94 | Masonry Design for Buildings (Limit States Design) | Table 4.1.9.1.B. 4.1.9.3.(5) 4.3.2.1.(1) |
| CSA | S307-M1980 | Load Test Procedure for Wood Roof Trusses for Houses and Small Buildings | 9.23.13.11.(5) |
| CSA | CAN3-S367-M81 | Air Supported Structures | 4.4.1.1.(1) |
| CSA | CAN/CSA-S406-M92 | Construction of Preserved Wood Foundations | 9.13.3.4.(1) 9.15.1.3.(3) |
| CSA | S413-94 | Parking Structures | 2.1.1.9.(1) 4.4.2.1.(1) |
| CSA | CAN/CSA-Z32.4-M86 | Essential Electrical Systems for Hospitals | 3.2.7.6.(1) |
| CSA | CAN/CSA-Z91-M90 | Safety Code for Window Cleaning Operations | 4.1.10.8.(2) |
| CSA | CAN/CSA-Z240.2.1-92 | Structural Requirements for Mobile Homes | 2.1.1.4.(2) 9.12.2.2.(6) 9.15.1.4.(1) |
| CSA | CAN/CSA-Z240.3.1-M92 | Plumbing Requirements for Mobile Homes | 2.1.1.4.(2) |
| CSA | CAN/CSA-Z240.8.1-M92 | Light Duty Windows | 2.1.1.4.(2) 9.7.2.1.(2) |
| CSA | CAN/CSA-Z240.10.1-M94 | Site Preparation, Foundation and Anchorage of Mobile Homes | 9.15.1.4.(1) 9.23.6.3.(1) |
| CSA | CAN/CSA-Z241-M92 | Park Model Trailers | 9.39.1.1.(1) 9.39.2.1.(1) |
| CSA | CAN/CSA-Z305.1-92 | No-Flammable Medical Gas Piping Systems | 3.7.5.2.(1) |
| CSA | CAN/CSA-Z317.2-M91 | Special Requirements for Heating, Ventilation and Air Conditioning (HVAC) Systems in Health Care Facilities | 6.2.1.1.(1) |
| CSA | CSA 6.19-01 | Residential Carbon Monoxide Alarming Devices | 6.2.5A.3.(1) 9.33.4.3.(1) |
| DBR | Technical Paper No. 194 | Fire Endurance of Protected Steel Columns and Beams | 11.5.1.1. |
| DBR | Technical Paper No. 207 | Fire Endurance of Unit Masonry Miscellaneous Assemblies | 11.5.1.1. |
| DBR | Technical Paper No. 222 | Fire Endurance of Light Framed and Miscellaneous Assemblies | 11.5.1.1. |
| HUD | Rehabilitation Guidelines No. 8 — 1980 | Guideline on Fire Ratings of Archaic Materials and Assemblies | 11.5.1.1. |
| ISO | ISO 8201; 1987(E) | Acoustics - Audible Emergency Evacuation Signal | 3.2.4.19.(2) |
| TPIC | 1988 | Truss Design Procedures and Specifications for Light Metal Plate Connected Wood Trusses | 9.23.13.11.(6) |
| MMAH | Supplementary Guidelines, 1997 | Supplementary Guidelines to the 1997 OBC | 2.1.1.11., 3.1.5.22.(2), 3.1.7.1.(2), 3.1.8.14.(2), 3.1.9.5.(1), 3.1.12.1.(3), 3.2.3.11.(1), 3.2.3.12.(4), 3.2.4.19.(7), 3.2.6.9.(3), 3.2.6.10.(2), 3.2.6.15.(1), 3.6.1.5.(1), 3.12.2.1.(8), 3.12.3.5.(1), 3.12.3.6.(2), 3.12.4.2.(7), 9.8.8.8.(2), 9.10.3.1.(1), 9.10.3.2.(1), 9.10.5.1.(4), 9.11.2.1., 9.13.7.1.(1), 9.15.3.3.(4), 9.10.13.14.(1) 8.2.1.2.(2), 8.6.2.2.(5) |
| MOEE | Guidelines 1985, with Subsequent Revision | Guidelines for the Design of Sanitary Sewage Works, Storm Sewers, Water Storage Facilities, Water Distribution Systems, Servicing in areas subject to adverse conditions, Water supply for small residential development and seasonally operated water supply | 7.1.6.5.(1) |
| American Public Health Association, American Waterworks Association, Water Environment Federation | 18th edition | Standard methods for the Examination of Water and Waste Water | 8.9.2.4.(1)(b) |
| NFPA | 13-1994 | Installation of Sprinkler Systems | 3.2.4.16.(1) 3.2.5.13.(1) 3.2.8.4.(7) 3.3.2.12.(3) 7.6.2.3.(4) |
| NFPA | 13D-1994 | Installation of Sprinkler Systems in One- and Two-Family Dwellings and Mobile Homes | 3.2.5.13.(3) |
| NFPA | 13R-1991 | Installation of Sprinkler Systems in Residential Occupancies up to and including Four Stories in Height | 3.2.5.13.(2) |
| NFPA | 14-1993 | Installation of Standpipe and Hose Systems | 3.2.9.2.(1) |
| NFPA | 24-92 | Standard for the Installation of Fire Service Mains and Their Appurtenances | 7.2.11.1.(1) |
| NFPA | 71-1989 | Installation, Maintenance and Use of Central Station Signalling Systems | 3.2.4.7.(4) |
| NFPA | 72-1990 | Installation, Maintenance and Use of Proprietary Protective Signalling Systems | 3.2.4.7.(4) 3.12.5.4.(1) |
| NFPA | 80-1992 | Fire Doors and Windows | 3.1.8.5.(2) 3.1.8.10.(2) 3.1.8.12.(2) 3.1.8.14.(1) 3.12.3.1.(2) 9.10.13.1.(1) 9.10.13.2.(3) |
| NFPA | 82-1994 | Incinerators, Waste and Linen Handling Systems and Equipment | 6.2.6.1.(1) 9.10.10.5.(2) |
| NFPA | 96-1994 | Ventilation Control and Fire Protection of Commercial Cooking Operations | 6.2.2.6. (1) |
| NFPA | 130-1990 | Fixed Guideway Transit Systems | 3.12.7.1. |
| NFPA | 211-1992 | Standard for Chimneys, Fireplaces, Vents and Solid Fuel-Burning Appliances | 6.3.1.2.(2) 6.3.1.3.(1) |
| NFPA | 214-1992 | Water-Cooling Towers | 6.2.3.15.(4) |
| NFPA | 701-1992 | Standard Method of Fire Tests for Flame-Resistant Textiles and Films | 3.13.1.6.(1) 3.13.2.5.(1) |
| NLGA | 1994 | Standard Grading Rules for Canadian Lumber | 9.3.2.1.(1) Table 9.3.2.1. |
| UL | UL 2034-1996 | Single and Multiple Station Carbon Monoxide Detectors | 6.2.5A.3.(1) 9.33.4.3.(1) |
| ULC | CAN/ULC-S101-M89 | Standard Methods of Fire Endurance Tests of Building Construction and Materials | 3.1.5.11.(3) 3.1.5.11.(4) 3.1.5.11.(6) 3.1.7.1.(1) 3.1.11.7.(1) 3.2.3.7.(7) 3.2.6.9.(6) 3.2.6.14.(4) |
| ULC | CAN/ULC-S102-M88 | Standard Method of Test for Surface Burning Characteristics of Building Materials and Assemblies | 3.1.12.1.(1) |
| ULC | CAN/ULC-S102.2-M88 | Standard Method of Test for Surface Burning Characteristics of Flooring, Floor Covering, and Miscellaneous Materials and Assemblies | 3.1.12.1.(2) 3.1.13.4.(1) |
| ULC | S102.3-M1982 | Standard Method of Fire Test of Light Diffusers and Lenses | 3.1.13.4.(1) |
| ULC | CAN4-S104-M80 | Standard Method of Fire Test of Door Assemblies | 3.1.8.4.(1) 3.2.6.9.(3) 9.10.13.2.(1) |
| ULC | CAN4-S105-M85 | Standard Specification for Fire Door Frames Meeting the Performance Required by CAN4-S104 | 9.10.13.6.(1) |
| ULC | CAN4-S106-M80 | Standard Method for Fire Tests of Window and Glass Block Assemblies | 3.1.8.4.(1) 3.13.2.5.(1) |
| ULC | CAN/ULC-S107-M87 | Standard Method for Fire Tests of Roof Coverings | 3.1.15.1.(1) |
| ULC | CAN/ULC-S109-M87 | Standard for Flame Tests of Flame-Resistant Fabrics and Films | 3.1.4.7.(1) 3.1.5.22.(1) 3.13.1.6.(1) 6.2.3.18.(1) 6.2.4.9.(1) |
| ULC | CAN/ULC-S110-M1986 | Standard Methods of Fire Test for Air Ducts | 6.2.3.2.(2) 6.2.3.2.(4) |
| ULC | CAN4-S111-M80 | Standard Method of Fire Tests for Air Filter Units | 6.2.3.14.(1) 6.2.4.14.(1) |
| ULC | CAN/ULC-S112-M90 | Standard Method of Fire Test of Fire-Damper Assemblies | 3.1.8.4.(1) |
| ULC | CAN4-S112.2-M84 | Standard Method of Fire Test of Ceiling Firestop Flap Assemblies | 3.1.9.5.(2) 3.6.4.3.(2) |
| ULC | CAN4-S113-M79 | Standard Specification for Wood Core Doors Meeting the Performance Required by CAN4-S104-77 for Twenty Minute Fire Rated Closure Assemblies | 9.10.13.2.(1) |
| ULC | CAN4-S114-M80 | Standard Method of Fire Test for Determination of Non-Combustibility in Building Materials | 1.1.3.2. |
| ULC | CAN4-S115-M85 | Standard Method of Fire Tests for Firestop Systems | 3.1.9.1.(1) 3.1.9.1.(2) 3.1.9.4.(4) 9.10.9.7.(3) |
| ULC | CAN4-S124-M85 | Standard Method of Test for the Evaluation of Protective Coverings for Foamed Plastic | 3.1.5.11.(2) |
| ULC | CAN/ULC-S126-M86 | Standard Method of Test for Fire Spread Under Roof-Deck Assemblies | 3.1.14.1.(1) 3.1.14.2.(1) |
| ULC | CAN/ULC-S134-92 | Fire Test of Exterior Wall Assemblies | 3.1.5.5.(1) |
| ULC | S505-1974 | Standard for Fusible Links for Fire Protection Service | 3.1.8.9.(1) |
| ULC | S513-78 | Standard for Threaded Couplings for 38 mm and 65 mm Fire Hose | 3.2.9.2.(7) |
| ULC | CAN/ULC-S524-M91 | Standard for the Installation of Fire Alarm Systems | 3.2.4.5.(1) |
| ULC | CAN/ULC-S531-M87 | Standard for Smoke Alarms | 3.2.4.21.(1) 9.10.18.1.(1) |
| ULC | CAN/ULC-S537-M87 | Standard for the Verification of Fire Alarm Systems | 3.2.4.5.(2) |
| ULC | S543-M1983 | Standard for Internal Lug Quick Connect Couplings for Fire Hoses | 3.2.9.2.(7) |
| ULC | CAN/ULC-S553-M86 | Installation of Smoke Alarms | 3.2.4.21.(7) |
| ULC | CAN/ULC-S610-M87 | Standard for Factory-Built Fireplaces | 9.22.8.1. |
| ULC | CAN/ULC-S628-93 | Fireplace Inserts | 9.22.10.1.(1) |
| ULC | CAN/ULC-S629-M87 | Standard for 650oC Factory-Built Chimneys | 9.21.1.2. |
| ULC | CAN/ULC-S639-M87 | Standard for Steel Liner Assemblies for Solid Fuel-Burning Masonry Fireplaces | 9.22.2.3. |
| ULC | CAN/ULC-S701-M97 | Standard for Thermal Insulation, Polystyrene, Boards and Pipe Covering | Table 9.23.16.2.A. 9.25.2.3.(1) 9.25.2.3.(4) |
| ULC | ULC/ORD-C199P-M1988 | Guide for the Investigation of Combustible Piping for Sprinkler Systems | 3.2.5.14.(2) |
| ULC | ULC/ORD-C376-1995 | Fire Growth of Foamed Plastic Insulated Building Panels in a Full-Scale Room Configuration | 3.1.5.11.(7) |
| ULC | ULC/ORD-C693-1994 | Central Station Fire Protective Signalling Systems and Services | 3.2.4.7.(4) |
| Column 1 | 2 | 3 | 4 |

2.6.4. Alternate Test Standards

2.6.4.1.  Comparable Test Results

(1)  The results of tests based on test standards other than as described in this Code may be used if the alternate test standards provide comparable results.

Section 2.7. Equivalents

2.7.1. Application

2.7.1.1.  General

(1)  A chief building official or a registered code agency may allow, under Section 9 of the Act, the use of materials, systems or building designs not authorized by this Code, if the use of the proposed materials, systems or building designs

(a)	is permitted under this Section, and

(b)	will, in the opinion of the chief building official or registered code agency, provide the level of performance that would be achieved by conforming with the requirements of this Code.

(2)  A chief building official or a registered code agency that allows, under Section 9 of the Act, the use of materials, systems or building designs not authorized by this Code shall make a record of the decision that includes:

(a)	the decision to allow the use of the material, system or building design, and

(b)	 all documents in support of the request provided to the chief building official or registered code agency by the person requesting the use of the material, system or building design.

2.7.2. Acceptance of Equivalents

2.7.2.1.  Materials

(1)  Materials not specifically described in Parts 3, 5, 6, 7, 8 and 9, or which vary from the specific requirements in those Parts or for which no recognized test procedure has been established, may be used if the person requesting the use of such material can establish on the basis of past performance, tests described in Article 2.7.2.4. or other evaluation that the use of the proposed material will provide the level of performance that would be achieved by conformance with the requirements of the building code.

2.7.2.2.  Systems

(1)  Systems not specifically described in Parts 3, 5, 6, 7, 8 and 9, or for which no recognized test procedure has been established, may be used if the person requesting the use of such system can establish on the basis of past performance, tests described in Article 2.7.2.4. or other evaluation that the use of the proposed system will provide the level of performance that would be achieved by conformance with the requirements of the building code.

2.7.2.3.  Building Designs

(1)  Building designs not specifically described in Part 4 may be used if the person requesting the use of such building design can establish that the use of the proposed building design will provide the level of performance that would be achieved by conformance with the requirements of the building code.

2.7.2.4.  Tests

(1)  Where no published test method to establish the suitability of a material or system proposed under Articles 2.7.2.1. or 2.7.2.2. exists, then the tests used for the purposes of those Articles shall be designed to simulate or exceed anticipated service conditions or shall be designed to compare the performance of the material or system with a similar material or system that is known to be acceptable.

(2)  The results of tests or evaluations based on test standards other than as described in the building code may, in accordance with Article 2.6.4.1., be used for the purposes of Sentence (1) if the alternate test standards provide comparable results.

Section 2.8.  Rulings and Interpretations

2.8.1. Designated Materials Evaluation Bodies

2.8.1.1.  Designated Bodies

(1)  The following body is designated as a materials evaluation body for the purposes of Clause 29 (1) (a) of the Act:

Canadian Construction Materials Centre
Institute for Research in Construction
National Research Council of Canada
Montreal Road
Ottawa, Ontario
K1A 0R6

2.8.2. Minister’s Rulings

2.8.2.1.  Minister’s Rulings

(1)  The Minister may impose terms and conditions, including conditions of termination, when making rulings under Clause 29 (1) (a) of the Act adopting the evaluation report of a materials evaluation body designated in the building code.

2.8.2.2.  Criteria

(1)  A ruling made under Clause 29 (1) (c) of the Act may only approve the use of an alternative material, system or building design in a manner

(a)	that will, in the opinion of the Minister, achieve the level of performance that is required by this Code, and

(b)	that is consistent with,

(i)	a decision of the Building Code Commission in respect of a dispute described in Clause 24 (1) (a) of the Act,

(ii)	an approval of the use of the material, system or building design in the whole of another province or territory in accordance with the law of that province or territory,

(iii)	an approval of the use of the material, system or building design under Section 9 of the Act by a chief building official, or

(iv)	a revision of the National Building Code of Canada that has been approved by the Canadian Commission on Building and Fire Codes.

2.8.3. Interpretations By Minister

2.8.3.1.  Interpretations By Minister

(1)  Every interpretation issued by the Minister under Section 28.1 of the Act shall be made available to the public

(a)	by posting the interpretation on the Building Code website, and

(b)	by providing a written copy of the interpretation on receipt of a request for it.

Section 2.9. Search Warrant

2.9.1. Forms

2.9.1.1.  Information & Warrant Forms

(1)  An information to obtain a warrant to enter and search lands and buildings under Subsection 21(1) of the Act shall be in Form 2.9.1.A.

(2)  A warrant to enter and search lands and buildings under Subsection 21(1) of the Act shall be in Form 2.9.1.B.

Form 2.9.1.A.

Building Code Act, 1992

INFORMATION TO OBTAIN SEARCH WARRANT UNDER SECTION 21 OF THE BUILDING CODE ACT, 1992

ONTARIO COURT (PROVINCIAL DIVISION)

PROVINCE OF ONTARIO

| This is the information of |  |  |  |  | ......................................................................................................................................................... |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | (name) |  |  |  |  |  |  |  |  |
| of | ............................................................................................ |  |  |  |  |  |  |  |  | ............................................................................................. |  |  |  |
|  | (address) |  |  |  |  |  |  |  |  | (occupation) |  |  |  |
| I have reasonable ground to believe and do believe that the offence of |  |  |  |  |  |  |  |  |  |  |  |  | ................................................................................... |
| contrary to Building Code Act, 1992 Section |  |  |  |  |  |  | ……….. | has been committed and that the entry into and search of a certain |  |  |  |  |  |
| building, receptacle or place, namely, |  |  |  |  |  | ………………………………………………………………………………………. |  |  |  |  |  |  |  |
| (building, receptacle or place) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ...................................................................................................................................................................................................... |  |  |  |  |  |  |  |  |  |  |  |  |  |
| of ........................................................................................, at |  |  |  |  |  |  |  |  | ................................................................................................. |  |  |  |  |
| (owner) |  |  |  |  |  |  |  |  | (address) |  |  |  |  |
| will afford the following evidence: ......................................................................……............................................................... |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ....................................................................................................................................................................................................... |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (describe evidence to be searched for, including things to be seized, if any) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| relevant to the commission of the offence. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| And I further say that my grounds for so believing are: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ....................................................................................................................................................................................................... |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ....................................................................................................................................................................................................... |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Therefore, I request that a search warrant be issued to |  |  |  |  |  |  |  |  |  |  |  |  |  |
| check appropriate box |  | □ |  | enter into and search the said ……………………………………………………………………………… |  |  |  |  |  |  |  |  |  |
|  |  |  |  | ………………………………………….……… |  |  |  |  |  |  | (building, receptacle or place) |  |  |
|  |  |  |  |  |  |  |  |  |  |  | for the said evidence. |  |  |
|  |  | □ |  | enter into and search the said ……………………………………………………………………………… |  |  |  |  |  |  |  |  |  |
|  |  |  |  | …………………………………………………. |  |  |  |  |  |  | (building, receptacle or place) |  |  |
|  |  |  |  |  |  |  |  |  |  |  | for the said evidence and to seize the following things: |  |  |
|  |  |  |  | ......................................................................................................................................................................... |  |  |  |  |  |  |  |  |  |
|  |  | (describe things to be seized) |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | ..................................................................................... |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Informant |  |
|  |  |  | Sworn before me at ...................................................., |  |  |  |  |  |  |  |  |  |  |
|  |  |  | This ….. day of …….…………………….., ………. |  |  |  |  |  |  |  |  | ………………………………………………………. |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Provincial Judge or Justice of the Peace |  |

Form 2.9.1.B.

Building Code Act, 1992

SEARCH WARRANT UNDER SECTION 21 OF THE BUILDING CODE ACT, 1992

ONTARIO COURT (PROVINCIAL DIVISION)

PROVINCE OF ONTARIO

| To: ……………………………………………………………………………………………………………………………. , |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Whereas, on the information on oath of ....................... , |  |  |  | I am satisfied that there is reasonable ground to believe that the |  |  |
| Offence of ........................................................................... |  |  |  |  | contrary to Building Code Act, 1992 Section .............................. |  |  |
| has been committed and that ............…………........................................................................................................................... |  |  |  |  |  |  |  |
| …………………………………………………………………………………………………………………………………... |  |  |  |  |  |  |  |
| (describe evidence to be searched for, including things to be seized, if any) |  |  |  |  |  |  |  |
| that there is reasonable ground to believe will afford evidence of the said offence may be found at .......................................... |  |  |  |  |  |  |  |
| ....................................................................................................................................................................................................... |  |  |  |  |  |  |  |
| (building, receptacle or place) |  |  |  |  |  |  |  |
| of .........................................................., at .................................................................................................................................. |  |  |  |  |  |  |  |
| (owner) |  |  |  |  |  | (address) |  |
| hereinafter called the premises. |  |  |  |  |  |  |  |
| This is therefore to authorise you to enter such ............................................................................................................................ |  |  |  |  |  |  |  |
|  |  |  |  |  |  | (name or location of building, receptacle or place) |  |
| Between the hours of 6:00 a.m. and 9:00 p.m., or ....................................................................................................................... |  |  |  |  |  |  |  |
|  |  |  |  |  |  | (time warrant to be executed) |  |
| check appropriate box |  | □ |  | and to search for the said evidence. |  |  |  |
|  |  | □ |  | and to search the said evidence and to seize the following things ................................................................ |  |  |  |
|  |  |  |  | ......................................................................................................................................................................... |  |  |  |
|  |  | (describe things to be seized) |  |  |  |  |  |
|  |  | and carry them before me or another Provincial Judge or Justice of the Peace so that they may be dealt with according to the law. |  |  |  |  |  |
| This warrant expires on the ……..…… day of …………………………... a day not later than the fifteenth day after its issue. |  |  |  |  |  |  |  |
|  |  |  | Issued at .................................................................... |  |  |  |  |
|  |  |  | this ...................... day of ....................... , .................. |  |  |  | ......................................................................................... |
|  |  |  |  |  |  |  | Provincial Judge or Justice of the Peace |

2.10. Building Code Commission

2.10.1. Hearings

2.10.1.1.  Divisions

(1)  The Building Code Commission may sit in two or more divisions simultaneously so long as a quorum of each division is present.

2.10.1.2.  Single Member

(1)  One member of the Building Code Commission may, with the approval of the chair or vice-chair, hear and determine any dispute set out in Sentence (2) and, for that purpose, the member has all the jurisdiction and powers of the Commission.

(2)  The disputes referred to in Sentence (1) are:

(a)	any dispute described in Clause 24 (1) (a) of the Act respecting the sufficiency of compliance with technical requirements of this Code related to sewage systems, and

(b)	any dispute described in Clause 24 (1) (b) or (c) of the Act.

2.10.1.3.  Time Period

(1)  A hearing to decide a dispute described in Clause 2.10.1.2.(2)(b) shall be held not more than five days after the Commission receives an application for a hearing in a form approved by the Commission.

(2)  The time period described in Sentence (1) commences on the day after the Commission receives the application and excludes Saturdays, holidays and all other days when the offices of the Government of Ontario are not open for the transaction of business with the public.

2.10.1.4.  Eligibility

(1)  No member of the Commission shall be:

(a)	a member of the public service of Ontario,

(b)	an employee of a principal authority, or

(c)	a person who is registered under Article 2.19.3.2. as a registered code agency, an officer, director, partner or employee of a registered code agency or a person engaged by a registered code agency to perform functions under the Act on behalf of the registered code agency.

Section 2.11.  Revoked:  O. Reg. 305/03, s. 15.

Section 2.12.  Revoked:  O. Reg. 305/03, s. 15.

2.13.  Designated Persons and Powers

2.13.1.  General

2.13.1.1.  General

(1)  The director and employees of the Ministry of Municipal Affairs and Housing specified by the director are designated for the purposes of the enforcement of the Act and this Code in relation to the qualifications of:

(a)	chief building officials,

(b)	inspectors,

(c)	registered code agencies,

(d)	persons engaging in the activities described in Subsection 15.11(5) of the Act, and

(e)	persons engaged in the business of constructing on site, installing, repairing, servicing, cleaning or emptying sewage systems.

(2)  The director may, for the purposes set out in Sentence (1), exercise the following powers under the Act of a chief building official:

(a)	certify for the purposes of Subsection 37 (2) of the Act statements as to any matter of record in the office of the director, and

(b)	apply for an order under Section 38 of the Act.

(3)  The employees of the Ministry of Municipal Affairs and Housing designated by the director may, for the purposes set out in Sentence (1), exercise the following powers under the Act of an inspector:

(a)	subject to Section 16 of the Act, exercise the powers of entry for inspection purposes in Subsection 12 (1) of the Act, and

(b)	exercise the powers of an inspector under Section 18 of the Act.

(4)  Sections 15.23 and 19 of the Act apply to the exercise of powers under this Article by the director and employees of the Ministry of Municipal Affairs and Housing designated by the director.

2.14.  Prescribed Person

2.14.1.  General

2.14.1.1.  General

(1)  The director is prescribed for the purposes of Section 38.1 of the Act.

2.15. Enforcement of the Provisions of the Act and Building Code Related to Sewage Systems

2.15.1.  General

2.15.1.1.  General

(1)  Pursuant to Subsection 3.1 (1) of the Act, the boards of health and conservation authorities listed in Column 1 of Table 2.15.1.1. shall enforce the provisions of the Act and the building code related to sewage systems in the municipalities and the territory without municipal organization described in Column 2 of Table 2.15.1.1.

Table 2.15.1.1.

| Enforcement of the provisions of the Act and the Building Code related to Sewage Systems |  |
| --- | --- |
| Board of Health or Conservation Authority | Geographic Area |
| Board of Health for the Northwestern Health Unit | All municipalities and territory without municipal organization located in the Northwestern Health Unit |
| Board of Health for the Thunder Bay District Health Unit | All municipalities and territory without municipal organization located in the Thunder Bay District Health Unit |
| Board of Health for the Porcupine Health Unit | All municipalities and territory without municipal organization located in the Porcupine Health Unit |
| Board of Health for the District of Algoma Health Unit | All municipalities and territory without municipal organization located in the District of Algoma Health Unit |
| Board of Health for the Sudbury and District Health Unit | All municipalities and territory without municipal organization located in the Sudbury and District Health Unit |
| Board of Health for the Timiskaming Health Unit | All municipalities and territory without municipal organization located in the Timiskaming Health Unit |
| North Bay-Mattawa Conservation Authority | All municipalities and territory without municipal organization located in: |
|  | 1. the District of Nipissing, except those parts of the District of Nipissing located in the Temiskaming Health Unit, and |
|  | 2. the District of Parry Sound except for the Township of The Archipelago, the geographic Townships of Blair, Brown, Harrison, Henvey, Mowat and Wallbridge and the unsurveyed territory north of the geographic Township of Henvey to the French River. |
| Column 1 | Column 2 |

Section 2.16. Qualifications for Chief Building Officials and Inspectors

2.16.1. Scope

2.16.1.1.  Scope

(1)  Except as provided in Sentence (2), this Section prescribes, for the purposes of Subsections 15.11 (1), (2) and (3) of the Act

(a)	the qualifications that a person must satisfy to be appointed after December 31, 2005 and to remain appointed after that day as

(i)	a chief building official under the Act, or

(ii)	an inspector who has the same powers and duties as a chief building official in relation to plumbing,

(b)	the qualifications that a person must satisfy to be appointed on or after the day this Article comes into force and to remain appointed after that day

(i)	as an inspector who has the same powers and duties as a chief building official in relation to sewage systems, or

(ii)	as an inspector whose duties include plans review or inspection under the Act of sewage systems, and

(c)	the qualifications that a person must satisfy to be appointed after December 31, 2005 and to remain appointed after that day as an inspector under the Act, other than an inspector described in Subclause (a)(ii) or (b)(i) or (ii).

(2)  The qualification requirements for chief building officials and inspectors in Sentence (1) do not apply to plan review and inspection of:

(a)	site services including

(i)	surface drainage, and

(ii)	plumbing located underground either outside a building or under a building,

(b)	construction of a factory-built house certified to CAN/CSA-A277 “Procedure for Certification of Factory-Built Houses”,

(c)	construction of a mobile home conforming to CAN/CSA-Z240 Series “Mobile Homes”,

(d)	construction of a park model trailer conforming to CAN/CSA-Z241 Series “Park Model Trailers”, or

(e)	signs.

2.16.2. Chief Building Officials

2.16.2.1.  Qualifications

(1)  The following are prescribed as qualifications for a person to be appointed and to remain appointed under the Act as a chief building official or as an inspector who has the same powers and duties as a chief building official in relation to sewage systems or plumbing:

(a)	the person shall successfully complete the examination program administered or authorized by the Ministry of Municipal Affairs and Housing relating to the person’s knowledge of the Act and this Code and the powers and duties of chief building officials,

(b)	if, under Subsection 22 (2) of the Act, the person will also exercise any of the powers or perform any of the duties of an inspector, the person shall also have the qualifications contained in Sentence 2.16.4.1(1), and

(c)	the person shall file the information set out in Sentence 2.16.6.1.(1) with the director in a form established by the director.

(2)  An inspector who has the same powers and duties as a chief building official in relation to sewage systems and who had, on the day before the day this Article came into force, the qualification described in Article 2.11.3.1. as it read on that day:

(a)	shall be deemed to have successfully completed the examination programme described in Clause (1)(a),

(b)	shall be deemed to have successfully completed the examination program described in Clause 2.16.4.1.(1)(a) in the category of qualification described in Column 3 of Row 10 of Table 2.20.2.1., and

(c)	shall be deemed to have filed with the director the information required in Clause (1)(c) if the person filed with the director, before the day this Article came into force, the information required under Article 2.11.3.1. as that Article read on the day before the day this Article came into force.

(3)  A person is required to have the qualifications set out in Sentence (1) in accordance with the following rules:

1.	A person appointed as a chief building official shall have the qualifications set out in Sentence (1) on and after the later of

i.	January 1, 2006, and

ii.	the day he or she is appointed as a chief building official.

2.	A person appointed as an inspector who has the same powers and duties as a chief building official in relation to plumbing shall have the qualifications set out in Sentence (1) on and after the later of

i.	January 1, 2006, and

ii.	the day he or she is appointed as an inspector who has the same powers and duties as a chief building official in relation to plumbing.

3.	A person appointed as an inspector who has the same powers and duties as a chief building official in relation to sewage systems shall have the qualifications set out in Sentence (1) on and after the later of

i.	the day this Article comes into force, and

ii.	the day he or she is appointed as an inspector who has the same powers and duties as a chief building official in relation to sewage systems.

2.16.3. Supervisors and Managers

2.16.3.1.  Qualifications

(1)  The following are prescribed as the qualifications for a person to be appointed after December 31, 2005 and to remain appointed under the Act after that day as an inspector whose duties are solely the supervision or management of inspectors:

(a)	the person shall successfully complete the examination program administered or authorized by the Ministry of Municipal Affairs and Housing of the person’s knowledge of the Act and this Code and the powers and duties of chief building officials,

(b)	the person shall successfully complete the examination program administered by the Ministry of Municipal Affairs and Housing of the person’s knowledge of the Act and this Code related to any one category of qualification set out in Column 3 of Table 2.20.2.1., and

(c)	the person shall file the information set out in Sentence 2.16.6.1.(1) with the director in a form established by the director.

2.16.4. Inspectors

2.16.4.1.  Qualifications

(1)  Except as provided in Article 2.16.4.2., the following are prescribed as qualifications for a person to be appointed and to remain appointed under the Act as an inspector whose duties include plans review or inspection under the Act:

(a)	the person shall successfully complete the examination program administered or authorized by the Ministry of Municipal Affairs and Housing relating to the person’s knowledge of the Act and this Code in the category or categories of qualifications in Column 3 of Table 2.20.2.1. that correspond to the types of buildings set out in Column 4 of Table 2.20.2.1. in respect of which the person will exercise the powers or perform the duties of an inspector under the Act, and

(b)	the person shall file the information set out in Sentence 2.16.6.1.(1) with the director in a form established by the director.

(2)  An inspector who had, on the day before the day this Section came into force, the qualification described in Article 2.11.3.1., as it read on that day

(a)	shall be deemed to have successfully completed the examination program described in Clause (1)(a) in the category of qualification described in Column 3 of Row 10 of Table 2.20.2.1., and

(b)	shall be deemed to have filed with the director the information required in Clause (1)(c) if the person filed with the director, before the day this Section came into force, the information required under Article 2.11.3.1. as it read on that day.

(3)  A person is required to have the qualifications set out in Sentence (1) in accordance with the following rules:

1.	A person appointed as an inspector whose duties include plans review and inspection of sewage systems under the Act shall have the qualifications set out in Sentence (1) on and after the later of

i.	September 1, 2003, and

ii.	the day on which he or she is appointed as an inspector whose duties include plans review and inspection of sewage systems.

2.	A person appointed as an inspector, other than an inspector described in paragraph 1, shall have the qualifications set out in Sentence (1) on and after the later of

i.	January 1, 2006, and

ii.	the day on which he or she is appointed as an inspector.

2.16.4.2.  Qualifications for Intern Inspectors

(1)  A person appointed under the Act as an intern inspector whose duties include supervised plans review or inspection under the Act is exempt from the requirements in Article 2.16.4.1. if

(a)	the person is enrolled in an internship program approved by the Minister, and

(b)	the person is supervised by an inspector or chief building official who meets the category of qualification in respect of which the person will exercise the powers or perform the duties.

(2)  An intern inspector described in Clause (1)(a) shall not issue orders under the Act except orders under Subsections 12 (2) or 13 (1) of the Act.

(3)  An intern inspector described in Clause (1)(a) shall not undertake a site inspection of a building related to a notice in respect of

(a)	substantial completion of footings and foundations prior to commencement of backfilling, or

(b)	completion of construction and installation of components required to permit the issuance of an occupancy permit under Sentence 2.4.3.1.(2) or to permit occupancy under Sentence 2.4.3.2.(1), if the building or part of the building to be occupied is not fully completed.

2.16.5. Updating of Qualifications

2.16.5.1.  Updating of Qualifications

(1)  When an examination that is part of an examination program referred to in Clause 2.16.2.1.(1)(a), 2.16.3.1.(1)(a) or (b) or 2.16.4.1.(1)(a) or (b) is replaced with a new examination, the director shall give notice of the new examination to every person who has, pursuant to Clause 2.16.2.1.(1)(c), 2.16.3.1(1)(c) or 2.16.4.1.(1)(c), informed the director that the person completed the examination before it was replaced or who is deemed to have successfully completed the examination program.

(2)  The director may give the notice referred to in Sentence (1) by sending it by regular letter mail to the last address of the person filed with the director.

(3)  It is a prescribed qualification for the purposes of Subsections 15.11 (1), (2) and (3) of the Act that, not later than 180 days after the day on which a notice referred to in Sentence (1) is sent, the person to whom the notice is given shall:

(a)	successfully complete all new examinations referred to in the notice, and

(b)	file the information set out in Sentence 2.16.6.1.(1) with the director in a form established by the director.

2.16.6. Information

2.16.6.1.  Qualifications

(1)  The information referred to in Clauses 2.16.2.1.(1)(c), 2.16.3.1.(1)(c), 2.16.4.1.(1)(c) and 2.16.5.1.(3)(b) is the following:

(a)	the person’s name, residence address and residential mailing address, if different from the residence address,

(b)	the name and address of every principal authority that has appointed the person as a chief building official or inspector under the Act, and

(c)	information about the examinations that the person has successfully completed, in such form and in such detail as may be required by the director.

(2)  A person who files information under Sentence (1) with the director shall advise the director of any change of the information not later than 15 days after the change.

2.16.7. Fees

2.16.7.1.  Fees

(1)  The fee payable upon the filing of information under Clause 2.16.2.1.(1)(c), 2.16.3.1.(1)(c), 2.16.4.1.(1)(c) or 2.16.5.1.(3)(b) is $80.

(2)  The amount of a fee referred to in Sentence (1) is reduced by $10 if the information is filed and the fee is paid in accordance with a means of electronic filing and payment specified by the director.

(3)  The Ministry of Municipal Affairs and Housing may charge a fee to a person who takes an examination for the purposes of this Section.

2.16.8. Public Register

2.16.8.1.  Public Register

(1)  The director shall establish and maintain a register available to the public listing every person who has the qualifications required by Subsections 15.11 (1), (2) and (3) of the Act and has been appointed as a chief building official or inspector by a principal authority.

(2)  The register referred to in Sentence (1) shall contain the following information with respect to each person listed in it:

(a)	the name of the person,

(b)	any identifying number assigned by the director to that person,

(c)	the name of each principal authority that has appointed the person as a chief building official or inspector, and

(d)	the qualifications of the person.

2.16.9. Categories of Qualifications

2.16.9.1.  Categories

(1)  Table 2.20.2.1. contains the categories of qualifications for the purposes of this Section.

Section 2.17.  Qualifications for Designers

2.17.1. Scope

2.17.1.1.  Scope

(1)  This Section prescribes, for the purposes of Clause 8 (2) (c) and Subsection 15.11 (5) of the Act, the qualifications for a person who carries out design activities after December 31, 2005.

2.17.2. General

2.17.2.1.  Persons Engaged in the Business of Providing Design Activities to the Public

(1)  Every person engaged in the business of providing design activities to the public after December 31, 2005, other than a person who is the holder of a Certificate of Practice or a Temporary Licence issued under the Architects Act, must have the qualification set out in Sentence 2.17.4.1.(1).

2.17.2.2.  Other Designers

(1)  Every person who carries out design activities after December 31, 2005, other than an architect, must have the qualifications set out in Sentence 2.17.5.1.(1) if the person is not required to have the qualification set out in Sentence 2.17.4.1.(1).

2.17.3. Definition

2.17.3.1.  Definition

(1)  In this Section,

registered means registered under Article 2.17.4.2.

2.17.4. Qualifications — Persons Engaged in the Business of Providing Design Activities to the Public

2.17.4.1.  General

(1)  Except as provided in Sentences (3) and (4), every person engaged in the business of providing design activities to the public after December 31, 2005 must have the following qualification:

(a)	The person must be registered with the director.

(2)  A registration shall be in a form established by the director.

(3)  A person is exempt from the requirement to comply with the qualification in Sentence (1) if the person’s design activities relate only to

(a)	construction of a home as defined under the Ontario New Home Warranties Plan Act that will be constructed or sold by that person, if the person is a builder or vendor as defined in that Act and is registered under that Act,

(b)	construction of a building that is owned by that person,

(c)	construction of a farm building that is

(i)	of low human occupancy,

(ii)	of 2 storeys or less in building height, and

(iii)	has a building area of less than 600 m²,

(d)	the extension, material alteration or repair of:

(i)	a detached house, semi-detached house, townhouse or row house containing not more than two dwelling units in each house, or

(ii)	a detached structure that serves a building described in Subclause (3)(d)(i) and does not exceed 50 m2 in building area,

(e)	a sewage system to be constructed by that person if the person is registered under Article 2.18.3.2.,

(f)	construction of tents described in Sentence 3.13.1.2.(2),

(g)	construction of signs,

(h)	construction of site services, including

(i)	surface drainage, and

(ii)	plumbing located underground, either outside a building or under a building,

(i)	construction of a factory-built house certified to CAN/CSA-A277 “Procedure for Certification of Factory-Built Houses”,

(j)	construction of a mobile home conforming to CAN/CSA-Z240 Series “Mobile Homes”,

(k)	construction of a park model trailer conforming to CAN/CSA-Z241 Series “Park Model Trailers”,

(l)	construction of pre-engineered elements of a building if the design of the elements is carried out by a person competent in the specific discipline appropriate to the circumstances,

(m)	construction of appliances, equipment and similar incidental components of a building, or

(n)	construction of a building for which a permit under Section 8 of the Act is applied for or issued before January 1, 2006 and for which construction is commenced within six months after the permit is issued.

(4)  A person is exempt from the requirements to comply with the qualification in Sentence (1) if the person’s design activities are with respect to a detached house, semi-detached house, townhouse or row house containing not more than two dwelling units in each house and the design activities relate only to

(a)	a plumbing system,

(b)	a heating, ventilation and air conditioning system, or

(c)	ancillary buildings such as garages.

2.17.4.2.  Registration and Renewal of a Registration

(1)  Subject to Article 2.17.4.9., the director may register an applicant, or renew a registration, in each class of registration applied for, if

(a)	the applicant or registered person or, if the applicant or registered person is a corporation or partnership, a director, officer, partner or employee of the applicant or registered person, has successfully completed the examination program administered or authorized by the Ministry of Municipal Affairs and Housing relating to the person’s knowledge of the Act and this Code in the category of qualification set out on Column 3 of Table 2.20.2.1. that corresponds to each class of registration set out in Column 2 of Table 2.20.2.1. for which application is made,

(b)	all persons who will review and take responsibility for design activities provided to the public by the applicant or registered person for the purposes of Clause 2.17.4.7.(1)(d) have successfully completed the examination program administered or authorized by the Ministry of Municipal Affairs and Housing relating to the person’s knowledge of the Act and this Code in the category of qualification set out on Column 3 of Table 2.20.2.1. that correspond to each class of registration set out in Column 2 of Table 2.20.2.1. for which application is made,

(c)	the applicant or registered person is covered by the insurance required under Subsection 2.21.2. during the term of the registration applied for,

(d)	the application is complete, and

(e)	all fees required under Article 2.17.4.5. are paid.

2.17.4.3.  Application for Registration or Renewal of a Registration

(1)  An application for registration or renewal of a registration shall be made to the director in a form established by the director.

(2)  An application for renewal of a registration shall be made at least 60 days before the expiry of the registration to be renewed.

(3)  An application for registration or renewal of a registration shall include an undertaking by the applicant or registered person to comply with the conditions set out in Article 2.17.4.7.

(4)  If a partnership or a corporation is the applicant for registration or renewal of registration, the application shall set out the names and residence addresses of all of its partners, directors or officers, as the case may be.

(5)  An application for registration or renewal of a registration shall contain the names of all partners, directors, officers or employees of the applicant or registered person, as the case may be, and all other persons engaged by the applicant or registered person who:

(a)	have the qualifications set out in Clause 2.17.4.2.(1)(a) in the class or classes of registration for which the application is made, and

(b)	have the qualifications set out in Clause 2.17.4.2.(1)(b) and will review and take responsibility for the design activities provided to the public by the applicant or registered person in the class or classes of registration for which the application is made.

(6)  An application for registration or renewal of a registration shall contain evidence, provided by the applicant or registered person, that the persons referred to in Sentence (5) meet the qualifications set out in Clauses 2.17.4.2.(1)(a) and (b).

(7)  An application for registration or renewal of a registration shall contain evidence, provided by the applicant or registered person, that the applicant or registered person is covered by the insurance required under Subsection 2.21.2. during the term of the registration applied for.

2.17.4.4.  Term

(1)  A registration expires one year after it is issued but the director may, for the purposes of staggering the renewal dates of the registrations, issue the initial registration for a term of not less than 90 days and not more than 18 months.

2.17.4.5.  Fees

(1)  The fee for a registration is $125.

(2)  The fee for a registered person to add a new class of registration is $25.

(3)  The fee for renewal of a registration is $80.

(4)  The amount of a fee referred to in Sentence (1), (2) or (3) is reduced by 15 per cent and rounded to the nearest whole dollar if the application is made and the fee is paid in accordance with a means of electronic filing and payment specified by the director.

(5)  The Ministry of Municipal Affairs and Housing may charge a fee to a person who takes an examination for the purposes of this Subsection.

2.17.4.6.  Not Transferable

(1)  A registration is not transferable.

2.17.4.7.  Conditions

(1)  The following are the conditions of a registration:

(a)	the registered person shall carry out design activities only in respect of the type of building described in Column 4 of Table 2.20.2.1. that correspond to the class or classes of registration held by the registered person,

(b)	if the registered person is a corporation or partnership, there must throughout the term of the registration be an officer, director, partner or employee of the registered person who has the qualifications set out in Clause 2.17.4.2.(1)(a) for each class of registration set out in Column 2 of Table 2.20.2.1. that is held by the registered person,

(c)	not more than 180 days after the day a notice is given under Sentence 2.17.4.8.(1) by the director to the registered person, the registered person shall

(i)	ensure that the registered person and the persons described in Clause (b) have successfully completed all new examinations referred to in the notice, and

(ii)	provide the following information to the director:

(A)	the names of all persons described in Subclause (i), and

(B)	information about the examinations that the persons described in Subclause (i) have successfully completed, in such form and in such detail as may be required by the director,

(d)	the registered person shall ensure that a person described in Clause (b) or another person who has the qualifications set out in Clause 2.17.4.2.(1)(b) in respect of the class of registration set out in Column 2 of Table 2.20.2.1. to which the design activities relate will review and take responsibility for design activities in each class of registration that are provided to the public by the registered person,

(e)	not more than 180 days after the day when a notice is given under Sentence 2.17.4.8.(1) by the director to the registered person, the registered person shall:

(i)	ensure that persons described in Clause (d) who will review and take responsibility for design activities provided to the public by the registered person in the class of registration to which the notice relates, have successfully completed all new examinations referred to in the notice, and

(ii)	provide the following information to the director:

(A)	the names of all persons described in Subclause (i), and

(B)	information about the examinations that the persons referred to in Subclause (i) have successfully completed, in such form and in such detail as may be required by the director,

(f)	the registered person shall ensure that a person described in Clause (d) who reviews and takes responsibility for design activities provided to the public by the registered person shall include the following information on any document submitted to a chief building official or registered code agency in the circumstances set out in Subsection 15.11 (5) of the Act:

(i)	the name of the registered person and any registration number issued to the registered person by the director,

(ii)	a statement that the person has reviewed and taken responsibility for the design activities,

(iii)	the person’s name and any identifying number issued to the person by the director in respect of the qualifications described in Clause 2.17.4.2.(1)(b), and

(iv)	the person’s signature,

(g)	the registered person shall, during the term of the registration, be covered by the insurance required under Subsection 2.21.2.,

(h)	the registered person shall, within 15 days after the event, notify the director in writing of

(i)	any change in address of the registered person for correspondence relating to the registration, and

(ii)	any change in the information set out in Sentences 2.17.4.3.(4) and (5),

(i)	the registered person shall give prompt written notice to the director of any material change in any of the information, other than the information referred to in Clause (h), that is contained in or accompanies an application for registration or renewal of a registration,

(j)	the registered person shall, from time to time, at the registered person’s expense, give the director such documents or information relating to the registration or to activities carried out under the registration as the director may reasonably require,

(k)	the registered person shall allow the representatives of the director access to the registered person’s books and records during normal business hours for the purpose of confirming matters related to the registration.

2.17.4.8.  Updating of Qualifications

(1)  Where an examination referred to in Clause 2.17.4.2.(1)(a) or (b) is replaced with a new examination, the director shall give notice of the new examination to every registered person who is registered in a class of registration to which the new examination relates.

(2)  The director may give the notice referred to in Sentence (1) by sending it by regular letter mail to the last address of the registered person that has been provided to the director.

2.17.4.9.  Suspension, Revocation, Refusal to Register or Renew a Registration

(1)  The director may, in the circumstances set out in Sentence (2):

(a)	refuse to register an applicant or to renew a registration, or

(b)	suspend or revoke a registration.

(2)  The circumstances referred to in Sentence (1) are:

(a)	the registered person is in contravention of the Act or this Code,

(b)	the registered person is in breach of a condition of the registration other than the condition set out in Clause 2.17.4.7.(1)(g),

(c)	the registration was issued on the basis of mistaken, false or incorrect information,

(d)	the director is of the opinion that the past conduct of the applicant or registered person or, if the applicant or registered person is a partnership or a corporation, the partners, officers or directors of the registered person, as the case may be, affords reasonable grounds for belief that the business that would be or is authorized by the registration will not be carried on in accordance with law,

(e)	the application is incomplete, or

(f)	any fees required under Article 2.17.4.5. remain unpaid.

(3)  If the director proposes to refuse to register or renew a registration or proposes to suspend or revoke a registration under Sentence (1), the director shall serve a notice of the proposal, together with the reasons for it, on the applicant or registered person.

(4)  A notice under Sentence (3) shall state that the applicant or registered person is entitled to a hearing before the Tribunal if the applicant or registered person, within 15 days after service of the notice referred to in Sentence (3), serves the director and the Tribunal with notice in writing requesting a hearing.

(5)  If the applicant or registered person does not request a hearing by the Tribunal in accordance with Sentence (4), the director may carry out the proposal stated in the notice under Sentence (3).

(6)  If the applicant or registered person requests a hearing before the Tribunal in accordance with Sentence (4), the Tribunal shall appoint a time for and hold a hearing and may by order direct the director to carry out the director’s proposal or refrain from carrying it out and to take such other action as the Tribunal considers the director ought to take in accordance with the Act and this Code, and for those purposes the Tribunal may substitute its opinion for that of the director.

(7)  The director, the applicant or registered person who requested the hearing, and such other persons as the Tribunal may specify, are parties to proceedings before the Tribunal.

(8)  Sentences (3) to (7) do not apply and the director may cancel the registration of a registered person upon receipt of a request in writing for cancellation from the registered person in a form established by the director.

(9)  If, within the time period set out in Sentence 2.17.4.3.(2), a registered person has applied for renewal of a registration, paid the fee required under Article 2.17.4.5. and provided evidence satisfactory to the director that the registered person is covered by insurance required under Subsection 2.21.2. for the term of the renewal of the registration, the registration shall be deemed to continue until the earliest of

(a)	the day the registration is renewed,

(b)	if the registered person is served with notice that the director proposes to refuse to renew the registration, the day the time for giving notice requesting a hearing expires or, if a hearing is held, the day the Tribunal makes its order, and

(c)	the day when the registered person ceases to be covered by the insurance required under Subsection 2.21.2.

2.17.4.10.  Mandatory Suspension or Revocation of Registration or Refusal to Register or Renew Registration

(1)  The director shall, in the circumstances set out in Sentence (2)

(a)	refuse to register an applicant,

(b)	refuse to renew a registration, or

(c)	suspend or revoke a registration.

(2)  The circumstances referred to in Sentence (1) are that

(a)	the applicant or registered person is not covered by the insurance required under Subsection 2.21.2., or

(b)	an order under Subsection 69 (2) of the Provincial Offences Act is in effect directing that the registration of the person be suspended and no registration be issued to the person until a fine is paid.

(3)  If the director refuses to register an applicant, refuses to renew a registration or suspends or revokes a registration under Sentence (1), the director shall serve a notice of the refusal, suspension or revocation, together with the reasons for it, on the registered person.

(4)  A suspension or revocation of a registration under Sentence (1) takes effect immediately and the commencement of a proceeding before the Tribunal does not stay the operation of the suspension or revocation of the registration.

(5)  A notice under Sentence (3) shall state that the registered person is entitled to a hearing before the Tribunal if the registered person, within 15 days after service of the notice referred to in Sentence (3), serves the director and the Tribunal with notice in writing requesting a hearing.

(6)  The Tribunal may, on the application of the registered person, stay the operation of a decision of the director to suspend or revoke the registration and may grant the stay subject to conditions.

(7)  If a registered person requests a hearing before the Tribunal in accordance with Sentence (5), the Tribunal shall appoint a time for and hold a hearing and may by order confirm, alter or revoke the decision of the director to refuse to register or to suspend or revoke the registration, as the case may be, and may take such action as the Tribunal considers the director ought to take in accordance with the Act and this Code, and for those purposes the Tribunal may substitute its opinion for that of the director.

(8)  The director and the registered person who requested the hearing, and such other persons as the Tribunal may specify, are parties to proceedings before the Tribunal.

2.17.5. Qualifications — Other Designers

2.17.5.1.  General

(1)  Except as provided in Sentence (2), a person who carries out design activities after December 31, 2005 but is not required under Sentence 2.17.4.1.(1) to be registered with the director must have the following qualifications:

(a)	he or she shall successfully complete the examination program administered or authorized by the Ministry of Municipal Affairs and Housing relating to his or her knowledge of the Act and this Code in the category of qualification set out in Column 3 of Table 2.20.2.1. that corresponds to the type of buildings described in Column 4 of Table 2.20.2.1. for which the person carries out design activities,

(b)	he or she shall file the information set out in Sentence 2.17.5.3.(1) with the director in a form established by the director, and

(c)	he or she shall include the following information on any document respecting design activities that the person has reviewed and taken responsibility for and that is submitted to a chief building official or registered code agency in the circumstances set out in Subsection 15.11 (5) of the Act:

(i)	the person’s name and any identifying number issued to the person issued by the director in respect of the qualifications described in Clause (a),

(ii)	a statement that the person has reviewed and taken responsibility for the design activities, and

(iii)	the person’s signature.

(2)  A person is exempt from the requirement to comply with the qualifications in Sentence (1) if his or her design activities relate only to

(a)	design activities in respect of which a person described in Clause 2.17.4.7.(1)(d) or who has the qualifications required under Sentence (1) will review and take responsibility,

(b)	construction of:

(i)	a detached house, semi-detached house, townhouse or row house owned by the person and containing not more than two dwelling units in each house, or

(ii)	an ancillary building that serves a building described in Subclause (i),

(c)	construction of a farm building that

(i)	is of low human occupancy,

(ii)	is 2 storeys or less in building height, and

(iii)	has a building area of less than 600 m²,

(d)	a sewage system to be constructed by that person and:

(i)	the person is registered under Article 2.18.3.2., or

(ii)	the sewage system is owned by the person,

(e)	construction of tents described in Sentence 3.13.1.2.(2),

(f)	construction of signs,

(g)	construction of site services including

(i)	surface drainage, and

(ii)	plumbing located underground either outside a building or under a building,

(h)	construction of pre-engineered elements of a building provided that the design of the elements is carried out by a person competent in the specific discipline appropriate to the circumstances,

(i)	construction of appliances, equipment and similar incidental components of a building,

(j)	construction of an ancillary building

(i)	that serves a detached house, semi-detached house, townhouse or row house if the house contains not more than two dwelling units, and

(ii)	that does not exceed 50 m2 in building area, or

(k)	construction of a building for which a permit under Section 8 of the Act is applied for or issued before January 1, 2006 and for which construction commences within six months after the permit is issued.

2.17.5.2.  Updating of Qualifications

(1)  When an examination that is part of an examination program referred to in Clause 2.17.5.1.(1)(a) is replaced with a new examination, the director shall give notice of the new examination to every person who has, pursuant to Clause 2.17.5.1.(1)(b), informed the director that he or she has completed the examination before its replacement.

(2)  The director may give the notice referred to in Sentence (1) by sending it by regular letter mail to the last address of the person that has been filed with the director.

(3)  It is a prescribed qualification for the purposes of Clause 8 (2) (c) and Subsection 15.11 (5) of the Act that, not more than 180 days after the day on which the notice referred to in Sentence (1) is given, the person to whom the notice is given shall:

(a)	successfully complete all new examinations referred to in the notice, and

(b)	file the information set out in Sentence 2.17.5.3.(1) with the director in a form established by the director.

2.17.5.3.  Information

(1)  The information referred to in Clauses 2.17.5.1.(1)(b) and 2.17.5.2.(3)(b) is the following:

(a)	the person’s name, residence address and residential mailing address, if different from the residence address, and

(b)	information about the examinations that the person has successfully completed, in such detail as may be required by the director.

(2)  A person who has filed information under Sentence (1) with the director shall advise the director of any change of address within 15 days of the change.

2.17.5.4.  Fees

(1)  The fee payable upon the filing of information referred to in Clause 2.17.5.1.(1)(b) or 2.17.5.2.(3)(b) is $80.

(2)  The amount of a fee referred to in Sentence (1) is reduced by $10 if the information is filed and the fee is paid in accordance with a means of electronic filing and payment specified by the director.

(3)  The Ministry of Municipal Affairs and Housing may charge a fee to a person who takes an examination for the purposes of this Section.

2.17.6. Public Register

2.17.6.1.  Public Register

(1)  The director shall establish and maintain a register available to the public that lists every person who has the qualifications required by Clause 8 (2) (c) and Subsection 15.11 (5) of the Act.

(2)  The register referred to in Sentence (1) shall contain the following information in respect of every registered person:

(a)	the name of the registered person,

(b)	any identifying number assigned by the director to the registered person,

(c)	the business address of the registered person,

(d)	classes of registration of the registered person,

(e)	the names of the person or persons who will review and take responsibility for design activities carried out by the registered person in each class of registration, and

(f)	any identifying number assigned by the director to the person or persons referred to in Clause (e).

(3)  The register referred to in Sentence (1) shall contain the following information in respect of persons who have the qualifications referred to in Sentence 2.17.5.1.(1):

(a)	the name of the person,

(b)	any identifying number assigned by the director to the person,

(c)	the qualifications of that person.

2.17.7. Classes of Registration and Categories of Qualifications

2.17.7.1.  Classes and Categories

(1)  Table 2.20.2.1. contains the classes of registration and categories of qualifications for the purposes of this Section.

Section 2.18. Qualifications for Persons Engaged in the Business of Constructing On Site, Installing, Repairing, Servicing, Cleaning or Emptying Sewage Systems

2.18.1. Scope

2.18.1.1.  Scope

(1)  This Section prescribes, for the purposes of Subsection 15.12 (1) of the Act, the qualifications for persons engaged in the business of constructing on site, installing, repairing, servicing, cleaning or emptying sewage systems after this Section comes into force.

2.18.2. Definition

2.18.2.1.  Definition

(1)  In this Section,

registered means registered under Article 2.18.3.2.

2.18.3. Qualifications

2.18.3.1.  General

(1)  Commencing on the day this Section comes into force, persons engaged in the business of constructing on site, installing, repairing, servicing, cleaning or emptying sewage systems shall have the following qualification:

(a)	The person must be registered with the director.

(2)  A registration shall be in a form established by the director.

(3)  A license issued under Sentence 2.12.3.1. of this Code, as that Sentence read immediately before the day this Section came into force, shall be deemed to be a registration for the purposes of Clause (1)(a).

(4)  A person is exempt from the requirement to comply with the qualification in Sentence (1) in respect of the activities of cleaning and emptying sewage systems if the person has been issued a certificate of approval under Section 39 of the Environmental Protection Act in respect of the activities of cleaning and emptying sewage systems.

2.18.3.2.  Registration and Renewal of a Registration

(1)  Subject to Article 2.18.3.9., the director may register an applicant, or renew a registered person’s registration, if

(a)	all persons who will supervise construction on site, installation, repair, servicing, cleaning or emptying sewage systems carried out by the applicant or registered person have successfully completed the examination program administered or authorized by the Ministry of Municipal Affairs and Housing relating to the person’s knowledge of the Act, this Code and the construction, maintenance and operation of sewage systems,

(b)	the application is complete, and

(c)	all fees required under Article 2.18.3.5. are paid.

(2)  A person who had, on the day before the day this Subsection came into force, the qualification described in Subclause 2.12.4.6.(1)(a), as it read on that day, shall be deemed to have successfully completed the examination program described in Clause (1)(a).

2.18.3.3.  Application for Registration or Renewal of a Registration

(1)  An application for registration or renewal of a registration shall be made to the director in a form established by the director.

(2)  An application for renewal of a registration shall be made at least 60 days before the expiry of the registration to be renewed.

(3)  An application for registration or renewal of a registration shall include an undertaking by the applicant or registered person to comply with the conditions set out in Article 2.18.3.7.

(4)  If a partnership or a corporation is the applicant for registration or renewal of a registration, the application shall set out the names and residence addresses of all its partners, directors or officers, as the case may be.

(5)  An application for registration or renewal of a registration shall contain the names  of all partners, directors, officers or employees of the applicant or registered person, as the case may be, and all other persons who have been engaged by the applicant or registered person, who:

(a)	have the qualifications set out in Clause 2.18.3.2.(1)(a), and

(b)	will supervise the construction on site, installation, repair, servicing, cleaning or emptying of sewage systems to be carried out by the applicant or registered person.

(6)  An application for registration or renewal of a registration shall contain evidence, provided by the applicant or registered person, that the persons referred to in Sentence (5) meet the qualifications set out in Clause 2.18.3.2.(1)(a).

2.18.3.4.  Term

(1)  A registration expires 3 years after the date of its issuance.

2.18.3.5.  Fees

(1)  The fee for a registration or renewal of a registration is $50.

(2)  The amount of a fee referred to in Sentence (1) is reduced by $5 if the application is made and the fee is paid in accordance with a means of electronic filing and payment specified by the director.

(3)  The Ministry of Municipal Affairs and Housing may charge a fee to a person who takes an examination for the purposes of this Section.

2.18.3.6.  Not Transferable

(1)  A registration is not transferable.

2.18.3.7.  Conditions

(1)  The following are the conditions of a registration:

(a)	the registered person shall ensure that the construction on site, installation, repair, servicing, cleaning or emptying of sewage systems carried out by the registered person is supervised by a person who has the qualifications set out in Clause 2.18.3.2.(1)(a),

(b)	not more than 180 days after the day a notice is given under Sentence 2.18.3.8.(1) by the director to the registered person, the registered person shall:

(i)	ensure that the construction on site, installation, repair, servicing, cleaning or emptying of sewage systems carried out by the registered person is supervised by persons who have successfully completed the new examinations referred to in the notice, and

(ii)	provide the following information to the director:

(A)	the name of the person or persons carrying out the supervision, and

(B)	information about the examinations that the person or persons have successfully completed, in such detail as may be required by the director,

(c)	the registered person shall, within 15 days after the event, notify the director in writing

(i)	of any change in address of the registered person for correspondence relating to the registration, and

(ii)	of any change in the information set out in Sentences 2.18.3.3.(4) and (5),

(d)	the registered person shall give prompt written notice to the director of any material change in any of the information other than the information referred to in Clause (1)(c) that is contained in or accompanies an application for registration or renewal of a registration,

(e)	the registered person shall, from time to time, at the registered person’s expense, give the director such documents or information relating to the registration or to activities carried out under the registration as the director may reasonably require, and

(f)	the registered person shall allow the representatives of the director access to the registered person’s books and records during normal business hours for the purpose of confirming matters related to the registration.

2.18.3.8.  Updating of Qualifications

(1)  When an examination that is part of an examination program referred to in Clause 2.18.3.2.(1)(a) is replaced with a new examination, the director shall give notice of the new examination to every registered person.

(2)  The director may give the notice referred to in Sentence (1) by sending it by regular letter mail to the last address of the registered person that has been provided to the director.

2.18.3.9.  Suspension, Revocation, Refusal to Register or Renew a Registration

(1)  The director may, in the circumstances set out in Sentence (2):

(a)	refuse to register an applicant or renew a registration, or

(b)	suspend or revoke a registration.

(2)  The circumstances referred to in Sentence (1) are:

(a)	the registered person is in contravention of the Act or this Code,

(b)	the registered person is in breach of a condition of the registration,

(c)	the registration was issued on the basis of mistaken, false or incorrect information,

(d)	the director is of the opinion that the past conduct of the applicant or registered person or, if the applicant or registered person is a partnership or a corporation, the partners, officers or directors of the registered person, as the case may be, affords reasonable grounds for belief that the business that would be or is authorized by the registration will not be carried on in accordance with law,

(e)	an order under Subsection 69 (2) of the Provincial Offences Act is in effect directing that the registration of the person be suspended and that no registration be issued to that person until a fine is paid,

(f)	the application is incomplete, or

(g)	any fees required under Article 2.18.3.5. remain unpaid.

(3)  If the director proposes to refuse to register or renew a registration or proposes to suspend or revoke a registration, the director shall serve a notice of the proposal, together with the reasons for it, on the applicant or registered person.

(4)  A notice under Sentence (3) shall state that the applicant or registered person is entitled to a hearing before the Tribunal if the applicant or registered person, within 15 days after service of the notice referred to in Sentence (3), serves the director and the Tribunal with notice in writing requesting a hearing.

(5)  If an applicant or registered person does not request a hearing by the Tribunal in accordance with Sentence (4), the director may carry out the proposal stated in the notice under Sentence (3).

(6)  If an applicant or registered person requests a hearing before the Tribunal in accordance with Sentence (4), the Tribunal shall appoint a time for and hold a hearing and may by order direct the director to carry out the director’s proposal or refrain from carrying it out and to take such other action as the Tribunal considers the director ought to take in accordance with the Act and this Code, and for such purposes the Tribunal may substitute its opinion for that of the director.

(7)  The director, the applicant or registered person who requested the hearing, and such other persons as the Tribunal may specify, are parties to proceedings before the Tribunal.

(8)  Sentences (3) to (7) do not apply and the director may cancel the registration of a registered person upon receipt of a request in writing for cancellation from the registered person in a form established by the director.

(9)  If, within the time period set out in Sentence 2.18.3.3.(2), a registered person has applied for renewal of a registration and paid the fee required under Article 2.18.3.5., the registration shall be deemed to continue until the earlier of

(a)	the day the registration is renewed, and

(b)	if the registered person is served with notice that the director proposes to refuse to renew the registration, the day the time for giving notice requesting a hearing expires or, if a hearing is held, until the day the Tribunal makes its order.

2.18.4. Public Register

2.18.4.1.  Public Register

(1)  The director shall establish and maintain a register available to the public listing every person who has the qualifications required by Subsection 15.12 (1) of the Act.

(2)  The register referred to in Sentence (1) shall contain the following information with respect to every registered person:

(a)	the name of the registered person,

(b)	any identifying number assigned by the director to the registered person,

(c)	the business address of the registered person,

(d)	the names of the person or persons who will supervise the construction on site, installation, repair, servicing, cleaning or emptying sewage systems carried out by the registered person, and

(e)	any identifying number assigned by the director to the persons referred to in Clause (d).

Section 2.19. Qualifications for Registered Code Agencies

2.19.1. Scope

2.19.1.1.  Scope

(1)  This Section prescribes, for the purposes Subsection 15.11 (4) of the Act, the qualifications that a person must meet in order to be eligible to be appointed after June 30, 2005 as a registered code agency under the Act.

2.19.2. Definition

2.19.2.1.  Definition

(1)  In this Section,

registered means registered under Article 2.19.3.2.

2.19.3. Qualifications

2.19.3.1.  General

(1)  The following are prescribed as qualifications for persons to be appointed after June 30, 2005 under the Act as a registered code agency:

(a)	The person must be registered with the director.

(2)  A registration shall be in a form established by the director.

2.19.3.2.  Registration and Renewal of a Registration

(1)  Subject to Article 2.19.3.9., the director may register an applicant, or renew a registered person’s registration, in each class of registration applied for if

(a)	the applicant or registered person or, if the applicant or registered person is a corporation or partnership, a director, officer, partner or employee of the applicant or registered person, has successfully completed the examination program administered or authorized by the Ministry of Municipal Affairs and Housing relating to the person’s knowledge of the Act and this Code and the powers and duties of a registered code agency,

(b)	the applicant or registered person or, if the applicant or registered person is a corporation or partnership, one or more directors, officers, partners or employees of the applicant or registered person, have successfully completed the examination program administered or authorized by the Ministry of Municipal Affairs and Housing relating to the person’s knowledge of the Act and this Code in the category of qualification set out in Column 2 of Table 2.20.2.2. that corresponds to each class of registration set out in Column 1 of Table 2.20.2.2. for which application is made,

(c)	all persons who will carry out plans review and inspection activities on behalf of the registered code agency have the qualifications set out in Clause (b) in respect of each class of registration for which application is made,

(d)	the applicant or registered person has in place a quality management plan referred to in Sentence 2.19.3.3.(3) for carrying out the activities of the applicant or registered person under the registration that is acceptable to the director,

(e)	the applicant or registered person is covered by the insurance required under Subsection 2.21.2. during the term of the registration applied for,

(f)	the application is complete, and

(g)	all fees required under Article 2.19.3.5. are paid.

2.19.3.3.  Application for Registration or Renewal of a Registration

(1)  An application for registration or renewal of a registration shall be made to the director in a form established by the director.

(2)  An application for renewal of a registration shall be made at least 60 days before the expiry of the registration being renewed.

(3)  An application for registration or renewal of a registration shall include a quality management plan for carrying out the activities of the applicant or registered person under the registration, including, without limitation:

(a)	procedures relating to the commencement of activities as a registered code agency, including procedures to verify that the applicant or registered person is qualified to undertake the activities and to verify that there exists no conflict of interest within the meaning of Sentence 2.22.3.1.(4),

(b)	identification of the responsibilities of persons who will carry out plans review and inspection activities of the applicant or registered person and procedures for the supervision of those persons,

(c)	procedures for assessing plans and specifications for conformity with this Code, including procedures for the acceptance under Section 9 of the Act of equivalent materials, systems and building designs,

(d)	procedures for inspecting the construction of buildings,

(e)	procedures for receipt of notices that construction is ready for inspection and of written reports from architects and professional engineers arising out of the general review of the construction of buildings,

(f)	procedures for the issuance of certificates and orders under the Act, including the responsibility of the persons with the qualifications set out in Sentences 2.22.5.3.(1) and (2),

(g)	procedures for referral of matters to a chief building official under Subsection 14 (5) of the Act,

(h)	procedures for participation of the applicant or registered person in proceedings before the Building Code Commission under Section 24 of the Act and before the Superior Court of Justice under Section 25 of the Act,

(i)	procedures for documenting the activities of the applicant or registered person under the registration, including data control, records retention and the maintenance of security and confidentiality of records, and transferring records to the principal authority,

(j)	procedures for training and supervision of personnel, and

(k)	procedures for the review and up-dating of the quality management plan.

(4)  An application for registration or renewal of a registration shall include an undertaking by the applicant or registered person to comply with the conditions set out in Article 2.19.3.7.

(5)  If a partnership or a corporation is the applicant for registration or renewal of a registration, an application for registration or renewal of a registration shall set out the names and residence addresses of all its partners, directors or officers, as the case may be.

(6)  An application for registration or renewal of a registration shall contain the names of all partners, directors, officers or employees of the applicant or registered person, as the case may be, and all other persons who have been engaged by the applicant or registered person, who:

(a)	have the qualifications set out in Clauses 2.19.3.2.(1)(a) and (b), and

(b)	have the qualifications set out in Clauses 2.19.3.2.(1)(b) and (c) and will exercise powers and perform functions under the Act on behalf of the applicant or registered person.

(7)  An application for registration or renewal of a registration shall contain evidence, provided by the applicant or registered person, that the persons referred to in Sentence (6) meet the qualifications set out in Clauses 2.19.3.2.(1)(a) to (c).

(8)  An application for registration or renewal of a registration shall contain evidence, provided by the applicant or registered person, that the applicant or registered person is covered by the insurance required under Subsection 2.21.2. during the term of the registration applied for.

2.19.3.4.  Term

(1)  A registration expires one year after the date of its issuance.

2.19.3.5.  Fees

(1)  The fee for registration is $300.

(2)  The fee for the addition of a new class of registration is $50.

(3)  The fee for renewal of a registration is $220.

(4)  The amount of a fee referred to in Sentence (1), (2) or (3) is reduced by 15 per cent and rounded to the nearest whole dollar if the application is made and the fee is paid in accordance with a means of electronic filing and payment specified by the director.

(5)  The Ministry of Municipal Affairs and Housing may charge a fee to a person who takes an examination for the purposes of this Section.

2.19.3.6.  Not Transferable

(1)  A registration is not transferable.

2.19.3.7.  Conditions

(1)  The following are the conditions of a registration:

(a)	the registered person shall carry out activities under the registration in accordance with the Act, this Code and the quality management plan referred to in Clause 2.19.3.2.(1)(d),

(b)	if the registered person is a corporation or partnership, during the term of the registration there must be

(i)	an officer, director, partner or employee of the registered person who has the qualifications set out in Clause 2.19.3.2.(1)(a), and

(ii)	one or more officers, directors, partners or employees of the registered person who have the qualifications set out in Clause 2.19.3.2.(1)(b) in respect of each class of registration that is held by the registered person,

(c)	not more than 180 days after the day a notice is given under Sentence 2.19.3.8.(1) by the director to the registered person, the registered person shall:

(i)	ensure that the persons referred to in Clause (1)(b) have successfully completed the new examinations referred to in the notice, and

(ii)	provide to the director the names of the persons and information about the examinations that the persons have successfully completed, in such detail as may be required by the director,

(d)	the registered person shall during the term of the registration, be covered by the insurance required by Subsection 2.21.2.,

(e)	the registered person shall, within 15 days after the event, notify the director in writing

(i)	of any change in address of the registered person for correspondence relating to the registration, and

(ii)	of any change in the information set out in Sentences 2.19.3.3.(5) and (6),

(f)	the registered person shall give prompt written notice to the director of any material change in any of the information, other than the information referred to in Clause (e) that is contained in or accompanies an application for registration or renewal of a registration,

(g)	the registered person shall, from time to time, at the registered person’s expense, give to the director such documents or information relating to the registration of the registered person or to activities carried out under the registration as the director may reasonably require,

(h)	the registered person shall allow the representatives of the director access to the registered person’s books and records during normal business hours for the purpose of confirming matters related to the registration.

2.19.3.8.  Updating of Qualifications

(1)  Where an examination in an examination program referred to in Clause 2.19.3.2.(1)(a), (b) or (c) is replaced with a new examination, the director shall give notice of the new examination to every registered person who is registered in a class of registration set out in Column 1 of Table 2.20.2.2. to which the examination relates.

(2)  The director may give the notice referred to in Sentence (1) by sending it by regular letter mail to the last address of the registered person that has been provided to the director.

2.19.3.9.  Suspension, Revocation, Refusal to Register or Renew a Registration

(1)  The director may, in the circumstances set out in Sentence (2),

(a)	refuse to register an applicant,

(b)	refuse to renew a registration, or

(c)	suspend or revoke a registration.

(2)  The circumstances referred to in Sentence (1) are:

(a)	the registered person is in contravention of the Act or this Code,

(b)	the registered person is in breach of a condition of the registration other than the condition set out in Clause 2.19.3.7.(1)(d),

(c)	the registration was issued on the basis of mistaken, false or incorrect information,

(d)	the director is of the opinion that the past conduct of the applicant or registered person or, if the applicant or registered person is a partnership or a corporation, the partners, officers or directors of the registered person, as the case may be, affords reasonable grounds for belief that the business that would be or is authorized by the registration will not be carried on in accordance with law,

(e)	the director is of the opinion that there are reasonable grounds for belief that the activities of the applicant or registered person are or will be carried on in a manner that poses a threat to public safety,

(f)	the application is incomplete, or

(g)	any fees required under Article 2.19.3.5. remain unpaid.

(3)  If the director proposes to refuse to register or renew a registration or proposes to suspend or revoke a registration under Sentence (1), the director shall serve a notice of the proposal, together with the reasons for it, on the applicant or registered person.

(4)  A notice under Sentence (3) shall state that the applicant or registered person is entitled to a hearing before the Tribunal if the applicant or registered person, within 15 days after service of the notice referred to in Sentence (3), serves the director and the Tribunal with notice in writing requesting a hearing.

(5)  If an applicant or registered person does not request a hearing by the Tribunal in accordance with Sentence (4), the director may carry out the proposal stated in the notice under Sentence (3).

(6)  If an applicant or registered person requests a hearing before the Tribunal in accordance with Sentence (4), the Tribunal shall appoint a time for and hold a hearing and may by order direct the director to carry out the director’s proposal or refrain from carrying it out and to take such other action as the Tribunal considers the director ought to take in accordance with the Act and this Code, and for those purposes the Tribunal may substitute its opinion for that of the director.

(7)  The director, the applicant or registered person who requested the hearing, and such other persons as the Tribunal may specify, are parties to proceedings before the Tribunal.

(8)  A proposal to suspend or revoke a registration by reason of Clause (2)(e) takes effect immediately and the commencement of a proceeding before the Tribunal does not stay the operation of the proposal to suspend or revoke the registration.

(9)  The Tribunal may, on the application of the registered person, stay the operation of the proposal of the director to suspend or revoke the registration, and may grant the stay subject to conditions.

(10)  Sentences (3) to (9) do not apply and the director may cancel the registration of a registered person upon receipt of a request in writing for cancellation from the registered person in a form established by the director.

(11)  Subject to Sentence (8), if within the time period set out in Sentence 2.19.3.3.(2) a registered person has applied for renewal of a registration, paid the fee required under Article 2.19.3.5. and provided evidence satisfactory to the director that the registered person is covered by insurance required under Subsection 2.21.2. for the term of the renewal of the registration, the registration shall be deemed to continue until the earliest of

(a)	the day the registration is renewed,

(b)	if the registered person is served with notice that the director proposes to refuse to renew the registration, the day the time for giving notice requesting a hearing expires or, if a hearing is held, the day the Tribunal makes its order, and

(c)	the day when the registered person ceases to be covered by the insurance required under Subsection 2.21.2.

2.19.3.10.  Mandatory Suspension or Revocation of Registration or Refusal to Register or Renew a Registration

(1)  The director shall, in the circumstances set out in Sentence (2),

(a)	refuse to register an applicant,

(b)	refuse to renew a registration, or

(c)	suspend or revoke a registration.

(2)  The circumstances referred to in Sentence (1) are:

(a)	the registered person is not covered by the insurance required under Subsection 2.21.2., or

(b)	an order under Subsection 69 (2) of the Provincial Offences Act is in effect directing that the registration of the person be suspended and that no registration be issued to that person until a fine is paid.

(3)  If the director refuses to register an applicant, refuses to renew a registration or suspends or revokes a registration under Sentence (1), the director shall serve a notice of the refusal, suspension or revocation, together with the reasons for it, on the registered person.

(4)  A suspension or revocation of a registration under Sentence (1) takes effect immediately and the commencement of a proceeding before the Tribunal does not stay the operation of the suspension or revocation of the registration.

(5)  The Tribunal may, on the application of the registered person, stay the operation of a decision of the director to suspend or revoke the registration, and may make the stay subject to conditions.

(6)  A notice under Sentence (3) shall state that the registered person is entitled to a hearing before the Tribunal if the registered person, within 15 days after service of the notice referred to in Sentence (3), serves the director and the Tribunal with notice in writing requesting a hearing.

(7)  If a registered person requests a hearing before the Tribunal in accordance with Sentence (6), the Tribunal shall appoint a time for and hold a hearing and may by order confirm, alter or revoke the decision of the director to refuse to register or to suspend or revoke the registration and may take such action as the Tribunal considers the director ought to take in accordance with the Act and this Code, and for such purposes the Tribunal may substitute its opinion for that of the director.

(8)  The director and the registered person who requested the hearing, and such other persons as the Tribunal may specify, are parties to proceedings before the Tribunal.

2.19.4. Public Register

2.19.4.1.  Public Register

(1)  The director shall establish and maintain a register available to the public listing every person who has the qualifications required by Subsection 15.11 (4) of the Act.

(2)  The register referred to in Sentence (1) shall contain the following information in respect of every registered person:

(a)	the name of the registered person,

(b)	any identifying number assigned by the director to the registered person,

(c)	the business address of the registered person,

(d)	the classes of registration of the registered person, and

(e)	the names of any persons who will exercise powers and perform functions under the Act on behalf of the registered person in each class of registration and any identifying number assigned by the director to that person.

2.19.5. Classes of Registration and Categories of Qualifications

2.19.5.1.  Classes and Categories

(1)  Table 2.20.2.2. contains the classes of registration and categories of qualifications for the purposes of this Section.

Section 2.20. Classes of Registration and Categories of Qualifications

2.20.1. Scope

2.20.1.1.  Scope

(1)  This Section sets out classes of registration and categories of qualifications for the purposes of Sections 2.16., 2.17., 2.19. and 2.22.

2.20.2. Classes of Registration and Categories of Qualifications

2.20.2.1.  Inspectors and Persons Who Carry out Design Activities

(1)  Table 2.20.2.1. sets out the classes of registration and categories of qualifications for persons who carry out design activities and the categories of qualifications for inspectors.

Table 2.20.2.1.

Classes of Registration and Categories of Qualifications For Inspectors and Persons Who Carry Out Design Activities Forming Part of Sentence 2.20.2.1.(1)

| Row Number | Classes of Registration for Persons engaged in the business of providing Design Activities to the public | Categories of Qualifications for Inspectors and Persons described in Clauses 2.17.4.2.(1)(a) and (b) and 2.17.5.1.(1)(a) | Type of Building |
| --- | --- | --- | --- |
| 1 | House | House | (a) A detached house, semi-detached house, townhouse or row house containing not more than two dwelling units in each house and the building systems, works, fixtures and service systems appurtenant to these buildings, |
|  |  |  | including: |
|  |  |  | (b) an ancillary building that serves the building, and |
|  |  |  | excluding: |
|  |  |  | (c) buildings and parts of buildings described in Column 4 of any of Rows 5, 6, 7, 8, 10 and 11 of this Table. |
| 2 | Small Buildings | Small Buildings | (a) Buildings described in Clauses 2.1.1.3.(1)(a), (b) and (c) and the building systems, works, fixtures and service systems appurtenant to these buildings, |
|  |  |  | including: |
|  |  |  | (b) buildings and parts of buildings |
|  |  |  | (i) described in Column 4 of Row 1 of this Table, or |
|  |  |  | (ii) to which any of Sections 3.10., 3.11., 3.11A., 3.13. and 3.14. apply and that are appurtenant to or serve buildings described in Clause (a), and |
|  |  |  | excluding: |
|  |  |  | (c) buildings and parts of buildings described in Column 4 of any of Rows 4 to 11 of this Table. |
| 3 | Large Buildings | Large Buildings | (a) Buildings described in Clause 2.1.1.2.(1)(a) or (b) and the building systems, works, fixtures and service systems appurtenant to these buildings, |
|  |  |  | excluding: |
|  |  |  | (b) buildings and parts of buildings described in Column 4 of any of Rows 4 to 11 of this Table. |
| 4 | Complex Buildings | Complex Buildings | Building systems, works, fixtures and service systems to which Subsection 3.2.6. or any provision in Articles 3.2.8.3. to 3.2.8.11. apply. |
| 5 | Plumbing — House | Plumbing — House | All plumbing systems to which Part 7 applies that are appurtenant to a building that is a detached house, semi-detached house, townhouse or row house containing not more than two dwelling units in each house. |
| 6 | Plumbing — All Buildings | Plumbing — All Buildings | (a) All plumbing systems to which Part 7 applies, |
|  |  |  | including: |
|  |  |  | (b) buildings and parts of buildings described in Column 4 of Row 5 of this Table. |
| 7 | HVAC — House | HVAC — House | All building systems, works, fixtures and service systems to which Section 9.32. or 9.33. applies that are appurtenant to a building that is a detached house, semi-detached house, townhouse or row house containing not more than two dwelling units in each house. |
| 8 | Building Services | Building Services | (a) Building systems, works, fixtures and service systems that are appurtenant to buildings described in Clause 2.1.1.2.(1)(a) or (b) or Clauses 2.1.1.3.(1)(a), (b) and (c) and that relate to fire suppression, fire detection, smoke control, exhaust, vertical movement of smoke, energy efficiency, lighting and emergency power, and |
|  |  |  | (b) building systems, works, fixtures and service systems appurtenant to buildings to which Part 6 applies or to which Section 9.32. or 9.33. applies, |
|  |  |  | including: |
|  |  |  | (c) buildings and parts of buildings described in Column 4 of Row 7 or 11 of this Table. |
| 9 | Building Structural | Building Structural | (a) Internal and external load-bearing structural elements essential to the stability or strength of a building described in Clause 2.1.1.2.(1)(a) or (b) or Clauses 2.1.1.3.(1)(a), (b) and (c) and that resist dead loads or live loads including, but not limited to, foundations, floors, walls, roofs, columns and beams, and |
|  |  |  | (b) structures designated in Sentence 2.1.2.1.(1). |
| 10 | On-site Sewage Systems | On-site Sewage Systems | Sewage systems to which Part 8 applies. |
| 11 | Detection, Lighting and Power | Detection, Lighting and Power | Early warning and electrical systems including systems appurtenant to buildings described in Clause 2.1.1.2.(1)(a) or (b) or Clauses 2.1.1.3.(1)(a), (b) and (c) and that relate to fire alarm and detection systems, voice communication systems, lighting systems, emergency lighting systems or emergency power systems for building services in all buildings. |
| 12 | Fire Protection | Fire Protection | Fire suppression, fire detection, fire fighting and fire safety systems appurtenant to buildings described in Clause 2.1.1.2.(1)(a) or (b) or Clauses 2.1.1.3.(1)(a), (b) and (c). |
| Column 1 | Column 2 | Column 3 | Column 4 |

Notes to Table 2.20.2.1.

1.  An inspector qualified in one category of qualification may carry out plans review and inspection in another category where to do so does not constitute a substantial part of the plans review or inspection on any project.

2.  A person registered in one class of registration or a person qualified in one category of qualification may carry out design activities in another class or category where to do so does not constitute a substantial part of the design activities on any project.

2.20.2.2.  Registered Code Agencies

(1)  Table 2.20.2.2. sets out the classes of registration for registered code agencies and the categories of qualifications for persons described in Clauses 2.19.3.2.(1)(a) to (c).

Table 2.20.2.2.

Classes of Registration and Categories of Qualifications Registered Code Agencies Forming Part of Sentence 2.20.2.2.(1)

| Classes of Registration for Registered Code Agencies | Category of Qualification for Persons described in Clauses 2.19.3.2.(1)(a) to (c) | Type of Building Reference to Table 2.20.2.1. |
| --- | --- | --- |
| House | House | Column 4 of Row 1 |
|  | Plumbing — House | Column 4 of Row 5 |
|  | HVAC — House | Column 4 of Row 7 |
|  | On-Site Sewage Systems | Column 4 of Row 10 |
| Small Buildings | Small Buildings | Column 4 of Row 2 |
|  | Plumbing — All Buildings | Column 4 of Row 6 |
|  | Building Services | Column 4 of Row 8 |
|  | Building Structural | Column 4 of Row 9 |
|  | On-Site Sewage Systems | Column 4 of Row 10 |
| Large Buildings | Large Buildings | Column 4 of Row 3 |
|  | Plumbing — All Buildings | Column 4 of Row 6 |
|  | Building Services | Column 4 of Row 8 |
|  | Building Structural | Column 4 of Row 9 |
|  | On-site Sewage Systems | Column 4 of Row 10 |
| Complex Buildings | Complex Buildings | Column 4 of Row 4 |
|  | Plumbing — All Buildings | Column 4 of Row 6 |
|  | Building Services | Column 4 of Row 8 |
|  | Building Structural | Column 4 of Row 9 |
|  | On-site Sewage Systems | Column 4 of Row 10 |
| On-site Sewage Systems | On-site Sewage Systems | Column 4 of Row 10 |
| Column 1 | Column 2 | Column 3 |

Section 2.21. Insurance

2.21.1. Scope

2.21.1.1.  Scope

(1)  This Section prescribes, for the purposes of Subsection 15.13 (1) of the Act, the insurance coverage that registered code agencies and persons referred to in Subsection 15.11 (5) of the Act must have.

2.21.2. Insurance for Registered Code Agencies and Persons Referred to in Subsection 15.11 (5) of the Act

2.21.2.1.  Definition

(1)  In this Subsection, registered person means a person who is registered under Article 2.17.4.2. or 2.19.3.2.

2.21.2.2.  Scope

(1)  Every person registered under Article 2.17.4.2. or 2.19.3.2. shall have insurance coverage under an insurance policy that satisfies the requirements set out in Article 2.21.2.3.

2.21.2.3.  Insurance Coverage

(1)  The insurance policy

(a)	shall indemnify the registered person against liability imposed by law arising out of the performance of or the failure to perform services as a registered person during any time while the person is registered under Article 2.17.4.1. or 2.19.3.2. for claims that are first made and reported to the insurer during the period of insurance or during any extended reporting period required by Clause (1)(c),

(b)	shall set out the name of the registered person,

(c)	in the case of a registered code agency registered under Article 2.19.3.2.,

(i)	shall require an extended reporting period of two years for the purposes of giving notice of any claim or occurrence that the registered code agency could reasonably foresee might give rise to a claim, with respect to an event that occurs prior to the person ceasing to be insured,

(ii)	shall provide that the extended reporting period described in Subclause (i) shall commence on the day the registered code agency ceases to be insured, and

(iii)	shall require the registered code agency to make full payment of all premiums for the extended reporting period referred to in Subclause (i) as part of the premiums for the issuance of the insurance policy,

(d)	shall provide for insurance coverage to commence,

(i)	on the date the registered person becomes registered, or

(ii)	in the case of a registered person previously insured in accordance with this Article, on the expiry of the previous policy,

(e)	shall require the insurer to provide prompt written notice to the director if the policy is declared void for material misrepresentation,

(f)	shall specify a limit of indemnity for any one claim and in the aggregate during any one period of insurance that is not less than

(i)	in the case of persons registered under Article 2.17.4.2.,

(A)		$1,000,000 per claim and $2,000,000 in the aggregate, if the person billed $100,000 or more in fees in the 12 months immediately before the issuance of the policy,

(B)	$500,000 per claim and $1,000,000 in the aggregate, if the person billed more than $50,000 and less than $100,000 in fees in the 12 months immediately before the issuance of the policy,

(C)	$250,000 per claim and $500,000 in the aggregate, if the person billed $50,000 or less in fees in the 12 months immediately before the issuance of the policy, or

(D)	the limits of indemnity for any one claim and in the aggregate that are set out in Sub-subclause (A), (B) or (C), as determined by reference to the person’s estimated fees billings for the 12-month period immediately after the issuance of the policy, if the person has been registered less than one year before the issuance of the policy, and

(ii)	in the case of a registered code agency registered under Article 2.19.3.2., $1,000,000 per claim and $2,000,000 in the aggregate, except that those limits shall apply exclusively to the exercise of the powers and performance of the duties of a registered code agency under the Act and shall be in addition to any insurance applicable to any other activities carried on by the registered code agency,

(g)	shall provide that any costs and expenses necessarily incurred by the insurer in the investigation, defence or settlement of claims under the policy shall not be part of the limit of indemnity set out in Clause (f) unless the limit of indemnity from any one claim exceeds $2,000,000,

(h)	shall not provide that the insured shall be responsible for the first portion of any sum that the insured becomes legally liable to pay in respect of a claim made against him, her or it in respect of any one claim or occurrence in an amount exceeding the lesser of:

(i)	$70,000, and

(ii)	5% of

(A)	the amount of fees billed by the insured in the 12 months immediately before the issuance of the policy, or

(B)	the amount of the insured’s estimated fees billings for the 12- month period immediately after the issuance of the policy, if the insured has been registered under Article 2.17.4.2. less than one year before the issuance of the policy,

(i)	shall provide that it cannot be cancelled by the insured unless,

(i)	the insured immediately replaces the policy with another policy that satisfies the requirements of this Article,

(ii)	the insurer has given notice in writing of the proposed cancellation to the director, and

(iii)	the notice described in Subclause (ii) was received by the director at least 30 days before the day the policy is cancelled,

(j)	shall provide that it cannot be cancelled by the insurer unless,

(i)	it is cancelled for non-payment of a premium,

(ii)	the insurer has given notice in writing of the proposed cancellation to the director, and

(iii)	the notice described in Subclause (ii) was sent to the director at least 30 days before the day the policy is cancelled,

(k)	shall provide for the continuation of coverage if the insured is adjudged a bankrupt, insolvent, incompetent or dies during the period of insurance, and

(l)	may provide that coverage be subject to such exclusions and conditions and otherwise on such terms as are consistent with normal insurance industry practice from time to time.

Section 2.22. Registered Code Agencies

2.22.1. Appointment of Registered Code Agency under Section 4.1 of the Act

2.22.1.1.  Agreements

(1)  An agreement between a principal authority and a registered code agency under Subsection 4.1 (1) of the Act shall be made in writing and shall:

(a)	specify the functions that the registered code agency is authorized to perform,

(b)	specify the construction of the building or class of buildings in respect of which the functions will be performed,

(c)	set out the procedure by which the principal authority will appoint the registered code agency to perform specified functions in respect of the construction of a building or class of buildings,

(d)	require that the registered code agency carry out its functions under the agreement in accordance with the Act and this Code and the quality management plan described in Clause 2.19.3.2.(1)(d),

(e)	provide for the provision by the principal authority to the registered code agency of such plans, specifications and other information, including applications for permits, that the registered code agency may require in order to act under the appointment.

(2)  An agreement under Subsection (1)

(a)	may contain provisions in addition to the provisions required under Subsection (1) if the additional provisions are not inconsistent with the provisions required under that Subsection, and

(b)	shall not contain any provision that relates to the construction of buildings for a class of registration for which the registered code agency is not registered under Section 2.19.

2.22.1.2.  Appointments

(1)  An appointment under Subsection 4.1 (2) of the Act by a principal authority of a registered code agency to perform specified functions in respect of the construction of a building or class of buildings shall be made in writing and shall:

(a)	specify the construction of the building or class of buildings in respect of which the appointment relates,

(b)	specify the functions described in Section 15.15 of the Act that the registered code agency is appointed to perform, and

(c)	require that the registered code agency carry out its functions under the appointment in accordance with the Act and this Code and the quality management plan described in Clause 2.19.3.2.(1)(d).

(2)  An appointment described in Subsection (1) may contain provisions in addition to the provisions required under Subsection (1) if the additional provisions are not inconsistent with the provisions required under that Subsection.

2.22.2.  Revoked:  O. Reg. 245/04, s. 3.

2.22.3. When a Registered Code Agency may not be Appointed or Continue to Act under an Appointment

2.22.3.1.  General

(1)  A registered code agency may not be appointed to perform functions under Section 15.15 of the Act in respect of a building or continue to act under an appointment in respect of a building if the registered code agency:

(a)	is not registered under Section 2.19 in respect of the class of registration to which the construction of the building relates, or

(b)	is in breach of a condition of its registration under Article 2.19.3.7.

(2)  Where under Section 2.3. the design and general review of construction of a building must be undertaken by an architect or professional engineer or both, a registered code agency may not be appointed to perform functions under Section 15.15 of the Act or continue to act under an appointment in respect of the construction of the building unless the registered code agency or an officer, director, partner or employee of the registered code agency is an architect or professional engineer or both, as the case may be.

(3)  A registered code agency shall not be appointed under the Act or continue to act under an appointment if the registered code agency would be in a conflict of interest.

(4)  For the purposes of Sentence (3), a registered code agency would be in a conflict of interest if the registered code agency or an officer, director, partner or employee of the registered code agency or any person engaged by the registered code agency to perform functions for it:

(a)	has participated or participates, in any capacity, in design activities or construction relating to any part of the building to which an appointment relates,

(b)	is or has been employed within the previous 180 days by a person who carried out design activities or construction relating to any part of the building,

(c)	has a professional or financial interest in:

(i)	the construction of the building to which the appointment relates,

(ii)	the building to which the appointment relates, or

(iii)	the person responsible for the design of the building to which the appointment relates,

(d)	is an elected official, officer or employee of a principal authority.

(5)  For the purposes of Clause (4)(c), involvement with a building as a registered code agency and entitlement to any fee paid for acting as a registered code agency in respect of a building shall not be considered to be a professional or financial interest in the construction of the building, the building or the person responsible for the design of the building.

2.22.4. Additional Functions that Registered Code Agencies may be Appointed To Perform

2.22.4.1.  General

(1)  In addition to the functions described in Paragraphs 1 to 5 of Section 15.15 of the Act, a registered code agency may be appointed to perform the functions set out in Sentence 2.22.5.3.(5).

2.22.5. Manner in which Registered Code Agency shall Perform Functions

2.22.5.1.  General

(1)  The registered code agency shall perform the functions specified in an appointment in accordance with the Act and this Code and the quality management plan referred to in Clause 2.19.3.2.(1)(d).

(2)  The registered code agency shall perform the functions specified in an appointment in accordance with the code of conduct set out in the Supplementary Guidelines to the 1997 OBC.

2.22.5.2.  Plans Review and Inspection Activities

(1)  The registered code agency shall ensure that plans review and inspection activities of the registered code agency are carried out by a person who has the qualifications set out in Clause 2.19.3.2.(1)(b) or (c) in respect of the type of building set out in Column 3 of Table 2.20.2.2. for which the person is carrying out the activities.

(2)  Not more than 180 days after the day a notice is given under Sentence 2.19.3.8.(1) by the director to the registered code agency, the registered code agency shall:

(a)	ensure that plans review and inspection activities of the registered code agency in the category of qualification to which the notice relates are carried out by persons who have successfully completed all new examinations referred to in the notice, and

(b)	provide the following information to the director:

(i)	the name and residence address of the person, and

(ii)	information required by the director about the examinations that the person or persons have successfully completed.

(3)  A registered code agency shall prepare written records of every inspection of the construction of a building that is undertaken by the registered code agency in the course of performing functions under an appointment.

(4)  The record required under Sentence (3) shall include:

(a)	the date of receipt of the notice of readiness for inspection, if any,

(b)	the date of the inspection,

(c)	the reason for the inspection,

(d)	whether non-compliance with this Code was observed in the course of the inspection and the details of the non-compliance.

(5)  If a registered code agency has issued an order under Subsection 12 (2), 13 (1) or 13 (6) of the Act, the registered code agency shall prepare a written record consisting of:

(a)	a copy of the order,

(b)	the persons on whom the order was served and the date and manner of service,

(c)	when and how the order was complied with, and

(d)	if the order has not been complied with, the efforts made by the registered code agency to achieve compliance by the persons responsible for compliance.

2.22.5.3.  Issuance of Certificates by Registered Code Agencies

(1)  Subject to Sentence (2), every certificate issued under the Act by a registered code agency shall, in accordance with the quality management plan referred to in Clause 2.19.3.2(1)(d), be signed by the registered code agency or, if the registered code agency is a corporation or partnership, by a person described in Clause 2.19.3.2.(1)(a).

(2)  If the certificate is issued in respect of the construction of a building that would under Section 2.3.1. be required to be designed by and under the general review of an architect or professional engineer or both, the certificate shall also be signed on behalf of the registered code agency by an architect or a professional engineer or both, as the case may be, who is an officer, director, partner or employee of the registered code agency.

(3)  A registered code agency may issue a plans review certificate if the registered code agency:

(a)	has been appointed to perform the functions described in Clause 4.1 (4) (a) or (c) of the Act in respect of the proposed construction of the building to which the plans review certificate applies,

(b)	has, in conformity with the Act, this Code and the quality management plan described in Clause 2.19.3.2.(1)(d), carried out the applicable functions for which the registered code agency was appointed, and

(c)	is satisfied on reasonable grounds that, on date on which the plans review certificate is issued, the proposed construction of the building to which the plans review certificate relates is in compliance with this Code.

(4)  A registered code agency may issue a change certificate if the registered code agency:

(a)	has been appointed to perform the functions described in Clauses 4.1 (4) (a) to (c) of the Act in respect of the construction or proposed construction of the building to which the change certificate applies,

(b)	has, in conformity with the Act, this Code and the quality management plan described in Clause 2.19.3.2.(1)(d), carried out the applicable functions for which the registered code agency was appointed, and

(c)	is satisfied on reasonable grounds that, on the date on which the change certificate is issued, the proposed construction of the building to which the change certificate relates is in compliance with this Code.

(5)  A registered code agency may issue a certificate for the occupancy of a building not fully completed if the registered code agency:

(a)	has been appointed to perform the functions described in Clause 4.1 (4) (b) or (c) of the Act in respect of the construction of the building to which the certificate for the occupancy of a building not fully completed applies,

(b)	has, in conformity with the Act, this Code and the quality management plan described in Clause 2.19.3.2.(1)(d), carried out the applicable functions for which the registered code agency was appointed, and

(c)	is satisfied on reasonable grounds that, on the date on which the certificate for the occupancy of a building not fully completed is issued, the construction of the building to which the certificate for the occupancy of a building not fully completed relates is in compliance with Clauses 2.4.3.1.(2)(a) to (q) of this Code.

(6)  A registered code agency may issue a final certificate if the registered code agency:

(a)	has been appointed to perform the functions described in Clause 4.1 (4) (b) or (c) of the Act in respect of the construction of the building to which the final certificate applies,

(b)	has, in conformity with the Act, this Code and the quality management plan described in Clause 2.19.3.2.(1)(d), carried out the applicable functions for which the registered code agency was appointed, and

(c)	is satisfied on reasonable grounds that on the date on which the final certificate is issued, the construction of the building to which the final certificate relates is in compliance with this Code.

(7)  Every certificate issued under the Act by a registered code agency shall be in a form approved by the Minister.

2.22.5.4.  Issuance of Orders by Registered Code Agencies

(1)  Orders under Subsections 13 (6) and 14 (1) of the Act shall, in accordance with the quality management plan described in Clause 2.19.3.2.(1)(d), be signed by the registered code agency or a person described in Clause 2.19.3.2.(1)(a).

(2)  Orders under Subsections 12 (2) and 13 (1) and Clause 18 (1) (f) of the Act shall, in accordance with the quality management plan described in Clause 2.19.3.2.(1)(d), be signed by the registered code agency or by a person described in Clause 2.19.3.2.(1)(b) or (c).

2.22.5.5.  Authorized Persons

(1)  Persons who possess the qualifications described in Clauses 2.19.3.2.(1)(a), (b) and (c) are prescribed for the purposes of Subsection 15.17 (1) of the Act.

(2)  The certificate of authorization referred to in Subsection 15.17 (2) of the Act shall, in accordance with the quality management plan described in Clause 2.19.3.2.(1)(d), be signed by a representative of the registered code agency who is described in Clause 2.19.3.2.(1)(a) and shall contain the following information:

(a)	the name of the registered code agency and any identifying number issued by the director to the registered code agency,

(b)	the title, business address and business telephone number of a representative of the registered code agency who may be contacted to answer questions about the certificate and the authorization to which it relates,

(c)	the name of the authorized person and any identifying number issued by the director to the authorized person in respect of that person’s qualifications,

(d)	the scope of the powers that may be exercised and the functions that may be performed by the authorized person,

(e)	the date of issuance of the certificate.

(3)  Every person described in Sentence (1) shall carry his or her certificate of authorization when performing duties and shall produce the certificate for inspection upon request.

2.22.5.6.  Prohibition

(1)  A registered code agency shall not dismiss, suspend, demote, discipline, harass or otherwise disadvantage an employee, or deny an employee a benefit of employment, by reason that

(a)	the employee, acting in good faith and on the basis of reasonable belief, has disclosed to the director that the registered code agency or any other person has contravened or intends to contravene a provision of the Act or this Code,

(b)	the employee, acting in good faith and on the basis of reasonable belief, has refused or stated an intention of refusing to do anything that is a contravention of a provision of the Act or this Code,

(c)	the employee, acting in good faith and on the basis of reasonable belief, has done or stated an intention of doing anything that is required to be done in order that a provision of the Act or this Code not be contravened, or

(d)	the registered code agency believes that the employee will do anything referred to in Clause (a), (b) or (c).

(2)  Nothing in this Section impairs any right of an employee either at law or under an employment contract or collective agreement.

(3)  In this Article, “employee” includes an independent contractor and “employer” includes the person who retains an employee who is an independent contractor.

2.22.5.7.  Information and Records

(1)  The registered code agency shall maintain records of all plans review and inspection activity, of all certificates and orders and of any other activities taken in carrying out functions under an appointment in accordance with the quality management plan described in Clause 2.19.3.2.(1)(d).

(2)  Any information collected by a registered code agency in the course of the exercise of powers and the performance of duties under this Act may be used only for the purpose of performing functions under an appointment under Subsection 4.1 (2) of the Act and may be disclosed only:

(a)	to a principal authority pursuant to an agreement under Subsection 4.1 (1) of the Act,

(b)	to a principal authority to aid the enforcement in any manner of the Act,

(c)	where required or permitted under this Act, this Code, other applicable legislation or an order of a court.

(3)  A registered code agency shall ensure that any agreement under which the registered code agency engages a person to assist the registered code agency to perform functions under an appointment includes a provision that requires the person to comply with Sentences (1) and (2).

2.22.6.  Termination of Appointment of a Registered Code Agency

2.22.6.1.  Termination of an Appointment Made under Subsection 4.1 (2) of the Act

(1)  A principal authority may, in accordance with the terms of an agreement under Subsection 4.1 (1) of the Act, terminate the appointment of a registered code agency before the appointment expires under Section 15.19 of the Act.

2.22.6.2.  Revoked:  O. Reg. 245/04, s. 6.

2.22.7. Information to be Provided

2.22.7.1.  Information to be Provided by a Principal Authority to the Director

(1)  If a principal authority that has appointed a registered code agency terminates the appointment before the appointment expires under Section 15.19 of the Act, the principal authority shall, as soon as possible after the termination, give the director notice of the termination and such other information concerning the circumstances of the termination and as may be required by the director.

(2)  If a principal authority has issued an order under Subsection 15.21 (1) of the Act, the principal authority shall as soon as possible after the order is issued give the director a copy of the order and such other information concerning the circumstances of the order and as may be required by the director.

2.22.7.2.  Revoked:  O. Reg. 245/04, s. 7.

2.22.7.3.  Revoked:  O. Reg. 245/04, s. 8.

2.22.7.4.  Information to be Provided by a Registered Code Agency to the Director

(1)  A registered code agency that becomes or expects to become unable to carry out the functions for which the registered code agency was appointed shall as soon as possible give notice to the director of this situation.

2.22.7.5.  Information to be Provided by a Registered Code Agency to the Chief Building Official

(1)  A registered code agency shall notify the chief building official if the registered code agency becomes or expects to become unable to carry out the functions for which the registered code agency was appointed.

(2)  A registered code agency shall give copies of the following records to the chief building official:

(a)	all orders issued by the registered code agency under Subsections 12 (2), 13 (1) and 13 (6) of the Act,

(b)	all written records prepared by the registered code agency under Sentences 2.22.5.2.(3) and (4),

(c)	all final certificates that are issued by the registered code agency,

(d)	records described in Sentence 2.7.1.1.(2) relating to the use of an equivalent material, system or building design under Section 9 of the Act, and

(e)	any records of information, copies of documents or things, tests, samples or photographs produced, removed, required, taken or ordered to be taken under Subsection 18 (1) of the Act.

(3)  The documents referred to in Sentence (2) shall be given to the chief building official:

(a)	within the time period specified in any agreement under Article 2.22.1.1. or appointment under Article 2.22.1.2 in respect of which the documents relate, whichever time period ends earlier,

(b)	within 15 days after the expiry or termination of the appointment of the registered code agency in respect of which the documents relate, if there is no time period specified in the agreement or appointment referred to in Clause (a), or

(c)	if the chief building official has given notice to the registered code agency that he or she requires the documents before the time set out in Clause (a) or (b), within 2 days after the request for documents.

(4)  The requirements of Sentence (2) apply even if the registered code agency is no longer registered under Subsection 2.19.

(5)  If a registered code agency in the course of carrying out functions under an appointment has reason to believe that a building described in Sentence (7) is unsafe within the meaning of Subsection 15.9 (2) or (3) of the Act, the registered code agency shall as soon as possible give notice to the chief building official of:

(a)	the location of the building, and

(b)	the reason why the registered code agency has reason to believe that the building is unsafe.

(6)  A registered code agency that has given a notice to the chief building official under Sentence (5) shall give the chief building official such other information about the unsafe condition as the chief building official may require.

(7)  Sentence (5) applies to:

(a)	a building in respect of which the registered code agency has been appointed to perform functions, and

(b)	a building that has been adversely affected by construction of a building referred to in Clause (a).

(8)  For the purposes of Sentence (3), a time period referred to in Clause (3) (a), (b) or (c)

(a)	does not start until the day after the day on which the obligation to provide the documents arises, and

(b)	does not include Saturdays, holidays and all other days on which the offices of the principal authority are not open for the transaction of business with the public.

2.22.8. Referral of Stop Work Order

2.22.8.1.  Referral

(1)  A registered code agency shall refer a matter under Subsection 14 (5) of the Act to the chief building official by giving the chief building official, as soon as possible

(a)	a report that contains the following information:

(i)	a copy of the order made under Section 12 or 13 of the Act that was not complied with and of the order under Subsection 14 (2) of the Act,

(ii)	the persons on whom the orders were served and the date and manner of service, and

(iii)	a statement that the orders have not been complied with, and

(b)	such other information as the chief building official may require in respect of the matter that has been referred.

(2)  The report under Clause (1)(a) shall be signed, in accordance with the quality management plan described in Clause 2.19.3.2.(1)(d), by the registered code agency or, if the registered code agency is a corporation or partnership, by a person described in Clause 2.19.3.2.(1)(a).

Section  2.23. Fees

2.23.1.  Fees

2.23.1.1.  Annual Report

(1)  The report referred to in Subsection 7 (4) of the Act shall contain the following information in respect of fees authorized under Clause 7 (1) (c) of the Act:

(a)	total fees collected in the 12-month period ending no earlier than three months before the release of the report,

(b)	the direct and indirect costs of delivering services related to the administration and enforcement of the Act in the area of jurisdiction of the principal authority in the 12-month period referred to in Clause (a),

(c)	a break-down of the costs described in Clause (b) into at least the following categories:

(i)	direct costs of administration and enforcement of the Act, including the review of applications for permits and inspection of buildings, and

(ii)	indirect costs of administration and enforcement of the Act, including support and overhead costs, and

(d)	if a reserve fund has been established for any purpose relating to the administration or enforcement of the Act, the amount of the fund at the end of the 12-month period referred to in Clause (a).

(2)  The principal authority shall give notice of the preparation of a report under Subsection 7 (4) of the Act to every person and organization that has requested that the principal authority provide the person or organization with such notice and has provided an address for the notice.

2.23.1.2.  Change of Fees

(1)  Before passing a by-law, regulation or resolution under Clause 7 (1) (c) of the Act to introduce or change a fee imposed for applications for a permit or for the issuance of a permit, a principal authority shall

(a)	hold at least one public meeting at which any person who attends has an opportunity to make representations with respect to the matter,

(b)	ensure that a minimum of 21 days notice of the public meeting is given in accordance with Clause (c), including giving 21 days notice to every person and organization that has, within five years before the day of the public meeting, requested that the principal authority provide the person or organization with such notice and has provided an address for the notice,

(c)	ensure that the notice under Clause (b),

(i)	sets out the intention of the principal authority to pass the by-law, regulation or resolution under Section 7 of the Act and whether the by-law, regulation or resolution would impose any fee that was not in effect on the day the notice is given or would change any fee that was in force on the day the notice is given,

(ii)	is sent by regular mail to the last address provided by the person or organization that requested the notice in accordance with Clause (b), and

(iii)	sets out the information described in Clause (d) or states that the information will be made available at no cost to any member of the public upon request, and

(d)	make the following information available to the public:

(i)	an estimate of the costs of administering and enforcing the Act by the principal authority,

(ii)	the amount of the fee or of the change to the existing fee, and

(iii)	the rationale for imposing or changing the fee.

O. Reg. 403/97, Part 2; O. Reg. 22/98, ss. 2-9; O. Reg. 278/99, s. 2; O. Reg. 205/00, s. 2; O. Reg. 283/01, ss. 2, 3; O. Reg. 220/02, ss. 2, 3; O. Reg. 305/03, ss. 3-18; O. Reg. 245/04, ss. 1-9; O. Reg. 145/05, ss. 1, 2; O. Reg. 146/05, ss. 1-12; O. Reg. 236/05, ss. 1-9; O. Reg. 349/06, s. 3; O. Reg. 422/06, s. 2.

Part 3
Fire Protection, Occupant Safety and Accessibility

| Section | 3.1. | General |
| --- | --- | --- |
|  | 3.1.1. | Scope |
|  | 3.1.2. | Classification of Buildings or Parts of Buildings by Major Occupancy |
|  | 3.1.3. | Multiple Occupancy Requirements |
|  | 3.1.4. | Combustible Construction |
|  | 3.1.5. | Noncombustible Construction |
|  | 3.1.6. | Reserved |
|  | 3.1.7. | Fire-Resistance Ratings |
|  | 3.1.8. | Fire Separations and Closures |
|  | 3.1.9. | Building Services in Fire Separations and Fire Rated Assemblies |
|  | 3.1.10. | Firewalls |
|  | 3.1.11. | Fire Stops in Concealed Spaces |
|  | 3.1.12. | Flame-Spread Rating and Smoke Developed Classification |
|  | 3.1.13. | Interior Finish |
|  | 3.1.14. | Roof Assemblies |
|  | 3.1.15. | Roof Covering |
|  | 3.1.16. | Occupant Load |
|  | 3.1.17. | Drainage and Grades |
|  | 3.1.18. | Above Ground Electrical Conductors |
| Section | 3.2. | Building Fire Safety |
|  | 3.2.1. | General |
|  | 3.2.2. | Building Size and Construction Relative to Occupancy |
|  | 3.2.3. | Spatial Separation and Exposure Protection |
|  | 3.2.4. | Fire Alarm and Detection Systems |
|  | 3.2.5. | Provisions for Fire-fighting |
|  | 3.2.6. | Additional Requirements for High Buildings |
|  | 3.2.7. | Lighting and Emergency Power Systems |
|  | 3.2.8. | Mezzanines and Openings Through Floor Assemblies |
|  | 3.2.9. | Standpipe Systems |
| Section | 3.3. | Safety Within Floor Areas |
|  | 3.3.1. | All Floor Areas |
|  | 3.3.2. | Assembly Occupancy |
|  | 3.3.3. | Care or Detention Occupancy |
|  | 3.3.4. | Residential Occupancy |
|  | 3.3.5. | Industrial Occupancy |
| Section | 3.4. | Exits |
|  | 3.4.1. | General |
|  | 3.4.2. | Number and Location of Exits from Floor Areas |
|  | 3.4.3. | Width and Height of Exits |
|  | 3.4.4. | Fire Separation of Exits |
|  | 3.4.5. | Exit Signs |
|  | 3.4.6. | Types of Exit Facilities |
|  | 3.4.7. | Fire Escapes |
| Section | 3.5. | Vertical Transportation |
|  | 3.5.1. | General |
|  | 3.5.2. | Elevator Required |
|  | 3.5.3. | Fire Separations |
|  | 3.5.4 | Dimensions and Signs |
| Section | 3.6. | Service Facilities |
|  | 3.6.1. | General |
|  | 3.6.2. | Service Rooms |
|  | 3.6.3. | Vertical Service Spaces and Service Facilities |
|  | 3.6.4. | Horizontal Service Spaces and Service Facilities |
| Section | 3.7. | Health Requirements |
|  | 3.7.1. | Height and Area of Rooms |
|  | 3.7.2. | Windows |
|  | 3.7.3. | Ventilation |
|  | 3.7.4. | Plumbing Facilities |
|  | 3.7.5. | Health Care Facility Systems |
|  | 3.7.6. | Food Premises |
| Section | 3.8. | Barrier-Free Design |
|  | 3.8.1. | General |
|  | 3.8.2. | Occupancy Requirements |
|  | 3.8.3. | Design Standards |
| Section | 3.9. | Portable Classrooms |
|  | 3.9.1. | Scope |
|  | 3.9.2. | Interior Finish |
|  | 3.9.3. | Application |
| Section | 3.10. | Self-Service Storage Buildings |
|  | 3.10.1. | Scope |
|  | 3.10.2. | Requirements for All Buildings |
|  | 3.10.3. | Additional Requirements for Buildings Containing More Than 1 Storey |
|  | 3.10.4. | Additional Requirements for 1 Storey Buildings |
| Section | 3.11. | Public Pools |
|  | 3.11.1. | General |
|  | 3.11.2. | Designations of Public Pools |
|  | 3.11.3. | Pool and Pool Deck Construction Requirements for All Class A and Class B Pools |
|  | 3.11.4. | Public Pools Equipped with Diving Boards or Diving Platforms |
|  | 3.11.5. | Ramps into Public Pools in Group B, Division 2 or 3, Major Occupancies |
|  | 3.11.6. | Modified Pools |
|  | 3.11.7. | Wave Action Pools |
|  | 3.11.8. | Recirculation for Public Pools |
|  | 3.11.9. | Dressing Rooms, Locker Facilities, and Plumbing Facilities for All Public Pools |
|  | 3.11.10. | Emergency Provisions for All Public Pools |
|  | 3.11.11. | Service Rooms and Storage for All Public Pools |
|  | 3.11A. | Public Spas |
|  | 3.11A.1. | General |
|  | 3.11A.2. | Public Spa and Deck Design and Construction Requirements |
|  | 3.11A.3. | Ramps Into Public Spas |
|  | 3.11A.4. | Water Circulation for Public Spas |
|  | 3.11A.5. | Emergency Provisions for All Public Spas |
|  | 3.11A.6. | Service Rooms and Storage for All Public Spas |
| Section | 3.12. | Rapid Transit Stations |
|  | 3.12.1. | Scope and Definitions |
|  | 3.12.2. | Construction Requirements |
|  | 3.12.3. | Safety Requirements Within Stations |
|  | 3.12.4. | Means of Egress |
|  | 3.12.5. | Fire Safety Provisions |
|  | 3.12.6. | Required Sanitary Facilities |
|  | 3.12.7. | Emergency Ventilation |
|  | 3.12.8. | Barrier-Free Design |
| Section | 3.13. | Tents and Air-Supported Structures |
|  | 3.13.1. | Tents |
|  | 3.13.2. | Air-Supported Structures |
| Section | 3.14. | Signs |
|  | 3.14.1. | Scope |
|  | 3.14.2. | Alterations |
|  | 3.14.3. | Structural Requirements |
|  | 3.14.4. | Plastic Sign Facing Materials |
|  | 3.14.5. | Location Restrictions |
| Section | 3.15. | Additional Requirements For Change of Use |
|  | 3.15.1. | Scope |
|  | 3.15.2. | Additional Construction |

Part 3
Fire Protection, Occupant Safety and Accessibility

Section 3.1. General

3.1.1. Scope

3.1.1.1.  Scope

(1)  The scope of this Part shall be as described in Section 2.1.

3.1.1.2.  Reserved

3.1.2. Classification of Buildings or Parts of Buildings by Major Occupancy

3.1.2.1.  Classification of Buildings

(1)  Except as permitted by Articles 3.1.2.3. to 3.1.2.6., every building or part thereof shall be classified according to its major occupancy as belonging to one of the Groups or Divisions described in Table 3.1.2.1.

Table 3.1.2.1.

Major Occupancy Classification

Forming Part of Sentence 3.1.2.1.(1)

| Group | Division | Description of Major Occupancies |
| --- | --- | --- |
| A | 1 | Assembly occupancies intended for the production and viewing of the performing arts |
| A | 2 | Assembly occupancies not elsewhere classified in Group A |
| A | 3 | Assembly occupancies of the arena type |
| A | 4 | Assembly occupancies in which occupants are gathered in the open air |
| B | 1 | Detention occupancies |
| B | 2 | Care and treatment occupancies |
| B | 3 | Care occupancies |
| C | — | Residential occupancies |
| D | — | Business and personal services occupancies |
| E | — | Mercantile occupancies |
| F | 1 | High hazard industrial occupancies |
| F | 2 | Medium hazard industrial occupancies |
| F | 3 | Low hazard industrial occupancies |
| Column 1 | 2 | 3 |

(2)  A building intended for use by more than one major occupancy shall be classified according to all major occupancies for which it is used or intended to be used.

3.1.2.2.  Occupancies of the Same Classification

(1)  Any building is deemed to be occupied by a single major occupancy, notwithstanding its use for more than one major occupancy, provided that all occupancies are classified as belonging to the same Group classification or, where the Group is divided into Divisions, as belonging to the same Division classification described in Table 3.1.2.1.

3.1.2.3.  Arena Type Buildings

(1)  An arena type building intended for occasional use for trade shows and similar exhibition purposes shall be classified as Group A, Division 3 occupancy.

(2)  If the building area of an arena type building referred to in Sentence (1) is more than 1 500 m2, the building shall be sprinklered.

3.1.2.4.  Police Stations

(1)  A police station with detention quarters is permitted to be classified as a Group B, Division 2 major occupancy provided the station is not more than 1 storey in building height and 600 m2 in building area.

3.1.2.5.  Group B, Division 3 Occupancies

(1)  Group B, Division 3 occupancies are permitted to be classified as Group C major occupancies provided

(a)	the occupants live as a single housekeeping unit in a suite with sleeping accommodation for not more than 10 persons, and

(b)	not more than 2 occupants require assistance in evacuation in case of an emergency.

3.1.2.6.  Restaurants

(1)  A restaurant is permitted to be classified as a Group E major occupancy provided the restaurant is designed to accommodate not more than 30 persons consuming food or drink.

3.1.3. Multiple Occupancy Requirements

3.1.3.1.  Separation of Major Occupancies

(1)  Except as permitted by Sentences (2) and (3), major occupancies shall be separated from adjoining major occupancies by fire separations having fire-resistance ratings conforming to Table 3.1.3.1.

Table 3.1.3.1.

Major Occupancy Fire Separations(1)

Forming Part of Sentence 3.1.3.1.(1)

| Major Occupancy | Minimum Fire-Resistance Rating of Fire Separation, h (1) |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Adjoining Major Occupancy |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A-1 | A-2 | A-3 | A-4 | B-1 | B-2 | B-3 | C | D | E | F-1 | F-2 | F-3 |
| A-1 A-2 A-3 A-4 B-1 B-2 B-3 C D E F-1 F-2 F-3 | — 1 1 1 2 2 2 1 1 2 (2) 2 1 | 1 — 1 1 2 2 2 1 1 2 (2) 2 1 | 1 1 — 1 2 2 2 1 1 2 (2) 2 1 | 1 1 1 — 2 2 2 1 1 2 (2) 2 1 | 2 2 2 2 — 2 2 2 2 2 (2) 2 2 | 2 2 2 2 2 — 1 2 2 2 (2) 2 2 | 2 2 2 2 2 1 — 2 2 2 (2) 2 2 | 1 1 1 1 2 2 2 — 1 2(3) (2) 2(4) 1 | 1 1 1 1 2 2 2 1 — — 3 — — | 2 2 2 2 2 2 2 2(3) — — 3 — — | (2) (2) (2) (2) (2) (2) (2) (2) 3 3 — 2 2 | 2 2 2 2 2 2 2 2(4) — — 2 — — | 1 1 1 1 2 2 2 1 — — 2 — — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |

Notes to Table 3.1.3.1.:

(1) Section 3.3. contains requirements for the separation of occupancies and tenancies that are in addition to the requirements for the separation of major occupancies.

(2) See Sentence 3.1.3.2.(1).

(3) See Sentence 3.1.3.1.(2).

(4) See Sentence 3.1.3.2.(2).

(2)  In a building not more than 3 storeys in building height, if not more than 2 dwelling units are contained together with a Group E major occupancy, the fire-resistance rating of the fire separation between the 2 major occupancies need not be more than 1 h.

(3)  The fire separations required between major occupancies in Sentence (1) are permitted to be penetrated by floor openings protected in conformance with Subsection 3.2.8., except for fire separations for Group F, Division 1 major occupancies and for mezzanines described in Sentence 3.2.8.2.(1).

3.1.3.2.  Prohibition of Occupancy Combinations

(1)  No major occupancy of Group F, Division 1 shall be contained within a building with any occupancy classified as Group A, B or C.

(2)  Except as provided in Sentence (4) and Sentence 3.10.2.4.(9), not more than one suite of residential occupancy shall be contained within a building classified as a Group F, Division 2 major occupancy.

(3)  A sleeping room or sleeping area shall not open directly into a room or area where food is intended to be stored, prepared, processed, distributed, served, sold or offered for sale.

(4)  A Group F, Division 2 major occupancy is permitted in a building containing only live/work units and is for the exclusive use of the occupants of the live/work units.

3.1.4. Combustible Construction

3.1.4.1.  Combustible Materials Permitted

(1)  A building permitted to be of combustible construction is permitted to be constructed of combustible materials described in Part 9, with or without noncombustible components.

3.1.4.2.  Protection of Foamed Plastics

(1)  Foamed plastics which form part of a wall or ceiling assembly in combustible construction shall be protected from adjacent spaces in the building, other than adjacent concealed spaces within attic or roof spaces, crawl spaces, and wall assemblies

(a)	by one of the interior finishes described in Subsections 9.29.4. to 9.29.9.,

(b)	by any thermal barrier that meets the requirements of Sentence 3.1.5.11.(2), or

(c)	where the building does not contain a Group B or Group C major occupancy, by sheet metal

(i)	mechanically fastened to the supporting assembly independent of the insulation,

(ii)	not less than 0.38 mm thick, and

(iii)	with a melting point not below 650oC.

3.1.4.3.  Wires and Cables

(1)  Optical fibre cables and electrical wires and cables installed in a building permitted to be of combustible construction shall

(a)	not convey flame or continue to burn for more than 1 min when tested in conformance with the Vertical Flame Test in Clause 4.11.1. of CAN/CSA-C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables”, or

(b)	be located in

(i)	totally enclosed noncombustible raceways,

(ii)	concealed spaces in walls,

(iii)	concrete slabs, or

(iv)	totally enclosed nonmetallic raceways conforming to Article 3.1.5.19.

(2)  The requirement in Clause (1)(a) is considered to be met where the wires and cables

(a)	exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test - Cables in Cabletrough in Clause 4.11.4. of CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT4 Rating), or

(b)	exhibit a flame-spread of not more than 1.5 m, a smoke density of not more than 0.5 at peak optical density and a smoke density not more than 0.15 at average optical density when tested in conformance with the Flame and Smoke Test in the Appendix to CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT6 Rating).

(3)  Service-entrance cables for communication and community antennae distribution systems need not conform to Sentence (1) provided

(a)	the service-entrance cables are located in a building permitted to be of combustible construction and are not more than 3 m in length from the point of entry into the building or from the point of leaving protection as required in Clause (1) (b), or

(b)	the service entrance cables enter into an electrical or telephone service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

3.1.4.4.  Fire-Retardant Treated Wood

(1)  If fire-retardant treated wood is specified in this Part, the wood shall

(a)	be pressure impregnated with fire-retardant chemicals in conformance with CAN/CSA-O80 Series-M, “Wood Preservation”, and

(b)	have a flame-spread rating not more than 25.

3.1.4.5.  Heavy Timber Construction Alternative

(1)  If combustible construction is permitted and is not required to have a fire-resistance rating more than 45 min, heavy timber construction is permitted to be used.

(2)  If heavy timber construction is permitted, it shall conform to Article 3.1.4.6.

3.1.4.6.  Heavy Timber Construction

(1)  Wood elements in heavy timber construction shall be arranged in heavy solid masses and with essentially smooth flat surfaces to avoid thin sections and sharp projections.

(2)  The actual dimensions of solid sawn lumber used in heavy timber construction shall conform to CAN/CSA-O141, “Softwood Lumber”.

(3)  Except as permitted by Sentences (4) to (7), the minimum dimensions of wood elements in heavy timber construction shall conform to Table 3.1.4.6.

Table 3.1.4.6.

Heavy Timber Dimensions

Forming Part of Sentence 3.1.4.6.(3)

| Supported Assembly | Structural Element | Solid Sawn (width x depth), mm x mm | Glued-Laminated (width x depth), mm x mm | Round (diam), mm |
| --- | --- | --- | --- | --- |
| Roofs only | Columns | 140 x 191 | 130 x 190 | 180 |
|  | Arches supported on the tops of walls or abutments | 89 x 140 | 80 x 152 | — |
|  | Beams, girders and trusses | 89 x 140 | 80 x 152 | — |
|  | Arches supported at or near the floor line | 140 x 140 | 130 x 152 | — |
| Floors, floors plus roofs | Columns | 191 x 191 | 175 x 190 | 200 |
|  | Beams, girders, trusses and arches | 140 x 241 or 191 x 191 | 130 x 228 or 175 x 190 | — |
| Column 1 | 2 | 3 | 4 | 5 |

(4)  Roof arches supported on the tops of walls or abutments, roof trusses, roof beams and roof girders in heavy timber construction shall be spliced where necessary with splice plates not less than 64 mm thick and be

(a)	not less than 64 mm wide where 2 or more spaced members are used for the construction, with intervening spaces

(i)	blocked solidly throughout, or

(ii)	tightly closed by a continuous wood cover plate not less than 38 mm thick secured to the underside of the members, or

(b)	not less than 64 mm wide, provided there is automatic sprinkler protection under the roof deck.

(5)  Floors in heavy timber construction shall be of glued-laminated or solid sawn plank not less than

(a)	64 mm thick, splined or tongued and grooved, or

(b)	38 mm wide and 89 mm deep set on edge and well-spiked together.

(6)  Floors in heavy timber construction shall be laid

(a)	so that no continuous line of end joints will occur except at points of support, and covered with

(i)	tongued and grooved flooring not less than 19 mm thick laid cross-wise or diagonally, or

(ii)	tongued and grooved phenolic-bonded plywood, strandboard or waferboard not less than 12.5 mm thick, and

(b)	not closer than 15 mm to the walls to provide for expansion, with the gap covered at the top or bottom.

(7)  Roofs in heavy timber construction shall be of tongued and grooved phenolic-bonded plywood not less than 28 mm thick, or glued-laminated or solid sawn plank that is

(a)	not less than 38 mm thick, splined or tongued and grooved, or

(b)	not less than 38 mm wide and 64 mm deep set on edge and laid so that no continuous line of end joints will occur except at the points of support.

(8)  Wood columns in heavy timber construction shall be continuous or superimposed throughout all storeys.

(9)  Superimposed wood columns in heavy timber construction shall be connected by

(a)	reinforced concrete or metal caps with brackets,

(b)	steel or iron caps with pintles and base plates, or

(c)	timber splice plates fastened to the columns by metal connectors housed within the contact faces.

(10)  Where beams and girders in heavy timber construction enter masonry, wall plates, boxes of the self-releasing type or hangers shall be used.

(11)  Wood girders and beams in heavy timber construction shall be closely fitted to columns, and adjoining ends shall be connected by ties or caps to transfer horizontal loads across the joints.

(12)  In heavy timber construction, intermediate wood beams used to support a floor shall be supported on top of the girders or on metal hangers into which the ends of the beams are closely fitted.

3.1.4.7.  Fabric Canopies

(1)  Where a building is permitted to be of combustible construction, fabrics or films used as part of an exterior canopy shall conform to CAN/ULC-S109-M, “Standard for Flame Tests of Flame-Resistant Fabrics and Films”.

3.1.5. Noncombustible Construction

3.1.5.1.  Noncombustible Materials

(1)  Except as permitted by Articles 3.1.5.2. to 3.1.5.23., 3.1.13.4. and 3.2.2.16., a building or part of a building required to be of noncombustible construction, shall be constructed with noncombustible materials.

3.1.5.2.  Minor Combustible Components

(1)  The following minor combustible components are permitted in a building required to be of noncombustible construction:

(a)	paint,

(b)	tightly adhering paper covering not more than 1 mm thick applied to a noncombustible backing provided the assembly has a flame-spread rating not more than 25,

(c)	mastics and caulking materials applied to provide flexible seals between the major components of exterior wall construction,

(d)	fire stop materials conforming to Sentence 3.1.9.1.(1) and Article 3.1.11.7.,

(e)	tubing for pneumatic controls provided it has an outside diameter not more than 10 mm,

(f)	adhesives, vapour barriers and sheathing papers,

(g)	electrical outlet and junction boxes,

(h)	wood blocking within wall assemblies intended for the attachment of handrails, fixtures, and similar items mounted on the surface of the wall, and

(i)	similar minor components.

3.1.5.3.  Combustible Roofing Materials

(1)  Combustible roof covering which has an A, B, or C classification determined in conformance with Subsection 3.1.15. is permitted on a building required to be of noncombustible construction.

(2)  Combustible roof sheathing and roof sheathing supports installed above a concrete deck are permitted on a building required to be of noncombustible construction provided

(a)	the concrete deck is not less than 50 mm thick,

(b)	the height of the roof space above the deck is not more than 1 000 mm,

(c)	the roof space is divided into compartments by fire stops in conformance with Article 3.1.11.5.,

(d)	openings through the concrete deck other than for noncombustible roof drains and plumbing piping are protected by masonry or concrete shafts

(i)	constructed as fire separations having a fire-resistance rating not less than 1 h, and

(ii)	extending from the concrete deck to not less than 150 mm above the adjacent roof sheathing,

(e)	the perimeter of the roof is protected by a noncombustible parapet extending from the concrete deck to not less than 150 mm above the adjacent sheathing, and

(f)	except as permitted by Clause (d), the roof space does not contain any building services.

(3)  Combustible cant strips, roof curbs, nailing strips and similar components used in the installation of roofing are permitted on a building required to be of noncombustible construction.

(4)  Wood nailer facings to parapets, not more than 600 mm high, are permitted on a building required to be of noncombustible construction, if the facings and any roof membranes covering the facings are protected by sheet metal.

3.1.5.4.  Combustible Glazing and Skylights

(1)  Combustible skylight assemblies are permitted in a building required to be of noncombustible construction if the assemblies have a flame-spread rating not more than

(a)	150 provided the assemblies

(i)	have an individual area not more than 9 m2,

(ii)	have an aggregate horizontal projected area of the openings through the ceiling not more than 25% of the area of the ceiling of the room or space in which they are located, and

(iii)	are spaced not less than 2 500 mm from adjacent assemblies and 1 200 mm from required fire separations, or

(b)	75 provided the assemblies

(i)	have an individual area not more than 27 m2,

(ii)	have an aggregate horizontal projected area of the openings through the ceiling not more than 33% of the area of the ceiling of the room or space in which they are located, and

(iii)	are spaced not less than 1 200 mm from adjacent assemblies and from required fire separations.

(2)  Combustible vertical glazing installed no higher than the second storey is permitted in a building required to be of noncombustible construction.

(3)  Except as permitted by Sentence (4), the combustible vertical glazing permitted by Sentence (2) shall have a flame-spread rating not more than 75.

(4)  The flame-spread rating of combustible glazing in Sentence (2) is permitted to be not more than 150 if the aggregate area of glazing is not more than 25% of the wall area of the storey in which it is located, and

(a)	the glazing is installed in a building not more than 1 storey in building height,

(b)	the glazing in the first storey is separated from the glazing in the second storey in accordance with the requirements of Article 3.2.3.16. for opening protection, or

(c)	sprinklers are installed in

(i)	any storey with combustible glazing, and

(ii)	the storey immediately above the storey with combustible glazing.

(5)  Combustible window sashes and frames are permitted in a building required to be of noncombustible construction provided

(a)	each window in an exterior wall face is an individual unit separated by noncombustible wall construction from every other opening in the wall,

(b)	windows in exterior walls in contiguous storeys are separated by not less than 1 000 mm of noncombustible construction, and

(c)	the aggregate area of openings in an exterior wall face of a fire compartment is not more than 40% of the area of the wall face.

3.1.5.5.  Combustible Components for Exterior Walls

(1)  Except for an exposing building face required to conform to Sentence 3.2.3.7.(1) or Sentence 3.2.3.7.(4), an exterior non-loadbearing wall assembly that includes combustible components is permitted to be used in a building required to be of noncombustible construction provided

(a)	the building is

(i)	not more than 3 storeys in building height, or

(ii)	not more than 6 storeys in building height if sprinklered,

(b)	the interior surfaces of the wall assembly are protected by a thermal barrier conforming to Sentence 3.1.5.11.(3), and

(c)	the wall assembly satisfies the criteria of Sentences (2) and (3) when subjected to testing in conformance with CAN/ULC-S134, “Standard Method of Fire Test of Exterior Wall Assemblies”.

(2)  Flaming on or in the wall assembly shall not spread more than 5 m above the opening during the test procedure referenced in Sentence (1).

(3)  The heat flux during the flame exposure on a wall assembly shall be not more than 35 kW/m2 measured 3.5 m above the opening during the test procedure referenced in Sentence (1).

(4)  A wall assembly permitted by Sentence (1) that includes combustible cladding of fire-retardant treated wood shall be tested for fire exposure after the cladding has been subjected to an accelerated weathering test as specified in ASTM D2898, “Methods for Accelerated Weathering on Fire-Retardant-Treated Wood for Fire Testing”.

(5)  Wood decorative cladding is permitted to be used on exterior canopy fascias of a building required to be of noncombustible construction provided the cladding is fire-retardant treated wood that has been, before testing, conditioned in conformance with ASTM D2898, “Methods for Accelerated Weathering on Fire-Retardant-Treated Wood for Fire Testing”, and the canopy is

(a)	a first floor canopy, or

(b)	not more than 6 m above ground level

(6)  The requirements in this Article do not apply where foamed plastic insulation is used in an exterior wall assembly of a building and the insulation is protected in conformance with Sentences 3.2.3.7.(7) and (8).

3.1.5.6.  Nailing Elements

(1)  Wood nailing elements attached directly to or set into a continuous noncombustible backing for the attachment of interior finishes, are permitted in a building required to be of noncombustible construction provided the concealed space created by the wood elements is not more than 50 mm thick.

3.1.5.7.  Combustible Millwork

(1)  Combustible millwork including interior trim, doors and door frames, show windows together with their frames, aprons and backing, handrails, shelves, cabinets and counters is permitted in a building required to be of noncombustible construction.

3.1.5.8.  Combustible Flooring Elements

(1)  Combustible stage flooring supported on noncombustible structural members is permitted in a building required to be of noncombustible construction.

(2)  Wood members more than 50 mm but not more than 375 mm high applied directly to or set into a noncombustible floor slab are permitted for the construction of a raised platform in a building required to be of noncombustible construction provided the concealed spaces are fire stopped in conformance with Sentence 3.1.11.3.(2).

(3)  The floor system for the raised platform referred to in Sentence (2) is permitted to include combustible subfloor and combustible finished flooring.

(4)  Combustible finished flooring is permitted in a building required to be of noncombustible construction.

3.1.5.9.  Combustible Stairs in Dwelling Units

(1)  Combustible stairs are permitted in a dwelling unit in a building required to be of noncombustible construction.

3.1.5.10.  Combustible Interior Finish

(1)  Combustible interior finish, including paint, wallpaper, and other interior finishes not more than 1 mm thick, is permitted in a building required to be of noncombustible construction.

(2)  Combustible interior wall finishes, other than foamed plastics, are permitted in a building required to be of noncombustible construction provided they

(a)	are not more than 25 mm thick, and

(b)	have a flame-spread rating not more than 150 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction.

(3)  Combustible interior ceiling finishes, other than foamed plastics, are permitted in a building required to be of noncombustible construction provided they

(a)	are not more than 25 mm thick, except for exposed fire-retardant treated wood battens, and

(b)	have a flame-spread rating not more than 25 on any exposed surface, or on any surface that would be exposed by cutting through the material in any direction, or are of fire-retardant treated wood, except that not more than 10% of the ceiling area within each fire compartment is permitted to have a flame-spread rating not more than 150.

3.1.5.11.  Combustible Insulation and its Protection

(1)  Combustible insulation, other than foamed plastics, is permitted in a building required to be of noncombustible construction provided that it has a flame-spread rating not more than 25 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, where the insulation is not protected as described in Sentences (3) and (4).

(2)  Foamed plastic insulation having a flame-spread rating not more than 25 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in a building required to be of noncombustible construction provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of

(a)	not less than 12.7 mm thick gypsum board mechanically fastened to a supporting assembly independent of the insulation,

(b)	lath and plaster, mechanically fastened to a supporting assembly independent of the insulation,

(c)	masonry,

(d)	concrete, or

(e)	any thermal barrier that meets the requirements of classification B when tested in conformance with CAN4-S124-M, “Standard Method of Test for the Evaluation of Protective Coverings for Foamed Plastic”.

(3)  Combustible insulation having a flame-spread rating more than 25 but not more than 500 on an exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the exterior walls of a building required to be of noncombustible construction, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier as described in Sentence (2), except that in a building that is not sprinklered and is more than 18 m high, measured between grade and the floor level of the top storey, or in a building that is not sprinklered and is regulated by the provisions of Subsection 3.2.6., the insulation shall be protected by a thermal barrier consisting of

(a)	gypsum board not less than 12.7 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled,

(b)	lath and plaster, mechanically fastened to a supporting assembly independent of the insulation,

(c)	masonry or concrete not less than 25 mm thick, or

(d)	any thermal barrier that, when tested in conformance with CAN/ULC-S101-M, “Standard Methods of Fire Endurance Tests of Building Construction and Materials”, will not develop an average temperature rise more than 140°C or a maximum temperature rise more than 180°C at any point on its unexposed face within 10 min.

(4)  Combustible insulation having a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the interior walls, within ceilings and within roof assemblies of a building required to be of noncombustible construction, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier as described in Sentence (2), except that in a building that is not sprinklered and is more than 18 m high, measured between grade and the floor level of the top storey, or in a building that is not sprinklered and is regulated by the provisions of Subsection 3.2.6., the insulation shall be protected by a thermal barrier consisting of

(a)	Type X gypsum board not less than 15.9 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled, conforming to

(i)	CAN/CSA-A82.27-M, “Gypsum Board”,

(ii)	ASTM C 36, “Gypsum Wallboard”,

(iii)	ASTM C 442, “Gypsum Backing Board and Coreboard”,

(iv)	ASTM C 588, “Gypsum Base for Veneer Plaster”,

(v)	ASTM C 630, “Water Resistant Gypsum Board Backing”,

(vi)	ASTM C 931, “Exterior Gypsum Soffit Board”, or

(vii)	ASTM C 960, “Predecorated Gypsum Board”,

(b)	non-loadbearing masonry or concrete not less than 50 mm thick,

(c)	loadbearing masonry or concrete not less than 75 mm thick, or

(d)	any thermal barrier that, when tested in conformance with CAN/ULC-S101-M, “Standard Methods of Fire Endurance Tests of Building Construction and Materials”,

(i)	will not develop an average temperature rise more than 140°C or a maximum temperature rise more than 180°C at any point on its unexposed face within 20 min, and

(ii)	will remain in place for not less than 40 min.

(5)  Combustible insulation, including foamed plastics, installed above roof decks, outside of foundation walls below ground level and beneath concrete slabs-on-ground is permitted to be used in a building required to be of noncombustible construction.

(6)  Thermosetting foamed plastic insulation having a flame-spread rating not more than 500 which forms part of a factory-assembled exterior wall panel that does not incorporate an air space is permitted to be used in a building required to be of noncombustible construction provided

(a)	the foamed plastic is protected on both sides by sheet steel not less than 0.38 mm thick which will remain in place for not less than 10 min when the wall panel is tested in conformance with CAN/ULC-S101-M, “Standard Methods of Fire Endurance Tests of Building Construction and Materials”,

(b)	the flame-spread rating of the wall panel, determined by subjecting a sample including an assembled joint to the appropriate test described in Subsection 3.1.12., is not more than the flame-spread rating permitted for the room or space which it bounds,

(c)	the building does not contain a Group B or Group C major occupancy, and

(d)	the building is not more than 18 m high, measured between grade and the floor level of the top storey.

(7)  Foamed plastic insulation having a flame-spread rating of not more than 500 which forms part of a factory-assembled interior or exterior wall or ceiling panel that does not incorporate an air space is permitted to be used in a building required to be of noncombustible construction provided

(a)	the building is sprinklered,

(b)	the building is not more than 18 m high, measured between grade and the floor level of the uppermost storey,

(c)	the building does not contain a Group A, B or C major occupancy,

(d)	the panels are listed for compliance with ULC/ORD C376-1995, “Fire Growth of Foamed Plastic Insulated Building Panels in a Full-Scale Room Configuration”, and

(e)	the flame-spread rating of the wall panel, determined by subjecting a sample, including an assembled joint, to the appropriate test described in Subsection 3.1.12., is not more than the flame-spread rating permitted for the room or space which it bounds.

3.1.5.12.  Combustible Elements in Partitions

(1)  Except as permitted by Sentence (2), solid lumber partitions not less than 38 mm thick and wood framing in partitions located in a fire compartment not more than 600 m2 in area are permitted to be used in a building required to be of noncombustible construction in a floor area that is not sprinklered provided the partitions

(a)	are not required fire separations, and

(b)	are not located in a care or detention occupancy.

(2)  Partitions installed in a building of noncombustible construction are permitted to contain wood framing provided

(a)	the building is not more than 3 storeys in building height,

(b)	the partitions are not located in a care or detention occupancy, and

(c)	the partitions are not installed as enclosures for exits or vertical service spaces.

(3)  Solid lumber partitions not less than 38 mm thick and partitions that contain wood framing are permitted to be used in a building required to be of noncombustible construction provided

(a)	the floor area containing the partitions is sprinklered, and

(b)	the partitions are not

(i)	located in a care or detention occupancy,

(ii)	installed as enclosures for exits or vertical service spaces, or

(iii)	used to satisfy the requirements of Clause 3.2.8.1.(1)(a).

3.1.5.13.  Storage Lockers in Residential Buildings

(1)  Storage lockers in storage rooms are permitted to be constructed of wood in a building of residential occupancy required to be of noncombustible construction.

3.1.5.14.  Combustible Ducts

(1)  Except as required by Sentence 3.6.4.3.(1), combustible ducts, including plenums and duct connectors, are permitted to be used in a building required to be of noncombustible construction provided these ducts and duct connectors are used only in horizontal runs.

(2)  Combustible duct linings, duct coverings, duct insulation, vibration isolation connectors, duct tape, pipe insulation and pipe coverings are permitted to be used in a building required to be of noncombustible construction provided they conform to the appropriate requirements of Part 6.

(3)  In a building required to be of noncombustible construction, combustible ducts need not comply with the requirements of Part 6 provided the ducts are

(a)	part of a duct system conveying only ventilation air, and

(b)	contained entirely within a dwelling unit.

3.1.5.15.  Combustible Piping Materials

(1)  Except as permitted by Clause 3.1.5.2.(1)(e), Sentences (2) and (3), and Article 3.1.5.21., combustible piping and tubing and associated adhesives are permitted to be used in a building required to be of noncombustible construction provided that, except when concealed in a wall or concrete floor slab, they

(a)	have a flame-spread rating not more than 25, and

(b)	if used in a building described in Subsection 3.2.6., have a smoke developed classification not more than 50.

(2)  Combustible sprinkler piping is permitted to be used within a sprinklered floor area in a building required to be of noncombustible construction.

(3)  Polypropylene pipes and fittings are permitted to be used for drain, waste and vent piping for the conveyance of highly corrosive materials and for piping used to distribute distilled or dialyzed water in laboratory and hospital facilities in a building required to be of noncombustible construction, provided

(a)	the building is sprinklered,

(b)	the piping is not located in a vertical shaft, and

(c)	piping that penetrates a fire separation is sealed at the penetration by a fire stop system that, when subjected to the fire test method in CAN4-S115-M, “Standard Method of Fire Tests of Firestop Systems”, has an FT rating not less than the fire-resistance rating of the fire separation.

3.1.5.16.  Combustible Plumbing Fixtures

(1)  Combustible plumbing fixtures are permitted in a building required to be of noncombustible construction if they are constructed of material having a flame-spread rating and smoke developed classification permitted in Subsection 3.1.13.

3.1.5.17.  Wires and Cables

(1)  Except as permitted by Articles 3.1.5.18. and 3.1.5.20, optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes are permitted in a building required to be of noncombustible construction, provided

(a)	the wires and cables exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test – Cables in Cabletrough in Clause 4.11.4. of CAN/CSA-C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT4 Rating),

(b)	the wires and cables are located in

(i)	totally enclosed noncombustible raceways,

(ii)	concealed spaces in walls,

(iii)	concrete slabs,

(iv)	a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h, or

(v)	totally enclosed nonmetallic raceways conforming to Article 3.1.5.19., or

(c)	the wires and cables are communication cables used at the service entry to a building and are not more than 3 m long.

(2)  The requirement in Clause (1)(a) is considered to be met where the wires and cables exhibit a flame-spread of not more than 1.5 m, a smoke density of not more than 0.5 at peak optical density and a smoke density not more than 0.15 at average optical density when tested in conformance with the Flame and Smoke Test in the Appendix to CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT6 Rating).

3.1.5.18.  Combustible Travelling Cables for Elevators

(1)  Combustible travelling cables are permitted on elevating devices in a building required to be of noncombustible construction.

3.1.5.19.  Nonmetallic Raceways

(1)  Totally enclosed nonmetallic raceways not more than 625 mm2 in cross-sectional area are permitted to be used in a building required to be of noncombustible construction to enclose optical fibre cables and electrical wires and cables, provided the raceways exhibit a vertical char not more than 1.5 m when tested in conformance with the Vertical Flame Test (FT4 Rating) – Conduit or Tubing on Cable Tray in Clause 6.16 of CSA C22.2 No. 211.0-M, “General Requirements and Methods of Testing for Nonmetallic Conduit”.

3.1.5.20.  Wires in Computer Room Floors

(1)  Optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes, located in the space below a raised floor in a computer room, are permitted in a building required to be of noncombustible construction provided they do not convey flame or continue to burn for more than 1 min when tested in conformance with the Vertical Flame Test in Clause 4.11.1. of CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT1 Rating).

(2)  The requirement in Sentence (1) is considered to be met where the wires and cables

(a)	exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test – Cables in Cabletrough in Clause 4.11.4. of CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT4 Rating), or

(b)	exhibit a flame-spread of not more than 1.5 m, a smoke density of not more than 0.5 at peak optical density and a smoke density not more than 0.15 at average optical density when tested in conformance with the Flame and Smoke Test in the Appendix to CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT6 Rating).

3.1.5.21.  Combustible Components in Public Pools and Public Spas

(1)  Combustible fittings and components in a public pool or public spa, including main drains, piping, skimmers, return inlets, steps, ladder rungs and liners, are permitted in a building required to be of noncombustible construction.

3.1.5.22.  Canopies Having Combustible Elements

(1)  Exterior canopies having combustible fabrics or films are permitted on a building required to be of noncombustible construction provided the fabrics and films conform to CAN/ULC-S109-M, “Standard for Flame Tests of Flame-Resistant Fabrics and Films”.

(2)  Except as permitted in Sentence (3), exterior marquees, not greater than 7.5 m from ground level to the top of the marquee, having combustible elements other than fabrics or films conforming to Sentence (1), are permitted on a building required to be of noncombustible construction, provided every opening in the exposed wall of the building above the marquee is protected with wired glass in accordance with the Supplementary Guidelines where these openings are within

(a)	4.5 m horizontally of the marquee, and

(b)	9 m vertically above the marquee.

(3)  The protection required by Sentence (2) is permitted to be waived if the building is sprinklered.

3.1.5.23.  Combustible Mezzanines

(1)  In a building required to be of noncombustible construction, a mezzanine located within a live/work unit is permitted to be of combustible construction provided the area of the mezzanine is not more than 25% of the floor area of the live/work unit or 20 m2, whichever is less, and has no obstructions more than 1 070 mm above the floor.

3.1.5.24.  Combustible Solar Collector Systems

(1)  A combustible solar collector system is permitted to be installed above the roof of a building required to be of noncombustible construction.

3.1.6. Reserved

3.1.7. Fire-Resistance Ratings

3.1.7.1.  Determination of Ratings

(1)  Except as permitted by Sentence (2) and Article 3.1.7.2., the rating of a material, assembly of materials or a structural member that is required to have a fire-resistance rating, shall be determined on the basis of the results of tests conducted in conformance with CAN/ULC-S101-M, “Standard Methods of Fire Endurance Tests of Building Construction and Materials”.

(2)  A material, assembly of materials or a structural member is permitted to be assigned a fire-resistance rating on the basis of the Supplementary Guidelines.

3.1.7.2.  Exception for Exterior Walls

(1)  The limit on the rise of temperature on the unexposed surface of an assembly as required by the tests referred to in Sentence 3.1.7.1.(1) shall not apply to an exterior wall that has a limiting distance of 1.2 m or more, provided correction is made for radiation from the unexposed surface in accordance with Sentence 3.2.3.1.(6).

3.1.7.3.  Exposure Conditions for Rating

(1)  Floor, roof and ceiling assemblies shall be rated for exposure to fire on the underside.

(2)  Firewalls and interior vertical fire separations shall be rated for exposure to fire on each side.

(3)  Exterior walls shall be rated for exposure to fire from inside the building.

3.1.7.4.  Minimum Fire-Resistance Rating

(1)  The use of materials or assemblies having a greater fire-resistance rating than required shall impose no obligation to exceed in whole or in part the minimum fire-resistance ratings required by this Part.

3.1.7.5.  Rating of Supporting Construction

(1)  Except as permitted by Sentence (2) and by Articles 3.2.2.20. to 3.2.2.83. for mixed types of construction, all loadbearing walls, columns and arches in the storey immediately below a floor or roof assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than that required for the supported floor or roof assembly.

(2)  Loadbearing walls, columns and arches supporting a service room or service space need not conform to Sentence (1).

(3)  If an assembly is required to be of noncombustible construction and have a fire-resistance rating, it shall be supported by noncombustible construction.

3.1.8. Fire Separations and Closures

3.1.8.1.  General Requirements

(1)  Any wall, partition or floor assembly required to be a fire separation shall

(a)	except as permitted by Sentence (2), be constructed as a continuous element, and

(b)	as required in this Part, have a fire-resistance rating as specified.

(2)  Openings in a fire separation shall be protected with closures, shafts or other means in conformance with Articles 3.1.8.4. to 3.1.8.17. and Subsections 3.1.9. and 3.2.8.

3.1.8.2.  Combustible Construction Support

(1)  Combustible construction that abuts on or is supported by a noncombustible fire separation shall be constructed so that its collapse under fire conditions will not cause the collapse of the fire separation.

3.1.8.3.  Continuity of Fire Separations

(1)  Except as permitted by Sentence 3.6.4.2.(2), a horizontal service space or other concealed space located above a required vertical fire separation, including the walls of a vertical shaft, shall be divided at the fire separation by an equivalent fire separation within the service space.

(2)  The fire separation required by Sentence (1) shall terminate so that smoke-tight joints are provided where it abuts on or intersects

(a)	a floor,

(b)	a roof slab, or

(c)	a roof deck.

(3)  Except as required by Subsection 3.6.3. for a shaft penetrating a roof assembly, a shaft, including an exit enclosure, that penetrates a fire separation, shall

(a)	extend through any horizontal service space or any other concealed space, and

(b)	terminate so that smoke-tight joints are provided where the shaft abuts on or intersects

(i)	a floor,

(ii)	a roof slab, or

(iii)	a roof deck.

3.1.8.4.  Determination of Ratings

(1)  Except as permitted by Sentences (2) and 3.1.8.14.(2), the fire-protection rating for a closure shall be determined on the basis of the results of tests conducted in conformance with the appropriate provisions in

(a)	CAN4-S104-M, “Standard Method for Fire Tests of Door Assemblies”,

(b)	CAN4-S106-M, “Standard Method for Fire Tests of Window and Glass Block Assemblies”, or

(c)	CAN/ULC-S112-M, “Standard Method of Fire Test of Fire-Damper Assemblies”.

(2)  Except as permitted by Sentence 3.1.8.10.(1), the fire-protection rating of a closure shall conform to Table 3.1.8.4. for the required fire-resistance rating of the fire separation.

Table 3.1.8.4.

Fire Protection Rating of Closure

Forming Part of Sentence 3.1.8.4.(2)

| Fire-Resistance Rating of Fire Separation | Required Fire-Protection Rating of Closure |
| --- | --- |
| 30 min | 20 min |
| 45 min | 45 min |
| 1 h | 45 min |
| 1.5 h | 1 h |
| 2 h | 1.5 h |
| 3 h | 2 h |
| 4 h | 3 h |
| Column 1 | 2 |

3.1.8.5.  Installation of Closures

(1)  Except where fire dampers, window assemblies and glass block are used as closures, closures of the same fire-protection rating installed on opposite sides of the same opening are deemed to have a fire-protection rating equal to the sum of the fire-protection ratings of the closures.

(2)  Except as otherwise specified in this Part, every door, window assembly or glass block used as a closure in a required fire separation

(a)	shall be installed in conformance with NFPA 80, “Standard for Fire Doors and Fire Windows”, and

(b)	where required to have a fire-protection rating, shall have labels or classification marks to identify the testing laboratory.

(3)  If a door is installed so that it could damage the integrity of a fire separation if its swing is unrestricted, door stops shall be installed to prevent the damage.

3.1.8.6.  Maximum Openings

(1)  The size of an opening in an interior fire separation required to be protected with a closure shall be not more than 11 m2, with no dimension more than 3.7 m, if a fire compartment on either side of the fire separation is not sprinklered.

(2)  The size of an opening in an interior fire separation required to be protected with a closure shall be not more than 22 m2, with no dimension more than 6 m, provided the fire compartments on both sides of the fire separation are sprinklered.

3.1.8.7.  Fire Dampers

(1)  Except as permitted by Article 3.1.8.8., a duct that connects 2 fire compartments or that penetrates an assembly required to be a fire separation shall be equipped with a fire damper.

(2)  A fire damper required by Sentence (1) or a fire damper used as a closure in a fire separation shall have a fire-protection rating conforming to Sentence 3.1.8.4.(2).

3.1.8.8.  Fire Dampers Waived

(1)  Fire dampers need not be provided in noncombustible branch ducts that have a melting point above 760°C and that penetrate a required fire separation provided the ducts

(a)	serve only air-conditioning units or combined air-conditioning and heating units discharging air not more than 1 200 mm above the floor and have a cross-sectional area not more than 0.013 m2, or

(b)	are connected to exhaust duct risers that are under negative pressure and in which the air flow is upward as required by Article 3.6.3.4. and are carried up inside the riser not less than 500 mm.

(2)  A continuous noncombustible duct penetrating a vertical fire separation not required to have a fire-resistance rating need not be equipped with a fire damper at the fire separation.

(3)  A noncombustible duct that penetrates a horizontal fire separation not required to have a fire-resistance rating need not be equipped with a fire damper at the fire separation.

(4)  A noncombustible duct that penetrates a fire separation that separates a vertical service space from the remainder of the building need not be equipped with a fire damper at the fire separation provided

(a)	the duct has a melting point above 760°C, and

(b)	each individual duct exhausts directly to the outside at the top of the vertical service space.

(5)  A continuous noncombustible duct having a melting point above 760°C that penetrates a vertical fire separation as required by Sentence 3.3.1.1.(1) between suites of other than residential or care or detention occupancy need not be equipped with a fire damper at the fire separation.

(6)  A duct that serves commercial cooking equipment and penetrates a required fire separation need not be equipped with a fire damper at the fire separation.

(7)  In elementary and secondary schools, a continuous noncombustible duct having a melting point above 760°C that pierces a fire separation having a fire-resistance rating of 30 min need not be equipped with a fire damper at the fire separation.

(8)  In a Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than 6 occupants requiring assistance in evacuation in case of an emergency and which is equipped with a fire alarm system, a duct need not be provided with a fire damper at a fire separation provided duct-type smoke detectors have been installed to control smoke circulation as described in Article 3.2.4.12.

3.1.8.9.  Installation of Fire Dampers

(1)  A fire damper shall be arranged to close automatically upon the operation of a fusible link conforming to ULC-S505, “Standard for Fusible Links for Fire Protection Service”, or other heat-actuated or smoke-actuated device.

(2)  A heat-actuated device referred to in Sentence (1) shall

(a)	be located where it is readily affected by an abnormal rise of temperature in the duct, and

(b)	have a temperature rating approximately 30°C above the maximum temperature that would exist in the system either with the system in operation or shut down.

(3)  A fire damper shall be installed in the plane of the fire separation so as to stay in place should the duct be dislodged during a fire.

(4)  A fire damper tested in the vertical or horizontal position shall be installed in the manner in which it was tested.

(5)  A tightly fitted access door shall be installed for each fire damper to provide access for the inspection of the damper and the resetting of the release device.

3.1.8.10.  Twenty-Minute Closures

(1)  A door assembly having a fire-protection rating not less than 20 min is permitted to be used as a closure in

(a)	a fire separation not required to have a fire-resistance rating more than 1 h, located between

(i)	a public corridor and a suite,

(ii)	a corridor and adjacent sleeping rooms, or

(iii)	a corridor and adjacent classrooms, offices and libraries in Group A, Division 2 major occupancies, or

(b)	a fire separation not required to have a fire-resistance rating more than 45 min, located in a building not more than 3 storeys in building height.

(2)  The requirements for noncombustible sills and combustible floor coverings in NFPA 80, “Standard for Fire Doors and Fire Windows”, do not apply to a door described in Sentence (1).

(3)  A door described in Sentence (1) shall have a clearance not more than 6 mm at the bottom and not more than 3 mm at the sides and top.

(4)  In elementary and secondary schools, a door assembly conforming to Articles 9.10.13.2. and 9.10.13.3. is permitted to be used as a closure in a fire separation having a fire-resistance rating of 30 min.

3.1.8.11.  Self-Closing Devices

(1)  Except as provided in Sentences (2) to (5), every door in a fire separation shall be equipped with a self-closing device designed to return the door to the closed position after each use.

(2)  Self-closing devices need not be provided on doors to freight elevators and dumbwaiters.

(3)  In a building that is not more than 3 storeys in building height, a self-closing device is not required on a door that is located between a classroom and a corridor providing access to exit from the classroom, except that a self-closing device is required on a door between a hazardous classroom and the corridor in an elementary or secondary school.

(4)  In a building that is not more than 3 storeys in building height, a self-closing device is not required on a door between a public corridor and an adjacent room or suite of business and personal services occupancy if the door is not located in

(a)	a dead-end portion of the corridor, or

(b)	a corridor which serves a hotel.

(5)  Within a fire compartment in a hospital or nursing home that complies with the requirements of Article 3.3.3.5., a self-closing device is not required on a door that is located between

(a)	a patient’s or resident’s sleeping room and a corridor serving the patient’s or resident’s sleeping room, or

(b)	a patient’s or resident’s sleeping room and an adjacent room that serves the patient’s or resident’s sleeping room.

3.1.8.12.  Hold-Open Devices

(1)  A hold-open device is permitted on a door in a required fire separation, other than an exit door in a building more than 3 storeys in building height, and on a door for a vestibule required by Article 3.3.5.7., provided the device is designed to release the door in conformance with Sentences (2) to (7).

(2)  Except as required by Sentences (3), (5), (6) and (7), a hold-open device permitted by Sentence (1) shall be designed to release by a signal from

(a)	an automatic sprinkler system,

(b)	a heat-actuated device,

(c)	fusible link, or

(d)	a smoke detector located as described in Appendix B of NFPA 80, “Standard for Fire Doors and Fire Windows”.

(3)  Except as required by Sentences (4), (5), (6) and (7), a hold-open device permitted by Sentence (1) shall be designed to release upon a signal from a smoke detector located as described in Appendix B of NFPA 80, “Standard for Fire Doors and Fire Windows”, if used on

(a)	an exit door,

(b)	a door opening into a public corridor,

(c)	an egress door referred to in Sentence 3.4.2.4.(2),

(d)	a door serving

(i)	an assembly occupancy,

(ii)	a care or detention occupancy, or

(iii)	a residential occupancy, or

(e)	a door required to function as part of a smoke control system.

(4)  Except as required by Sentences (5), (6) and (7), a hold-open device permitted by Sentence (1) shall be designed to release upon a signal from the building fire alarm system if a fire alarm system is provided, except that this requirement does not apply to

(a)	a hold-open device on a door located between a corridor used by the public and an adjacent sleeping room in a hospital or nursing home, or

(b)	a hold-open device that is designed to release by a heat-actuated device or a fusible link in conformance with Sentence (2).

(5)  Sentences (2) and (3) do not apply in a hospital or nursing home to

(a)	a door located between a corridor used by the public and an adjacent sleeping room, or

(b)	paired doors described in Sentence 3.3.3.3.(4).

(6)  A hold-open device on a door in Clause (5)(a) shall be designed to release the door upon a signal from

(a)	a smoke detector as required by Sentence 3.2.4.11.(1) for sleeping rooms in Group B occupancies, and

(b)	the fire alarm system when an alert signal is initiated within the same fire compartment in Sentence 3.3.3.5.(2).

(7)  A hold-open device on a door in Clause (5) (b) shall be designed to release the door upon a signal from the fire alarm system when an alert signal is initiated within the same fire compartment in Sentence 3.3.3.5.(2).

(8)  A rolling steel fire door installed as a closure in a fire separation shall be equipped with a hold-open device designed to release the shutter as described in Sentence (2).

3.1.8.13.  Door Latches

(1)  Except as permitted by Article 3.3.3.5., a swing-type door in a fire separation shall be equipped with a positive latching mechanism designed to hold the door in the closed position after each use.

3.1.8.14.  Wired Glass and Glass Block

(1)  Except as permitted by Articles 3.1.8.16. and 3.1.8.17. for the separation of exits, an opening in a fire separation having a fire-resistance rating not more than 1 h is permitted to be protected with fixed wired glass assemblies or glass blocks installed in conformance with NFPA 80, “Standard for Fire Doors and Fire Windows”.

(2)  Wired glass assemblies permitted by Sentence (1) and assigned a fire protection capability in the Supplementary Guidelines, are permitted to be used as closures in vertical fire separations without being tested in accordance with Sentence 3.1.8.4.(1).

(3)  Glass blocks permitted by Sentence (1) shall be installed in accordance with Subsection 4.3.2. and reinforced with steel reinforcement in each horizontal joint.

3.1.8.15.  Temperature Rise Limit for Doors

(1)  Except as permitted by Article 3.1.8.17., the maximum temperature rise on the opaque portion of the unexposed side of a door used as a closure in a fire separation in a location shown in Table 3.1.8.15., shall conform to the Table when tested in conformance with Sentence 3.1.8.4.(1).

3.1.8.16.  Area Limits for Wired Glass and Glass Block

(1)  Except as permitted by Article 3.1.8.17., the maximum area of wired glass in a door used in the locations shown in Table 3.1.8.15. shall conform to the Table.

(2)  Except as permitted by Article 3.1.8.17., the maximum area of glass block and wired glass panels not in a door, used in the locations shown in Table 3.1.8.15., shall conform to the Table.

Table 3.1.8.15.

Restrictions on Temperature Rise and Glazing for Closures

Forming Part Articles of 3.1.8.15. and 3.1.8.16.

| Location | Minimum Required Fire-Protection Rating of Door | Maximum Temperature Rise on Opaque Portion of Unexposed Side of Door, °C | Maximum Area of Wired Glass in Door, m2 | Maximum Aggregate Area of Glass Block and Wired Glass Panels not in Door, m2 |
| --- | --- | --- | --- | --- |
| Between a dead-end corridor and an adjacent occupancy where the corridor provides the only access to exit and is required to have a fire-resistance rating | Less than 45 min | No limit | No limit | No limit |
|  | 45 min | 250 after 30 min | 0.0645 | 0.0645 |
| Between an exit enclosure and the remainder of the floor area in buildings not more than 3 storeys in building height | All ratings | No limit | 0.8 | 0.8 |
| Between an exit enclosure and the remainder of the floor area (except as permitted above) | 45 min | 250 after 30 min | 0.0645 | 0.0645 |
|  | 1.5 h | 250 after 1 h | 0.0645 | 0.0645 |
|  | 2 h | 250 after 1 h | 0.0645 | 0.0645 |
| In a firewall | 1.5 h | 250 after 30 min | 0.0645 | 0 |
|  | 2 h | 250 after 1 h | 0 | 0 |
| Column 1 | 2 | 3 | 4 | 5 |

3.1.8.17.  Temperature Rise and Area Limits Waived

(1)  The temperature rise limits and glass area limits required by Articles 3.1.8.15. and 3.1.8.16. are waived for a closure between an exit enclosure and an enclosed vestibule or corridor provided

(a)	the vestibule or corridor is separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 45 min,

(b)	the fire separation required by Clause (a) contains no wired glass or glass block within 3 m of the closure into the exit enclosure, and

(c)	the vestibule or corridor contains no occupancy.

3.1.9. Building Services in Fire Separations and Fire Rated Assemblies

3.1.9.1.  Fire Stopping of Service Penetrations

(1)  Piping, tubing, ducts, chimneys, optical fibre cables, electrical wires and cables, totally enclosed noncombustible raceways, electrical outlet boxes and other similar building services that penetrate a membrane forming part of an assembly required to have a fire-resistance rating, or a fire separation, shall be

(a)	tightly fitted, or

(b)	sealed by a fire stop system that, when subjected to the fire test method in CAN4-S115-M, “Standard Method of Fire Tests of Firestop Systems”, has an F rating not less than the fire-protection rating required for closures in the fire separation.

(2)  Piping, tubing, ducts, chimneys, optical fibre cables, electrical wires and cables, totally enclosed noncombustible raceways, electrical outlet boxes and other similar building services that penetrate a firewall or a horizontal fire separation that is required to have a fire-resistance rating in conformance with Article 3.2.1.2., shall be sealed at the penetration by a fire stop system that, when subjected to the fire test method in CAN4-S115-M, “Standard Method of Fire Tests of Firestop Systems”, has an FT rating not less than the fire-resistance rating for the fire separation.

3.1.9.2.  Combustibility of Service Penetrations

(1)  Except as permitted by Articles 3.1.9.3. and 3.1.9.4., pipes, ducts, electrical outlet boxes, totally enclosed raceways or other similar service equipment that penetrate an assembly required to have a fire-resistance rating shall be noncombustible unless the assembly has been tested incorporating that service equipment.

3.1.9.3.  Penetration by Wires, Cables and Outlet Boxes

(1)  Optical fibre cables and electrical wires and cables in totally enclosed noncombustible raceways are permitted to penetrate an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2.

(2)  Except as permitted by Sentence (3), totally enclosed nonmetallic raceways conforming to Article 3.1.5.19., optical fibre cables, and electrical wires and cables, single or grouped, with combustible insulation, jackets or sheathes that conform to the requirements of Clause 3.1.5.17.(1)(a) and that are not installed in totally enclosed noncombustible raceways are permitted to penetrate an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the overall diameter of the single or grouped wires or cables, or the raceways is not more than 25 mm.

(3)  Single conductor metal sheathed cables with combustible jacketing that are more than 25 mm in overall diameter are permitted to penetrate a fire separation required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the cables are not grouped.

(4)  Combustible totally enclosed raceways which are embedded in a concrete floor slab are permitted in an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the concrete cover between the raceway and the bottom of the slab is not less than 50 mm.

(5)  Combustible outlet boxes are permitted in an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the opening through the membrane into the box is not more than 0.016 m2.

(6)  Outlet boxes that penetrate opposite sides of a wall assembly shall be offset where necessary to maintain the integrity of the fire separation.

3.1.9.4.  Combustible Piping Penetrations

(1)  Combustible sprinkler piping is permitted to penetrate a fire separation provided the fire compartments on each side of the fire separation are sprinklered.

(2)  Reserved

(3)  Except as permitted by Sentences (4) to (8), combustible piping shall not be used if any part of that system penetrates

(a)	a fire separation required to have a fire-resistance rating, or

(b)	a membrane that forms part of an assembly required to have a fire-resistance rating.

(4)  Combustible piping is permitted to penetrate a fire separation required to have a fire-resistance rating or a membrane that forms part of an assembly required to have a fire-resistance rating, provided

(a)	the piping is sealed at the penetration by a fire stop system that has an F rating not less than the fire-resistance rating required for the fire separation when subjected to the fire test method in CAN4-S115-M, “Standard Method of Fire Tests of Firestop Systems”, with a pressure differential of 50 Pa between the exposed and unexposed sides, with the higher pressure on the exposed side, and

(b)	the piping is not located in a vertical shaft.

(5)  Combustible drain piping is permitted to penetrate a horizontal fire separation provided it leads directly from a noncombustible water closet through a concrete floor slab.

(6)  Combustible piping is permitted on one side of a vertical fire separation provided it is not located in a vertical shaft.

(7)  Combustible piping is permitted to penetrate a vertical or horizontal fire separation provided the fire compartments on each side of the fire separation are sprinklered.

(8)  Combustible piping not more 25 mm in diameter containing chlorine gas is permitted to penetrate a fire separation between a chlorine gas service room, built in conjunction with a public pool or public spa, and the remainder of the building.

3.1.9.5.  Openings through a Membrane Ceiling

(1)  A membrane ceiling forming part of an assembly assigned a fire-resistance rating on the basis of the Supplementary Guidelines is permitted to be penetrated by openings leading into ducts within the ceiling space provided

(a)	the ducts are sheet steel, and

(b)	the amount of openings and their protection conform to the requirements of the Supplementary Guidelines.

(2)  Fire stop flaps in ceiling membranes required in Sentence (1) shall conform to CAN4-S112.2-M, “Standard Method of Fire Test of Ceiling Firestop Flap Assemblies”.

3.1.9.6.  Plenums

(1)  A ceiling assembly used as a plenum shall conform to Article 3.6.4.3.

3.1.10. Firewalls

3.1.10.1.  Prevention of Firewall Collapse

(1)  Except as permitted by Sentence (2), the connections and supports for structural framing members that are connected to or supported on a firewall and have a fire-resistance rating less than that required for the firewall, shall be designed so that the collapse of the framing members during a fire will not cause the collapse of the firewall.

(2)  Sentence (1) does not apply to a firewall consisting of two separate wall assemblies each tied to its respective building frame but not to each other, provided each wall assembly is

(a)	a fire separation having one half of the fire-resistance rating required for the firewall by Sentences 3.1.10.2.(1) and (2), and

(b)	designed so that the collapse of one wall assembly will not cause collapse of the other.

(3)  A firewall is permitted to be supported on the structural frame of a building of noncombustible construction provided the supporting frame has a fire-resistance rating not less than that required for the firewall.

(4)  Piping, ducts and totally enclosed noncombustible raceways shall be installed so that their collapse will not cause collapse of the firewall.

3.1.10.2.  Rating of Firewalls

(1)  A firewall which separates a building or buildings with floor areas containing a Group E or a Group F, Division 1 or 2 major occupancy shall be constructed as a fire separation of noncombustible construction having a fire-resistance rating not less than 4 h, except that where the upper portion of a firewall separates floor areas containing other than Group E or Group F, Division 1 or 2 major occupancies, the fire-resistance rating of the upper portion of the firewall is permitted to be not less than 2 h.

(2)  A firewall which separates a building or buildings with floor areas containing major occupancies other than Group E or Group F, Division 1 or 2 shall be constructed as a fire separation of noncombustible construction having a fire-resistance rating not less than 2 h.

(3)  Except for closures, the required fire-resistance rating of a firewall shall be provided by masonry or concrete.

3.1.10.3.  Continuity of Firewalls

(1)  A firewall shall extend from the ground continuously through, or adjacent to, all storeys of a building or buildings so separated, except that a firewall located above a basement storage garage conforming to Article 3.2.1.2. is permitted to commence at the floor assembly immediately above the storage garage.

(2)  A firewall is permitted to terminate on the underside of a reinforced concrete roof slab provided

(a)	the roof slab on both sides of the firewall has a fire-resistance rating not less than

(i)	1 h if the firewall is required to have a fire-resistance rating not less than 2 h, or

(ii)	2 h if the firewall is required to have a fire-resistance rating not less than 4 h, and

(b)	there are no concealed spaces within the roof slab in that portion immediately above the firewall.

3.1.10.4.  Parapets

(1)  Except as permitted by Sentences (2) and 3.1.10.3.(2), a firewall shall extend above the roof surface to form a parapet not less than

(a)	150 mm high for a firewall required to have a fire-resistance rating not less than 2 h, and

(b)	900 mm high for a firewall required to have a fire-resistance rating not less than 4 h.

(2)  A firewall that separates 2 buildings with roofs at different elevations need not extend above the upper roof surface to form a parapet, provided the difference in elevation between the roofs is more than 3 m.

3.1.10.5.  Maximum Openings

(1)  Openings in a firewall shall conform to the size limits described in Article 3.1.8.6. and the aggregate width of openings shall be not more than 25% of the entire length of the firewall.

3.1.10.6.  Exposure Protection for Adjacent Walls

(1)  The requirements of Article 3.2.3.13. shall apply to the external walls of 2 buildings that meet at a firewall at an angle less than 135°.

3.1.10.7.  Combustible Projections

(1)  Combustible material shall not extend across the end of a firewall but is permitted to extend across a roof above a firewall that is terminated in conformance with Sentence 3.1.10.3.(2).

(2)  If buildings are separated by a firewall, combustible projections on the exterior of one building, including balconies, platforms, canopies, eave projections and stairs, that extend outward beyond the end of the firewall, shall not be permitted within 2 400 mm of combustible projections and window or door openings of the adjacent building.

3.1.11. Fire Stops in Concealed Spaces

3.1.11.1.  Separation of Concealed Spaces

(1)  Concealed spaces in interior wall, ceiling and crawl spaces shall be separated from concealed spaces in exterior walls and attic or roof spaces by fire stops conforming to Article 3.1.11.7.

3.1.11.2.  Fire Stopping in Wall Assemblies

(1)  Except as permitted by Sentence (2), fire stops conforming to Article 3.1.11.7. shall be provided to block off concealed spaces within a wall assembly

(a)	at every floor level,

(b)	at every ceiling level where the ceiling forms part of an assembly required to have a fire-resistance rating, and

(c)	so that the maximum horizontal dimension is not more than 20 m and the maximum vertical dimension is not more than 3 m.

(2)  Fire stops conforming to Sentence (1) are not required provided

(a)	the wall space is filled with insulation,

(b)	the exposed construction materials and any insulation within the wall space are noncombustible,

(c)	the exposed construction materials and any insulation within the wall space have a flame-spread rating not more than 25 on any exposed surface, or on any surface that would be exposed by cutting through the material in any direction, and fire stops are installed so that the vertical distance between them is not more than 10 m, or

(d)	the insulated wall assembly contains not more than one concealed air space, and the horizontal thickness of that air space is not more than 25 mm.

3.1.11.3.  Fire Stopping between Nailing and Supporting Elements

(1)  In a building required to be of noncombustible construction, a concealed space in which there is an exposed ceiling finish with a flame-spread rating more than 25, shall be provided with fire stops conforming to Article 3.1.11.7. between wood nailing elements, so that the maximum area of the concealed space is not more than 2 m2.

(2)  In a building required to be of noncombustible construction, fire stops conforming to Article 3.1.11.7. shall be provided in the concealed spaces created by the wood members permitted by Sentence 3.1.5.8.(2) so that the maximum area of a concealed space is not more than 10 m2.

3.1.11.4.  Fire Stopping between Vertical and Horizontal Spaces

(1)  Fire stops conforming to Article 3.1.11.7. shall be provided

(a)	at all interconnections between concealed vertical and horizontal spaces in interior coved ceilings, drop ceilings and soffits in which the exposed construction materials within the space have a flame-spread rating more than 25, and

(b)	at the end of each run and at each floor level in concealed spaces between stair stringers in which the exposed construction materials within the space have a flame-spread rating more than 25.

3.1.11.5.  Fire Stopping of Roof Spaces, Balconies and Canopies

(1)  A concealed space within a ceiling or roof assembly of combustible construction, including an attic or roof space, in which sprinklers are not installed, shall be separated by construction conforming to Article 3.1.11.7. into compartments not more than

(a)	600 m2 in area with no dimension more than 60 m if the exposed construction materials within the space have a flame-spread rating not more than 25, and

(b)	300 m2 in area with no dimension more than 20 m if the exposed construction materials within the space have a flame-spread rating more than 25.

(2)  A concealed space in an exterior cornice, a mansard style roof, a balcony or a canopy in which exposed construction materials within the space have a flame-spread rating more than 25, shall be separated by construction conforming to Article 3.1.11.7.

(a)	at locations where the concealed space extends across the ends of required vertical fire separations, and

(b)	so that the maximum dimension in the concealed space is not more than 20 m.

3.1.11.6.  Fire Stopping of Crawl Spaces

(1)  A crawl space which is not considered as a basement by Article 3.2.2.9. and in which sprinklers are not installed, shall be separated by construction conforming to Article 3.1.11.7. into compartments not more than 600 m2 in area with no dimension more than 30 m.

3.1.11.7.  Fire Stop Materials

(1)  Except as permitted by Sentences (2) to (4), materials used to separate concealed spaces into compartments shall remain in place and prevent the passage of flames for not less than 15 min when subjected to the standard fire exposure in CAN/ULC-S101-M, “Standard Methods of Fire Endurance Tests of Building Construction and Materials”.

(2)  Gypsum board not less than 12.7 mm thick and sheet steel not less than 0.38 mm thick need not be tested in conformance with Sentence (1) provided all joints have continuous support.

(3)  In a building required to be of noncombustible construction, wood nailing elements described in Article 3.1.5.6. need not be tested in conformance with Sentence (1).

(4)  In a building permitted to be of combustible construction, in a combustible roof system permitted by Sentence 3.1.5.3.(2), and in a raised platform permitted by Sentence 3.1.5.8.(2), materials used to separate concealed spaces into compartments are permitted to be

(a)	solid lumber not less than 38 mm thick,

(b)	phenolic bonded plywood, waferboard, or strandboard not less than 12.5 mm thick with joints supported, or

(c)	two thicknesses of lumber, each not less than 19 mm thick with joints staggered, where the width or height of the concealed space requires more than one piece of lumber not less than 38 mm thick to block off the space.

(5)  Openings through materials referred to in Sentences (1) to (4) shall be protected to maintain the integrity of the construction.

(6)  Where materials referred to in Sentences (1) to (4) are penetrated by construction elements or by service equipment, fire stop materials shall be used to seal the penetration.

3.1.12. Flame-Spread Rating and Smoke Developed Classification

3.1.12.1.  Determination of Ratings

(1)  Except as required by Sentence (2) and as permitted by Sentence (3), the flame-spread rating and smoke developed classification of a material, assembly, or structural member shall be determined on the basis of not less than three tests conducted in conformance with CAN/ULC-S102-M, “Standard Method of Test for Surface Burning Characteristics of Building Materials and Assemblies”.

(2)  The flame-spread rating and smoke developed classification of a material or assembly shall be determined on the basis of not less than three tests conducted in conformance with CAN/ULC-S102.2-M, “Standard Method of Test for Surface Burning Characteristics of Flooring, Floor Covering, and Miscellaneous Materials and Assemblies”, if the material or assembly

(a)	is designed for use in a relatively horizontal position with only its top surface exposed to air,

(b)	cannot be tested in conformance with Sentence (1) without the use of supporting material that is not representative of the intended installation, or

(c)	is thermoplastic.

(3)  A material, assembly, or structural member is permitted to be assigned a flame-spread rating and smoke developed classification on the basis of the Supplementary Guidelines.

3.1.13. Interior Finish

3.1.13.1.  Interior Finish Description

(1)  Interior finish material shall include any material that forms part of the interior surface of a floor, wall, partition or ceiling, including

(a)	interior cladding of plaster, wood or tile,

(b)	surfacing of fabric, paint, plastic, veneer or wallpaper,

(c)	doors, windows and trim,

(d)	lighting elements such as light diffusers and lenses forming part of the finished surface of the ceiling, and

(e)	carpet material that overlies a floor that is not intended as the finished floor.

3.1.13.2.  Flame-Spread Rating

(1)  Except as otherwise required or permitted by this Subsection, the flame-spread rating of interior wall and ceiling finishes, including glazing and skylights, shall be not more than 150 and shall conform to Table 3.1.13.2.

Table 3.1.13.2.

Flame-Spread Ratings

Forming Part of Sentence 3.1.13.2.(1)

| Occupancy, Location or Element | Maximum Flame-Spread Rating for Walls and Ceilings |  |
| --- | --- | --- |
|  | Sprinklered | Not Sprinklered |
| Group A, Division 1 occupancies, including doors, skylights, glazing and light diffusers and lenses | 150 | 75 |
| Group B occupancies | 150 | NA |
| Exits(1) | 25 | 25 |
| Lobbies described in Sentence 3.4.4.2.(2) | 25 | 25 |
| Covered vehicular passageways, except for roof assemblies of heavy timber construction in such passageways | 25 | 25 |
| Vertical service spaces | 25 | 25 |
| Column 1 | 2 | 3 |

Note to Table 3.1.13.2.:

(1) See Articles 3.1.13.8. and 3.1.13.10.

(2)  Except as permitted by Sentence (3), doors, other than those in Group A, Division 1 occupancies, need not conform to Sentence (1) provided they have a flame-spread rating not more than 200.

(3)  Doors within a dwelling unit need not conform to Sentences (1) and (2).

(4)  Up to 10% of the total wall area and 10% of the total ceiling area of a wall or ceiling finish that is required by Sentence (1) to have a flame-spread rating less than 150 is permitted to have a flame-spread rating not more than 150, except that up to 25% of the total wall area of lobbies described in Sentence 3.4.4.2.(2) is permitted to have a flame-spread rating not more than 150.

(5)  Except in the case of Group A, Division 1 occupancies, combustible doors, skylights, glazing and light diffusers and lenses shall not be considered in the calculation of wall and ceiling areas described in Sentence (4).

3.1.13.3.  Bathrooms and Plumbing Fixtures

(1)  The flame-spread rating of interior wall and ceiling finishes for a bathroom in a suite of residential occupancy shall be not more than 200.

(2)  Plumbing fixtures shall have a flame-spread rating not more than 200.

3.1.13.4.  Light Diffusers and Lenses

(1)  The flame-spread rating of combustible light diffusers and lenses in all occupancies other than Group A, Division 1 is permitted to be more than the flame-spread rating limits required elsewhere in this Subsection, provided the light diffusers and lenses

(a)	have a flame-spread rating not more than 250 and a smoke developed classification not more than 600 when tested in conformance with CAN/ULC-S102.2-M, “Standard Method of Test for Surface Burning Characteristics of Flooring, Floor Covering, and Miscellaneous Materials and Assemblies”,

(b)	fall to the bottom of the test apparatus before igniting when tested in conformance with ULC-S102.3-M, “Standard Method of Fire Test of Light Diffusers and Lenses”,

(c)	are not prevented from falling from the ceiling by construction located beneath the elements, and

(d)	are not used in a corridor that is required to be separated from the remainder of the building by a fire separation or in an exit shaft unless individual diffusers or lenses are not more than 1 m2 in area and are not less than 1 200 mm apart.

3.1.13.5.  Skylights

(1)  Individual combustible skylights in a corridor that is required to be separated from the remainder of the building by a fire separation shall be not more than 1 m2 in area and not less than 1 200 mm apart.

3.1.13.6.  Corridors

(1)  Except as permitted by Sentences (2) and (3), the flame-spread rating shall be not more than 75 for the interior wall finish of

(a)	a public corridor,

(b)	a corridor used by the public in

(i)	an assembly occupancy, or

(ii)	a care or detention occupancy,

(c)	a corridor serving classrooms, or

(d)	a corridor serving sleeping rooms in a care or detention occupancy.

(2)  The flame-spread rating limit specified in Sentence (1) does not apply to corridors referred to in Sentence (1) provided the flame-spread rating is not more than

(a)	25 on the upper half of the wall, and

(b)	150 on the lower half of the wall.

(3)  The flame-spread rating limits specified in Sentences (1) and (2) for corridors referred to in Sentence (1) does not apply to a corridor in which the flame-spread rating is not more than 150 provided the floor area is sprinklered.

(4)  The flame-spread rating limits specified in Sentences (1), (2) and (3) apply to occupancies in the corridor as well as to the corridor itself.

(5)  Except in a floor area that is sprinklered and as permitted in Sentence (6), the interior ceiling finish of corridors and occupancies referred to in Sentences (1) and (4) shall have a flame-spread rating not more than 25.

(6)  The flame-spread rating limits specified in Sentence (5) do not apply to a corridor in which the flame-spread rating is not more than 150 provided the floor area is sprinklered.

3.1.13.7.  High Buildings

(1)  Except as permitted by Sentences (2) and (3), the interior wall, ceiling and floor finishes in a building regulated by the provisions of Subsection 3.2.6. shall conform to the flame-spread rating requirements in Articles 3.1.13.2. to 3.1.13.6. and to the flame-spread rating and smoke developed classification values in Table 3.1.13.7.

Table 3.1.13.7.

Flame-Spread Rating and Smoke Developed Classification in a High Building

Forming Part of Sentence 3.1.13.7.(1)

| Location or Element | Maximum Flame-Spread Rating |  |  | Maximum Smoke Developed Classification |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Wall Surface | Ceiling Surface(1) | Floor Surface | Wall Surface | Ceiling Surface(1) | Floor Surface |
| Exit stairways, vestibules to exit stairs and lobbies described in Sentence 3.4.4.2.(2) | 25 | 25 | 25 | 50 | 50 | 50 |
| Corridors not within suites | (2) | (2) | 300 | 100 | 50 | 500 |
| Elevator cars and vestibules | 25 | 25 | 300 | 100 | 100 | 300 |
| Service spaces and service rooms | 25 | 25 | 25 | 50 | 50 | 50 |
| Other locations and elements | (2) | (2) | No limit | 300 | 50 | No limit |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 |

Notes to Table 3.1.13.7:

(1) See Sentence 3.1.13.4.(1) for lighting elements.

(2) Other requirements of this Part apply.

(2)  Except for a building of Group B major occupancy and elevator cars, the flame-spread rating and smoke developed classification of interior wall, floor and ceiling finishes need not conform to the values in Table 3.1.13.7., provided the building is sprinklered and the sprinkler system is electrically supervised in conformance with Sentence 3.2.6.4.(1).

(3)  Trim, millwork and doors in an exit stairway, a vestibule to an exit stairway, a lobby described in Sentence 3.4.4.2.(2), or a corridor not within a suite need not conform to the flame-spread rating and smoke developed classification requirements of Sentence (1) provided they have

(a)	a flame-spread rating not more than 150,

(b)	a smoke developed classification not more than 300, and

(c)	an aggregate area not more than 10% of the area of the wall or ceiling on which they occur.

(4)  Except as permitted in Sentences (5) to (7), plumbing fixtures in a building regulated by the provisions of Subsection 3.2.6. shall have a smoke developed classification not more than 300.

(5)  A plumbing fixture that is not located in a Group B occupancy need not comply with Sentence (4) if the building is sprinklered.

(6)  A plumbing fixture may have a smoke developed classification more than 300 but not more than 500 if

(a)	it is in a room where the wall surfaces have a smoke developed classification not more than 200, and

(b)	it is located in,

(i)	a Group C occupancy, or

(ii)	a Group B occupancy and the building is sprinklered.

(7)  A therapeutic bathing system in a Group B occupancy need not comply with Sentence (4) if the room in which it is located,

(a)	does not open directly into patients’ or residents’ sleeping rooms, and

(b)	is sprinklered.

3.1.13.8.  Noncombustible Construction

(1)  In a building required to be of noncombustible construction

(a)	the flame-spread ratings required by Subsection 3.1.5. shall apply in addition to the requirements in this Subsection, and

(b)	the flame-spread ratings for exits in this Subsection shall also apply to any surface in the exit that would be exposed by cutting through the material in any direction, except that this requirement does not apply to doors, heavy timber construction in a sprinklered building and fire-retardant treated wood.

3.1.13.9.  Underground Walkways

(1)  Except for paint, the interior wall and ceiling finishes of an underground walkway shall be of noncombustible materials.

3.1.13.10.  Exterior Exit Passageway

(1)  The wall and ceiling finishes of an exterior exit passageway that provides the only means of egress from the rooms or suites it serves, including the soffit beneath and the guard on the passageway, shall have a flame-spread rating not more than 25, except that a flame-spread rating not more than 150 is permitted for up to 10% of the total wall area and for up to 10% of the total ceiling area.

3.1.14. Roof Assemblies

3.1.14.1.  Fire-Retardant Treated Wood Roof Systems

(1)  If a fire-retardant treated wood roof system is used to comply with the requirements of Subsection 3.2.2., the roof deck assembly shall meet the conditions of acceptance of CAN/ULC-S126-M, “Standard Method of Test for Fire Spread Under Roof-Deck Assemblies”.

(2)  Supports for the roof deck assembly referred to in Sentence (1) shall consist of

(a)	fire-retardant treated wood,

(b)	heavy timber construction,

(c)	noncombustible construction, or

(d)	a combination thereof.

3.1.14.2.  Metal Roof Deck Assemblies

(1)  Except as permitted by Sentence (2), a metal roof deck assembly shall meet the conditions of acceptance of CAN/ULC-S126-M, “Standard Method of Test for Fire Spread Under Roof-Deck Assemblies”, if

(a)	it supports a combustible material above the deck that could propagate a fire beneath the roof deck assembly, and

(b)	the deck is used to comply with the requirements of Sentences 3.2.2.25.(2), 3.2.2.32.(2), 3.2.2.53.(2), 3.2.2.59.(2), 3.2.2.69.(2) and 3.2.2.76.(2) for noncombustible construction.

(2)  The requirements of Sentence (1) are waived provided

(a)	the combustible material above the roof deck is protected by not less than 12.7 mm thick gypsum board, mechanically fastened to a supporting assembly if located beneath the roof deck, or by a thermal barrier conforming to one of Clauses 3.1.5.11.(2)(c) to (e) that is located

(i)	on the underside of the combustible material, or

(ii)	beneath the roof deck,

(b)	the building is sprinklered, or

(c)	the roof assembly has a fire-resistance rating not less than 45 min.

3.1.15. Roof Covering

3.1.15.1.  Roof Covering Classification

(1)  A roof covering classification shall be determined in conformance with CAN/ULC-S107-M, “Standard Methods of Fire Tests of Roof Coverings”.

3.1.15.2.  Roof Coverings

(1)  Except as permitted by Sentence (2), every roof covering shall have a Class A, B or C classification as determined in accordance with Article 3.1.15.1.

(2)  A roof covering is not required to have a Class A, B or C classification for

(a)	a tent,

(b)	an air-supported structure, or

(c)	a building of Group A, Division 2 occupancy not more than 2 storeys in building height and not more than 1 000 m2 in building area provided the roof covering is underlaid with noncombustible material.

3.1.16. Occupant Load

3.1.16.1.  Occupant Load Determination

(1)  The occupant load of a floor area or part of a floor area, or of a building or part of a building not having a floor area, shall be based on

(a)	the number of seats in an assembly occupancy having fixed seats,

(b)	2 persons per sleeping room or sleeping area in a dwelling unit or suite, or

(c)	the number of persons

(i)	for which the area is designed, or

(ii)	determined from Table 3.1.16.1. for occupancies other than those described in Clauses (a) and (b).

Table 3.1.16.1.

Occupant Load

Forming Part of Article 3.1.16.1.

| Type of Use of Building or Floor Area or Part Thereof | Area per Person, m2 |
| --- | --- |
| Assembly uses |  |
| space with fixed seats | See Clause (1)(a) |
| space with nonfixed seats | 0.75 |
| stages for theatrical performances | 0.75 |
| space with nonfixed seats and tables | 0.95 |
| standing space | 0.40 |
| stadia and grandstands | 0.60 |
| bowling alleys, pool and billiard rooms | 9.30 |
| classrooms | 1.85 |
| school shops and vocational rooms | 9.30 |
| reading or writing rooms or lounges | 1.85 |
| dining, alcoholic beverage and cafeteria space | 1.10 |
| laboratories in schools | 4.60 |
| exhibition halls other than those classified in Group E | 2.80 |
| Care or detention uses |  |
| B-1 : detention quarters | 11.60 |
| B-2 : treatment and sleeping room areas | 10.00 |
| B-3 : sleeping room areas | 10.00 |
| (See also Article 3.7.1.3.) |  |
| Residential uses |  |
| dwelling units | See Clause (1)(b) |
| dormitories | 4.60 |
| Business and personal services uses |  |
| personal service shops | 4.60 |
| offices | 9.30 |
| Mercantile uses |  |
| basements and first storeys | 3.70 |
| second storeys having a principal entrance from a pedestrian thoroughfare or a parking area | 3.70 |
| dining, alcoholic beverage and cafeteria space | 1.10 |
| other storeys | 5.60 |
| Industrial uses |  |
| manufacturing or process rooms | 4.60 |
| storage garages | 46.00 |
| storage spaces (warehouse) | 28.00 |
| aircraft hangars | 46.00 |
| Other uses |  |
| cleaning and repair of goods | 4.60 |
| kitchens | 9.30 |
| storage | 46.00 |
| public corridors intended for occupancies in addition to pedestrian travel | 3.70 |
| Column 1 | 2 |

(2)  If a floor area or part thereof has been designed for an occupant load other than that determined from Table 3.1.16.1., a permanent sign indicating that occupant load shall be posted in a conspicuous location.

(3)  For the purposes of this Article, mezzanines, tiers and balconies shall be regarded as part of the floor area.

(4)  If a room or group of rooms is intended for different occupancies at different times, the value to be used from Table 3.1.16.1. shall be the value which gives the greatest number of persons for the occupancies concerned.

(5)  Except as provided by Sentences (6) or (7), in dining, alcoholic beverage and cafeteria spaces the occupant load shall be determined from Table 3.1.16.1.

(6)  The occupant load in Sentence (5) is permitted to be the number of persons for which the space is designed.

(7)  The occupant load in Sentence (6) shall be not more than that determined by using an area of 0.6 m2 per person.

3.1.16.2.  Dance Floor

(1)  The occupant load of a room in which a dance floor is situated shall be calculated in respect of that portion of the room that is not occupied by the dance floor.

3.1.16.3.  Public Pools

(1)  The occupant load of a public pool, except a wave action pool, shall be determined by the following formula:

occupant load=D2.5 + S1.4

where D = the water surface area in square metres of the part of the pool that is deeper than 1 350 mm; and

where S = the water surface area in square metres of the part of the pool that is 1 350 mm in depth or less.

(2)  The occupant load of a wave action pool shall be determined by the following formula:

occupant load=D2.5 + S1.1

where D = the water surface area in square metres of the part of the pool where the still water depth is greater than 1 000 mm; and

where S = the water surface area in square metres of the part of the pool where the still water depth is 1 000 mm or less.

3.1.17. Drainage and Grades

3.1.17.1.  Drainage

(1)  The building shall be located and the building site graded so that water will not accumulate at or near the building and will not adversely affect any adjacent properties.

3.1.18. Above Ground Electrical Conductors

3.1.18.1.  Clearance to Buildings

(1)  Where a building is to be constructed in proximity to existing above ground electrical conductors of a voltage not less than 2.5 kV and not more than 46 kV

(a)	the building shall not be located beneath the conductors, and

(b)	the horizontal distance between the building and the conductors shall be not less than 3 m.

(2)  Where a building is to be constructed in proximity to existing above ground electrical conductors of a voltage more than 46 kV, the clearances between the building and the conductors shall conform to the requirements of CAN/CSA-C22.3 No.1, “Overhead Systems”.

3.1.18.2.  Exception

(1)  Article 3.1.18.1. does not apply to buildings containing electrical equipment and electrical installations used exclusively in the generation, transformation or transmission of electrical power or energy intended for sale or distribution to the public.

Section 3.2. Building Fire Safety

3.2.1. General

3.2.1.1.  Exceptions in Determining Building Height

(1)  A roof-top enclosure provided for elevator machinery, a stairway or a service room used for no purpose other than for service to the building, shall not be considered as a storey in calculating the building height.

(2)  Space under tiers of seats in a building of the arena type shall not be considered as adding to the building height provided the space is used only for dressing rooms, concession stands and similar purposes incidental to the major occupancy of the building.

(3)  Except as required in Sentence (4), (5) and (8), a mezzanine shall not be considered as a storey in calculating the building height provided

(a)	the aggregate area of the mezzanine floor is not more than 40% of the area of the room or storey in which it is located,

(b)	it is used as an open floor area except as permitted by Sentence 3.3.2.11.(2), and

(c)	the space above the mezzanine floor has no visual obstructions more than 1 070 mm above the floor.

(4)  Except as required by Sentence (5), a mezzanine shall not be considered as a storey in calculating building height and need not conform to Sentence (3) provided the aggregate area of the mezzanine floor is not more than 10% of the area of

(a)	the suite in which it is located, where there is more than one suite in the storey, or

(b)	the storey in which it is located, in all other cases.

(5)  Except a permitted by Sentence (8), if one or more levels of mezzanine is partially or wholly superimposed above another mezzanine in the room or storey, each level additional to the first level shall be considered as a storey in calculating the building height.

(6)  The floor assembly of a mezzanine that is required to be considered as a storey in determining building height, shall be constructed in conformance with the fire separation requirements of Articles 3.2.2.20. to 3.2.2.83. for floor assemblies.

(7)  A service space in which facilities are included to permit a person to enter and to undertake maintenance and other operations pertaining to building services from within the service space need not be considered a storey if it conforms to Articles 3.2.5.15. and 3.3.1.23., and Sentences 3.2.4.19.(12), 3.2.7.3.(2), 3.3.1.3.(7), 3.4.2.4.(3) and 3.4.4.4.(9).

(8)  Mezzanines, elevated walkways and platforms in Group F, Division 2 or 3 major occupancies need not be considered as storeys in calculating building height provided

(a)	the building is of noncombustible construction,

(b)	except for Clause (c), the mezzanines, elevated walkways and platforms are intended solely for periodic service and maintenance, and

(c)	where they are intended to be occupied, no mezzanine, elevated walkway or platform shall have an occupant load more than 4 persons.

3.2.1.2.  Storage Garage Considered as a Separate Building

(1)  A basement used primarily as a storage garage is permitted to be considered as a separate building for the purposes of Subsection 3.2.2., provided the floor and roof assemblies above the basement and the exterior walls of the basement above the adjoining ground level are constructed as fire separations of masonry or concrete having a fire-resistance rating not less than 2 h, except as permitted by Sentence (2).

(2)  The exterior wall of a basement that is required to be a fire separation with a fire-resistance rating in accordance with Sentence (1) is permitted to be penetrated by openings that are not protected by closures provided

(a)	the storage garage is sprinklered,

(b)	every opening in the exterior wall is separated from storeys above the opening by a projection of the floor or roof assembly above the basement, extending not less than

(i)	1 000 mm beyond the exterior face of the storage garage if the upper storeys are required to be of noncombustible construction, or

(ii)	2 000 mm beyond the exterior face of the storage garage if the upper storeys are permitted to be of combustible construction, or

(c)	the exterior walls of any storeys located above the floor or roof assembly referred to in Sentence (1) are recessed behind the outer edge of the assembly by not less than

(i)	1 000 mm if the upper storeys are required to be of noncombustible construction, or

(ii)	2 000 mm if the upper storeys are permitted to be of combustible construction.

(3)  The floor or roof assembly projection referred to in Clause (2)(b) shall have a fire-resistance rating not less than 2 h and shall have no openings within the projection.

3.2.1.3.  Roof Considered as a Wall

(1)  For the purposes of this Section any part of a roof that is pitched at an angle of 60° or more to the horizontal and is adjacent to a space intended for occupancy within a building shall be considered as part of an exterior wall of the building.

3.2.1.4.  Floor Assembly over Basement

(1)  Except as permitted by Sentences 3.2.2.42.(3), 3.2.2.43.(3), 3.2.2.45.(3), 3.2.2.46.(3), 3.2.2.47.(3) or 3.2.2.48.(3), a floor assembly immediately above a basement shall be constructed as a fire separation having a fire-resistance rating conforming to the requirements of Articles 3.2.2.20. to 3.2.2.83. for a floor assembly, but not less than 45 min.

(2)  All loadbearing walls, columns and arches supporting a floor assembly immediately above a basement shall have a fire-resistance rating not less than that required by Sentence (1) for the floor assembly.

3.2.1.5.  Fire Containment in Basements

(1)  Except as permitted by Sentences (2) and 3.2.2.15.(3), in a building in which an automatic sprinkler system is not required to be installed by Articles 3.2.2.20. to 3.2.2.83., every basement shall

(a)	be sprinklered, or

(b)	be subdivided into fire compartments not more than 600 m2 in area by a fire separation having a fire-resistance rating not less than that required for the floor assembly immediately above the basement.

(2)  An open-air storey need not conform to Sentence (1).

3.2.2. Building Size and Construction Relative to Occupancy

3.2.2.1.  Application

(1)  Except as permitted by Article 3.2.2.3., a building shall be constructed in conformance with this Subsection to prevent fire spread and collapse caused by the effects of fire.

3.2.2.2.  Special and Unusual Structures

(1)  A structure which cannot be identified with the characteristics of a building in Articles 3.2.2.20. to 3.2.2.83. shall be protected against fire spread and collapse in conformance with good fire protection engineering practice.

3.2.2.3.  Exceptions to Structural Fire Protection

(1)  Fire protection is not required for

(a)	steel lintels above openings not more than 2 m wide in loadbearing walls and not more than 3 m wide in non-loadbearing walls,

(b)	steel lintels above openings more than 2 m wide in loadbearing walls and more than 3 m wide in non-loadbearing walls provided the lintels are supported at intervals of not more than 2 m by structural members with the required fire-resistance rating,

(c)	the bottom flanges of shelf angles and plates that are not a part of the structural frame,

(d)	steel members for framework around elevator hoistway doorways, steel for the support of elevator and dumbwaiter guides, counterweights and other similar equipment, that are entirely enclosed in a hoistway and are not a part of the structural frame of the building,

(e)	steel members of stairways and escalators that are not a part of the structural frame of a building,

(f)	steel members of porches, exterior balconies, exterior stairways, fire escapes, cornices, marquees and other similar appurtenances, provided they are outside an exterior wall of a building, and

(g)	loadbearing steel or concrete members wholly or partly outside a building face in a building not more than 4 storeys in building height and classified as Group A, B, C, D or F, Division 3 major occupancy provided the members are

(i)	not less than 1 000 mm away from any unprotected opening in an exterior wall, or

(ii)	shielded from heat radiation in the event of a fire within the building by construction that will provide the same degree of protection that would be necessary if the member was located inside the building, with the protection extending on either side of the member a distance equal to the projection of the member from the face of the wall.

3.2.2.4.  Buildings with Multiple Major Occupancies

(1)  The requirements restricting fire spread and collapse for a building of a single major occupancy classification are provided in this Subsection according to its building height and building area.

(2)  If a building contains more than one major occupancy, classified in more than one Group or Division, the requirements of this Subsection concerning building size and construction relative to major occupancy shall apply according to Articles 3.2.2.5. to 3.2.2.8.

3.2.2.5.  Applicable Building Height and Area

(1)  In determining the fire safety requirements of a building in relation to each of the major occupancies contained therein, the building height and building area of the entire building shall be used.

3.2.2.6.  Multiple Major Occupancies

(1)  Except as permitted by Articles 3.2.2.7. and 3.2.2.8., in a building containing more than one major occupancy, the requirements of this Subsection for the most restricted major occupancy contained shall apply to the whole building.

3.2.2.7.  Superimposed Major Occupancies

(1)  Except as permitted by Article 3.2.2.8., in a building in which one major occupancy is located entirely above another major occupancy, the requirements in this Subsection for each portion of the building containing a major occupancy shall apply to that portion as if the entire building was of that major occupancy.

(2)  If one major occupancy is located above another major occupancy, the fire-resistance rating of the floor assembly between the major occupancies shall be determined on the basis of the requirements of this Subsection for the lower major occupancy.

3.2.2.8.  Exceptions for Major Occupancies

(1)  In a building in which the aggregate area of all major occupancies in a particular Group or Division is not more than 10% of the floor area of the storey in which they are located, these major occupancies need not be considered as major occupancies for the purposes of this Subsection, provided they are not classified as Group F, Division 1 or 2 occupancies.

(2)  A helicopter landing area on the roof of a building need not be considered a major occupancy for purposes of Subsection 3.2.2. where such landing area is not more than 10% of the area of the roof.

3.2.2.9.  Crawl Spaces

(1)  For the purposes of Articles 3.2.1.4. and 3.2.1.5., a crawl space shall be considered as a basement if it is

(a)	more than 1 800 mm high between the lowest part of the floor assembly and the ground or other surface below,

(b)	used for any occupancy,

(c)	used for the passage of flue pipes, or

(d)	used as a plenum in combustible construction.

(2)  A floor assembly immediately above a crawl space is not required to be constructed as a fire separation and is not required to have a fire-resistance rating provided the crawl space is not required to be considered as a basement by Sentence (1).

3.2.2.10.  Streets

(1)  Every building shall face a street located in conformance with the requirements of Articles 3.2.5.5. and 3.2.5.6. for access routes.

(2)  For the purposes of Subsections 3.2.2. and 3.2.5. an access route conforming to Subsection 3.2.5. is permitted to be considered as a street.

(3)  A building is considered to face 2 streets provided not less than 50% of the building perimeter is located within 15 m of the street or streets.

(4)  A building is considered to face 3 streets provided not less than 75% of the building perimeter is located within 15 m of the street or streets.

(5)  Enclosed spaces, tunnels, bridges and similar structures, even though used for vehicular or pedestrian traffic, are not considered as streets for the purpose of this Part.

3.2.2.11.  Exterior Balconies

(1)  An exterior balcony shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.83., as applicable to the occupancy classification of the building.

3.2.2.12.  Exterior Passageways

(1)  An elevated exterior passageway used as part of a means of egress shall conform to the requirements of Articles 3.2.2.20. to 3.2.2.83. for mezzanines.

3.2.2.13.  Occupancy on Roof

(1)  A portion of a roof that supports an occupancy shall be constructed in conformance with the fire separation requirements of Articles 3.2.2.20. to 3.2.2.83. for floor assemblies.

3.2.2.14.  Roof-Top Enclosures

(1)  A roof-top enclosure for elevator machinery or for a service room shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.83.

(2)  A roof-top enclosure for elevator machinery or for a service room, not more than one storey high, is not required to have a fire-resistance rating.

(3)  A roof-top enclosure for a stairway shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.83.

(4)  A roof-top enclosure for a stairway need not have a fire-resistance rating nor be constructed as a fire separation.

3.2.2.15.  Storeys below Ground

(1)  If a building is erected entirely below the adjoining finished ground level and does not extend more than one storey below that ground level, the minimum precautions against fire spread and collapse shall be the same as are required for basements under a building of 1 storey in building height having the same occupancy and building area.

(2)  If any portion of a building is erected entirely below the adjoining finished ground level and extends more than one storey below that ground level, the following minimum precautions against fire spread and collapse shall be taken:

(a)	except as permitted by Sentence (3), the basements shall be sprinklered,

(b)	a floor assembly below the ground level shall be constructed as a fire separation with a fire-resistance rating not less than

(i)	3 h if the basements are intended for use as Group E or Group F, Division 1 or 2 occupancies, or

(ii)	2 h if the basements are not intended for use as Group E or Group F, Division 1 or 2 occupancies, and

(c)	all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the construction that they support.

(3)  If the first storey of a building is not required to be sprinklered, sprinklers are not required in the storey immediately below the first storey provided the storey below

(a)	contains only residential occupancies, and

(b)	has at least one unobstructed access opening conforming to Sentence 3.2.5.1.(2) installed on that storey for each 15 m of wall length in at least one wall required by this Subsection to face a street.

3.2.2.16.  Heavy Timber Roof Permitted

(1)  Unless otherwise permitted by Articles 3.2.2.20. to 3.2.2.83., a roof assembly in a building up to 2 storeys in building height is permitted to be of heavy timber construction regardless of building area or type of construction required, provided the building is sprinklered.

(2)  If Sentence (1) permits a roof assembly to be of heavy timber construction, structural members in the storey immediately below the roof assembly are permitted to be of heavy timber construction.

3.2.2.17.  Sprinklers in Lieu of Roof Rating

(1)  The requirements in Articles 3.2.2.20. to 3.2.2.83. for roof assemblies to have a fire-resistance rating are permitted to be waived provided

(a)	the building is sprinklered,

(b)	the sprinkler system in Clause (a) is electrically supervised in conformance with Sentence 3.2.4.9.(2), and

(c)	the operation of the sprinkler system in Clause (a) will cause a signal to be transmitted to the fire department in conformance with Sentence 3.2.4.7.(4).

3.2.2.18.  Automatic Sprinkler System Required

(1)  If an automatic sprinkler system is required by Articles 3.2.2.20. to 3.2.2.83., the system shall conform to the requirements of Articles 3.2.4.7., 3.2.4.8., 3.2.4.9. 3.2.5.13.

3.2.2.19.  Buildings Containing Impeded Egress Zones

(1)  A building containing an impeded egress zone and conforming to the appropriate requirements of Articles 3.2.2.20. to 3.2.2.83. is not required to conform to the requirements of Articles 3.2.2.36. and 3.2.2.37. for a Group B, Division 1 major occupancy provided

(a)	the building is sprinklered,

(b)	it is not more than 1 storey in building height,

(c)	it does not include

(i)	a contained use area,

(ii)	sleeping accommodation,

(iii)	a high hazard industrial occupancy, or

(iv)	a mercantile occupancy,

(d)	the building area is not more than 6 400 m2 if the building includes a medium hazard industrial occupancy,

(e)	the impeded egress zone does not extend beyond the boundaries of the fire compartment in which it is located, and

(f)	the occupant load of the impeded egress zone is not more than 100.

3.2.2.20.  Group A, Division 1, Any Height, Any Area, Sprinklered

(1)  Except as permitted by Articles 3.2.2.21. and 3.2.2.22., a building classified as Group A, Division 1 shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.21.  Group A, Division 1, One Storey, Limited Area

(1)  A building classified as Group A, Division 1 is permitted to conform to Sentence (2) provided

(a)	it is not more than 1 storey in building height,

(b)	it has less than 40% of the area of the building as 2 storeys for the purpose of

(i)	development of productions including preparation of scenery and costumes and rehearsal of performers,

(ii)	organization of performers, scenery and sound equipment,

(iii)	preparation by performers for a performance,

(iv)	managerial functions, or

(v)	toilets, rest rooms and similar public facilities,

(c)	it has no occupancy above or below the auditorium other than one which serves it or is dependent on it,

(d)	it is not more than 600 m2 in building area, and

(e)	the occupant load is not more than 600.

(2)  The building referred to in Sentence (1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations,

(i)	with a fire-resistance rating not less than 45 min, or

(ii)	of heavy timber construction, and

(b)	loadbearing walls, columns and arches shall

(i)	have a fire-resistance rating not less than that required for the supported assembly, or

(ii)	be of heavy timber construction.

3.2.2.22.  Group A, Division 1, One Storey

(1)  A building classified as Group A, Division 1 is permitted to conform to Sentence (2) provided

(a)	it is not more than 1 storey in building height,

(b)	no part of an auditorium floor is more than 5 m above or below grade,

(c)	no occupancy is above or below the auditorium other than one which serves it or is dependent on it, and

(d)	the occupant load of the auditorium floor is not more than 300.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(c)	roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

(d)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction, and

(e)	loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation.

3.2.2.23.  Group A, Division 2, Any Height, Any Area, Sprinklered

(1)  Except as permitted by Articles 3.2.2.24. to 3.2.2.28., a building classified as Group A, Division 2 shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.24.  Group A, Division 2, up to 6 Storeys, Any Area, Sprinklered

(1)  A building classified as Group A, Division 2, that is not limited by building area, is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, and

(b)	it is not more than 6 storeys in building height.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.25.  Group A, Division 2, up to 2 Storeys

(1)  A building classified as Group A, Division 2 is permitted to conform to Sentence (2) provided

(a)	it is not more than 2 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.25.

Table 3.2.2.25.

Maximum Building Area, Group A, Division 2, up to 2 Storeys

Forming Part of Sentence 3.2.2.25.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 600 | 2 000 | 2 400 |
| 2 | 800 | 1 000 | 1 200 |
| Column 1 | 2 | 3 | 4 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less 45 min,

(c)	roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than

(i)	800 m2 if facing one street,

(ii)	1 000 m2 if facing 2 streets, or

(iii)	1 200 m2 if facing 3 streets, and

(d)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.26.  Group A, Division 2, up to 2 Storeys, Increased Area, Sprinklered

(1)  A building classified as Group A, Division 2 is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than

(i)	4 800 m2 if 1 storey in building height, or

(ii)	2 400 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less 45 min, and

(c)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.27.  Group A, Division 2, up to 2 Storeys, Sprinklered

(1)  A building classified as Group A, Division 2 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than

(i)	2 400 m2 if 1 storey in building height with no basement,

(ii)	1 200 m2 if 1 storey in building height, or

(iii)	600 m2 if 2 storeys in building height.

3.2.2.28.  Group A, Division 2, One Storey

(1)  A building classified as Group A, Division 2 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided

(a)	it is not more than 1 storey in building height, and

(b)	except as permitted by Sentence (2), it has a building area not more than

(i)	400 m2 if facing one street,

(ii)	500 m2 if facing 2 streets, or

(iii)	600 m2 if facing 3 streets.

(2)  In a building referred to in Sentence (1) without a basement, the building area limits of Sentence (1) are permitted to be doubled provided a fire separation with a fire-resistance rating not less than 1 h is used to separate the building into fire compartments, each one of which does not exceed the area limits of Clause 1(b).

3.2.2.29.  Group A, Division 3, Any Height, Any Area

(1)  Except as permitted by Articles 3.2.2.30. to 3.2.2.34., a building classified as Group A, Division 3 shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered if it is regulated by Subsection 3.2.6.,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less than 1 h,

(d)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and

(e)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.30.  Group A, Division 3, up to 2 Storeys

(1)  A building classified as Group A, Division 3 is permitted to conform to Sentence (2) provided

(a)	it is not more than 2 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.30.

Table 3.2.2.30.

Maximum Building Area, Group A, Division 3, up to 2 Storeys

Forming Part of Sentence 3.2.2.30.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 4 000 | 5 000 | 6 000 |
| 2 | 2 000 | 2 500 | 3 000 |
| Column 1 | 2 | 3 | 4 |

(2)  Except as permitted by Clauses (c) and (d), the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	roof assemblies shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of heavy timber construction, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly, except that arches and structural members within the storey immediately below a roof assembly are permitted to be of heavy timber construction.

3.2.2.31.  Group A, Division 3, up to 2 Storeys, Sprinklered

(1)  A building classified as Group A, Division 3 is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than

(i)	12 000 m2 if 1 storey in building height, or

(ii)	6 000 m2 if 2 storeys in building height.

(2)  Except as permitted by Clause (c) and Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly, except that arches are permitted to be of heavy timber construction.

3.2.2.32.  Group A, Division 3, One Storey, Increased Area

(1)  A building classified as Group A, Division 3 is permitted to conform to Sentence (2) provided

(a)	it is not more than 1 storey in building height, and

(b)	it has a building area not more than

(i)	2 400 m2 if facing one street,

(ii)	3 000 m2 if facing 2 streets, or

(iii)	3 600 m2 if facing 3 streets.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(b)	roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than

(i)	1 200 m2 if facing one street,

(ii)	1 500 m2 if facing 2 streets, or

(iii)	1 800 m2 if facing 3 streets, and

(c)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.33.  Group A, Division 3, One Storey, Sprinklered

(1)  A building classified as Group A, Division 3 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 1 storey in building height, and

(c)	it has a building area not more than 7 200 m2.

3.2.2.34.  Group A, Division 3, One Storey

(1)  A building classified as Group A, Division 3 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided

(a)	it is not more than 1 storey in building height, and

(b)	it has a building area not more than

(i)	1 000 m2 if facing one street,

(ii)	1 250 m2 if facing 2 streets, or

(iii)	1 500 m2 if facing 3 streets.

3.2.2.35.  Group A, Division 4

(1)  Except as permitted by Sentences (2) and (3), a building classified as Group A, Division 4 shall be of noncombustible construction.

(2)  Roof assemblies and supporting arches and columns are permitted to be of heavy timber construction.

(3)  A building classified as Group A, Division 4 is permitted to be of combustible construction provided

(a)	the occupant load is less than 1 500, and

(b)	the building has a limiting distance not less than 6 m.

(4)  Sprinklers shall be installed in all spaces below tiers of seats in a building classified as Group A, Division 4 if those spaces are used for occupancy.

3.2.2.36.  Group B, Division 1, Any Height, Any Area, Sprinklered

(1)  Except as permitted by Article 3.2.2.37., a building classified as Group B, Division 1 shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.37.  Group B, Division 1, up to 3 Storeys, Sprinklered

(1)  A building classified as Group B, Division 1 is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1) the building is sprinklered,

(b)	it is not more than 3 storeys in building height, and

(c)	it has a building area

(i)	that is not limited if the building is not more than 1 storey in building height,

(ii)	not more than 12 000 m2 if 2 storeys in building height, or

(iii)	not more than 8 000 m2 if 3 storeys in building height.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.38.  Group B, Division 2 or Division 3, Any Height, Any Area, Sprinklered

(1)  Except as permitted by Articles 3.2.2.39. to 3.2.2.41., a building classified as Group B, Division 2 or Division 3 shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.39.  Group B, Division 2 or Division 3, up to 3 Storeys, Sprinklered

(1)  A building classified as Group B, Division 2 or Division 3 is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 3 storeys in building height, and

(c)	it has a building area

(i)	that is not limited if the building is not more than 1 storey in building height,

(ii)	not more than 12 000 m2 if 2 storeys in building height, or

(iii)	not more than 8 000 m2 if 3 storeys in building height.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.40.  Group B, Division 2 or Division 3, up to 2 Storeys, Sprinklered

(1)  A building classified as Group B, Division 2 or Division 3 is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than

(i)	2 400 m2 if 1 storey in building height, or

(ii)	1 600 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.41.  Group B, Division 2 or Division 3, One Storey, Sprinklered

(1)  A building classified as Group B, Division 2 or Division 3 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 1 storey in building height, and

(c)	it has a building area not more than 500 m2.

3.2.2.42.  Group C, Any Height, Any Area

(1)  Except as permitted by Articles 3.2.2.43. to 3.2.2.48., a building classified as Group C shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	Reserved

(b)	except as permitted by Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h,

(d)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and

(e)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(3)  In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(2), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

3.2.2.43.  Group C, up to 6 Storeys

(1)  A building classified as Group C is permitted to conform to Sentence (2) provided

(a)	it is not more than 6 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.43.A. or Table 3.2.2.43.B.

Table 3.2.2.43.A.

Maximum Building Area, Group C, up to 6 Storeys

Forming Part of Sentence 3.2.2.43.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | unlimited | unlimited | unlimited |
| 2 | 6 000 | unlimited | unlimited |
| 3 | 4 000 | 5 000 | 6 000 |
| 4 | 3 000 | 3 750 | 4 500 |
| 5 | 2 400 | 3 000 | 3 600 |
| 6 | 2 000 | 2 500 | 3 000 |
| Column 1 | 2 | 3 | 4 |

Table 3.2.2.43.B.

Maximum Building Area, Group C, up to 6 Storeys, Sprinklered

Forming Part of Sentence 3.2.2.43.(1)

| No. of Storeys | Maximum Area, m2 |
| --- | --- |
| 1 | Unlimited |
| 2 | Unlimited |
| 3 | 12 000 |
| 4 | 9 000 |
| 5 | 7 200 |
| 6 | 6 000 |
| Column 1 | 2 |

(2)  The building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	except as permitted by Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating of not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating of not less than 1 h,

(c)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(3)  In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

3.2.2.44.  Reserved

3.2.2.45.  Group C, up to 4 Storeys, Sprinklered

(1)  A building classified as Group C is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 4 storeys in building height, and

(c)	it has a building area not more than

(i)	7 200 m2 if 1 storey in building height,

(ii)	3 600 m2 if 2 storeys in building height,

(iii)	2 400 m2 if 3 storeys in building height, or

(iv)	1 800 m2 if 4 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(3)  In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(2), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

(4)  In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived.

3.2.2.46.  Group C, up to 3 Storeys, Increased Area

(1)  A building classified as Group C is permitted to conform to Sentence (2) provided

(a)	it is not more than 3 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.46.

Table 3.2.2.46.

Maximum Building Area, Group C, up to 3 Storeys, Increased Area

Forming Part of Sentence 3.2.2.46.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 2 400 | 3 000 | 3 600 |
| 2 | 1 200 | 1 500 | 1 800 |
| 3 | 800 | 1 000 | 1 200 |
| Column 1 | 2 | 3 | 4 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(3)  In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(2), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

(4)  In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived.

3.2.2.47.  Group C, up to 3 Storeys

(1)  A building classified as Group C is permitted to conform to Sentence (2) provided

(a)	it is not more than 3 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.47.

Table 3.2.2.47.

Maximum Building Area, Group C, up to 3 Storeys

Forming Part of Sentence 3.2.2.47.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 800 | 2 250 | 2 700 |
| 2 | 900 | 1 125 | 1 350 |
| 3 | 600 | 750 | 900 |
| Column 1 | 2 | 3 | 4 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction a fire-resistance rating not less than 45 min, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(3)  In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(2), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 45 min but need not be constructed as fire separations.

(4)  In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived.

3.2.2.48.  Group C, up to 3 Storeys, Sprinklered

(1)  A building classified as Group C is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 3 storeys in building height, and

(c)	it has a building area not more than

(i)	5 400 m2 if 1 storey in building height,

(ii)	2 700 m2 if 2 storeys in building height, or

(iii)	1 800 m2 if 3 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction a fire-resistance rating not less than 45 min, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(3)  In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(2), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 45 min but need not be constructed as fire separations.

(4)  In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived.

3.2.2.49.  Group D, Any Height, Any Area

(1)  Except as permitted by Articles 3.2.2.50. to 3.2.2.56., a building classified as Group D shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered if it is regulated by Subsection 3.2.6.,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h,

(d)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, except that in a building not more than 1 storey in building height this requirement is waived, and

(e)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.50.  Group D, up to 6 Storeys

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided

(a)	it is not more than 6 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.50.

Table 3.2.2.50.

Maximum Building Area, Group D, up to 6 Storeys

Forming Part of Sentence 3.2.2.50.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | not limited | not limited | not limited |
| 2 | 7 200 | not limited | not limited |
| 3 | 4 800 | 6 000 | 7 200 |
| 4 | 3 600 | 4 500 | 5 400 |
| 5 | 2 800 | 3 600 | 4 320 |
| 6 | 2 400 | 3 000 | 3 600 |
| Column 1 | 2 | 3 | 4 |

(2)  The building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	roof assemblies shall have a fire-resistance rating not less than 1 h, except that in a building not more than 1 storey in building height this requirement is waived, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.51.  Group D, up to 6 Storeys, Sprinklered

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 6 storeys in building height, and

(c)	it has a building area

(i)	that is not limited if the building is not more than 2 storeys in building height,

(ii)	not more than 14 400 m2 if 3 storeys in building height,

(iii)	not more than 10 800 m2 if 4 storeys in building height,

(iv)	not more than 8 640 m2 if 5 storeys in building height, or

(v)	not more than 7 200 m2 if 6 storeys in building height.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.52.  Group D, up to 4 Storeys, Sprinklered

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 4 storeys in building height, and

(c)	it has a building area not more than 3 600 m2.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.53.  Group D, up to 3 Storeys

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided

(a)	it is not more than 3 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.53.

Table 3.2.2.53.

Maximum Building Area, Group D, up to 3 Storeys

Forming Part of Sentence 3.2.2.53.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 4 800 | 6 000 | 7 200 |
| 2 | 2 400 | 3 000 | 3 600 |
| 3 | 1 600 | 2 000 | 2 400 |
| Column 1 | 2 | 3 | 4 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(c)	roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than

(i)	2 400 m2 if facing one street,

(ii)	3 000 m2 if facing 2 streets, or

(iii)	3 600 m2 if facing 3 streets, and

(d)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.54.  Group D, up to 3 Storeys, Sprinklered

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 3 storeys in building height, and

(c)	it has a building area not more than

(i)	14 400 m2 if 1 storey in building height,

(ii)	7 200 m2 if 2 storeys in building height, or

(iii)	4 800 m2 if 3 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

(c)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.55.  Group D, up to 2 Storeys

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided

(a)	it is not more than 2 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.55.

Table 3.2.2.55.

Maximum Building Area, Group D, up to 2 Storeys

Forming Part of Sentence 3.2.2.55.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 000 | 1 250 | 1 500 |
| 2 | 800 | 1 000 | 1 200 |
| Column 1 | 2 | 3 | 4 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.56.  Group D, up to 2 Storeys, Sprinklered

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than

(i)	3 000 m2 if 1 storey in building height, or

(ii)	2 400 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.57.  Group E, Any Height, Any Area, Sprinklered

(1)  Except as permitted by Articles 3.2.2.58. to 3.2.2.62., a building classified as Group E shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.58.  Group E, up to 4 Storeys, Sprinklered

(1)  A building classified as Group E is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 4 storeys in building height, and

(c)	it has a building area not more than 1 800 m2.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.59.  Group E, up to 3 Storeys

(1)  A building classified as Group E is permitted to conform to Sentence (2) provided

(a)	it is not more than 3 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.59.

Table 3.2.2.59.

Maximum Building Area, Group E, up to 3 Storeys

Forming Part of Sentence 3.2.2.59.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 500 | 1 500 | 1 500 |
| 2 | 1 200 | 1 500 | 1 500 |
| 3 | 800 | 1 000 | 1 500 |
| Column 1 | 2 | 3 | 4 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(c)	roof assemblies shall have a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is of noncombustible construction or is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1.,

(d)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction, and

(e)	loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation.

3.2.2.60.  Group E, up to 3 Storeys, Sprinklered

(1)  A building classified as Group E is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 3 storeys in building height, and

(c)	it has a building area not more than

(i)	7 200 m2 if 1 storey in building height,

(ii)	3 600 m2 if 2 storeys in building height, or

(iii)	2 400 m2 if 3 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(c)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction, and

(d)	loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation.

3.2.2.61.  Group E, up to 2 Storeys

(1)  A building classified as Group E is permitted to conform to Sentence (2) provided

(a)	it is not more than 2 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.61.

Table 3.2.2.61.

Maximum Building Area, Group E, up to 2 Storeys

Forming Part of Sentence 3.2.2.61.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 000 | 1 250 | 1 500 |
| 2 | 600 | 750 | 900 |
| Column 1 | 2 | 3 | 4 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, and

(b)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.62.  Group E, up to 2 Storeys, Sprinklered

(1)  A building classified as Group E is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than

(i)	3 000 m2 if 1 storey in building height, or

(ii)	1 800 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, and

(b)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.63.  Group F, Division 1, up to 4 Storeys, Sprinklered

(1)  Except as permitted by Articles 3.2.2.64. to 3.2.2.66., a building classified as Group F, Division 1 shall conform to Sentence (2) provided

(a)	it is not more than 4 storeys in building height, and

(b)	it has a building area not more than

(i)	9 000 m2 if 1 storey in building height,

(ii)	4 500 m2 if 2 storeys in building height,

(iii)	3 000 m2 if 3 storeys in building height, or

(iv)	2 250 m2 if 4 storeys in building height.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.64.  Group F, Division 1, up to 3 Storeys, Sprinklered

(1)  A building classified as Group F, Division 1 is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 3 storeys in building height, and

(c)	it has a building area not more than

(i)	3 600 m2 if 1 storey in building height,

(ii)	1 800 m2 if 2 storeys in building height, or

(iii)	1 200 m2 if 3 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.65.  Group F, Division 1, up to 2 Storeys, Sprinklered

(1)  A building classified as Group F, Division 1 is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than

(i)	2 400 m2 if 1 storey in building height, or

(ii)	1 200 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.66.  Group F, Division 1, One Storey

(1)  A building classified as Group F, Division 1 is permitted to be of combustible construction or noncombustible construction used singly or in combination provided

(a)	it is not more than 1 storey in building height, and

(b)	it has a building area not more than 800 m2.

3.2.2.67.  Group F, Division 2, Any Height, Any Area, Sprinklered

(1)  Except as permitted by Articles 3.2.2.68. to 3.2.2.72., a building classified as Group F, Division 2 shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.68.  Group F, Division 2, up to 6 Storeys

(1)  A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided

(a)	it is not more than 6 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.68.A. or Table 3.2.2.68.B.

Table 3.2.2.68.A.

Maximum Building Area, Group F, Division 2, up to 6 Storeys

Forming Part of Sentence 3.2.2.68.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 9 000 | 11 250 | 13 500 |
| 2 | 4 500 | 5 625 | 6 750 |
| 3 | 3 000 | 3 750 | 4 500 |
| 4 | 2 250 | 2 810 | 3 375 |
| 5 | 1 800 | 2 250 | 2 700 |
| 6 | 1 500 | 1 875 | 2 250 |
| Column 1 | 2 | 3 | 4 |

Table 3.2.2.68.B.

Maximum Building Area, Group F, Division 2, up to 6 Storeys, Sprinklered

Forming Part of Sentence 3.2.2.68.(1)

| No. of Storeys | Maximum Area, m2 |
| --- | --- |
| 1 | 27 000 |
| 2 | 13 500 |
| 3 | 9 000 |
| 4 | 6 750 |
| 5 | 5 400 |
| 6 | 4 500 |
| Column 1 | 2 |

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.69.  Group F, Division 2, up to 4 Storeys, Increased Area

(1)  A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided

(a)	it is not more than 4 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.69.A. or Table 3.2.2.69.B.

Table 3.2.2.69.A.

Maximum Building Area, Group F, Division 2, up to 4 Storeys, Increased Area

Forming Part of Sentence 3.2.2.69.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 6 000 | 7 500 | 9 000 |
| 2 | 3 000 | 3 750 | 4 500 |
| 3 | 2 000 | 2 500 | 3 000 |
| 4 | 1 500 | 1 875 | 2 250 |
| Column 1 | 2 | 3 | 4 |

Table 3.2.2.69.B.

Maximum Building Area, Group F, Division 2, up to 4 Storeys, Increased Area, Sprinklered

Forming Part of Sentence 3.2.2.69.(1)

| No. of Storeys | Maximum Area, m2 |
| --- | --- |
| 1 | 18 000 |
| 2 | 9 000 |
| 3 | 6 000 |
| 4 | 4 500 |
| Column 1 | 2 |

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.70.  Group F, Division 2, up to 4 Storeys

(1)  A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided

(a)	it is not more than 4 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.70.A. or Table 3.2.2.70.B.

Table 3.2.2.70.A.

Maximum Building Area, Group F, Division 2, up to 4 Storeys

Forming Part of Sentence 3.2.2.70.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 3 200 | 4 000 | 4 800 |
| 2 | 1 600 | 2 000 | 2 400 |
| 3 | 1 070 | 1 340 | 1 600 |
| 4 | 800 | 1 000 | 1 200 |
| Column 1 | 2 | 3 | 4 |

Table 3.2.2.70.B.

Maximum Building Area, Group F, Division 2, up to 4 Storeys Increased Area, Sprinklered

Forming Part of Sentence 3.2.2.70.(1)

| No. of Storeys | Maximum Area, m2 |
| --- | --- |
| 1 | 9 600 |
| 2 | 4 800 |
| 3 | 3 200 |
| 4 | 2 400 |
| Column 1 | 2 |

(2)  The building referred to in Sentence (1) shall be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(c)	if the building is not sprinklered, roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in buildings not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than

(i)	1 600 m2 if facing 1 street,

(ii)	2 000 m2 if facing 2 streets, or

(iii)	2 400 m2 if facing 3 streets,

(d)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction, and

(e)	loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.71.  Group F, Division 2, up to 2 Storeys

(1)  A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided

(a)	it is not more than 2 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.71.

Table 3.2.2.71.

Maximum Building Area, Group F, Division 2, up to 2 Storeys

Forming Part of Sentence 3.2.2.71.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 000 | 1 250 | 1 500 |
| 2 | 600 | 750 | 900 |
| Column 1 | 2 | 3 | 4 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.72.  Group F, Division 2, up to 2 Storeys, Sprinklered

(1)  A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than

(i)	4 500 m2 if 1 storey in building height, or

(ii)	1 800 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.73.  Group F, Division 3, Any Height, Any Area

(1)  Except as permitted by Articles 3.2.2.74. to 3.2.2.83., a building classified as Group F, Division 3 shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered if it is regulated by Subsection 3.2.6.,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, except that floor assemblies are permitted to be fire separations with a fire-resistance rating not less than 1 h in a storage garage with all storeys constructed as open-air storeys,

(c)	mezzanines shall have a fire-resistance rating not less 1 h,

(d)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and

(e)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.74.  Group F, Division 3, up to 6 Storeys

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided

(a)	it is not more than 6 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.74.

Table 3.2.2.74.

Maximum Building Area, Group F, Division 3, up to 6 Storeys

Forming Part of Sentence 3.2.2.74.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | not limited | not limited | not limited |
| 2 | 7 200 | 9 000 | 10 800 |
| 3 | 4 800 | 6 000 | 7 200 |
| 4 | 3 600 | 4 500 | 5 400 |
| 5 | 2 880 | 3 600 | 4 320 |
| 6 | 2 400 | 3 000 | 3 600 |
| Column 1 | 2 | 3 | 4 |

(2)  The building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.75.  Group F, Division 3, up to 6 Storeys, Sprinklered

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 6 storeys in building height, and

(c)	it has a building area

(i)	that is not limited if the building is not more than 1 storey in building height,

(ii)	not more than 21 600 m2 if 2 storeys in building height,

(iii)	not more than 14 400 m2 if 3 storeys in building height,

(iv)	not more than 10 800 m2 if 4 storeys in building height,

(v)	not more than 8 640 m2 if 5 storeys in building height, or

(vi)	not more than 7 200 m2 if 6 storeys in building height.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.76.  Group F, Division 3, up to 4 Storeys

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided

(a)	it is not more than 4 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.76.

Table 3.2.2.76.

Maximum Building Area, Group F, Division 3, up to 4 Storeys

Forming Part of Sentence 3.2.2.76.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 4 800 | 6 000 | 7 200 |
| 2 | 2 400 | 3 000 | 3 600 |
| 3 | 1 600 | 2 000 | 2 400 |
| 4 | 1 200 | 1 500 | 1 800 |
| Column 1 | 2 | 3 | 4 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(c)	roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than

(i)	2 400 m2 if facing 1 street,

(ii)	3 000 m2 if facing 2 streets, or

(iii)	3 600 m2 if facing 3 streets, and

(d)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.77.  Group F, Division 3, up to 4 Storeys, Sprinklered

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 4 storeys in building height, and

(c)	it has a building area not more than

(i)	14 400 m2 if 1 storey in building height,

(ii)	7 200 m2 if 2 storeys in building height,

(iii)	4 800 m2 if 3 storeys in building height, or

(iv)	3 600 m2 if 4 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

(c)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.78.  Group F, Division 3, up to 2 Storeys

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided

(a)	it is not more than 2 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.78.

Table 3.2.2.78.

Maximum Building Area, Group F, Division 3, up to 2 Storeys

Forming Part of Sentence 3.2.2.78.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 600 | 2 000 | 2 400 |
| 2 | 800 | 1 000 | 1 200 |
| Column 1 | 2 | 3 | 4 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.79.  Group F, Division 3, up to 2 Storeys, Sprinklered

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than

(i)	7 200 m2 if 1 storey in building height, or

(ii)	2 400 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.80.  Group F, Division 3, One Storey

(1)  A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination provided

(a)	it is not more than 1 storey in building height, and

(b)	it has a building area is not more than

(i)	5 600 m2 if facing 1 street,

(ii)	7 000 m2 if facing 2 streets, or

(iii)	8 400 m2 if facing 3 streets.

3.2.2.81.  Group F, Division 3, One Storey, Sprinklered

(1)  A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination provided

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 1 storey in building height, and

(c)	it has a building area not more than 16 800 m2.

3.2.2.82.  Group F, Division 3, One Storey, Any Area, Low Fire Load Occupancy

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided it is

(a)	not more than 1 storey in building height,

(b)	used solely for low fire load occupancies such as

(i)	power generating plants, or

(ii)	plants for the manufacture or storage of noncombustible materials, and

(c)	not limited in building area.

(2)  The building referred to in Sentence (1) shall be of noncombustible construction.

3.2.2.83.  Group F, Division 3, Storage Garages up to 22 m High

(1)  A building used as a storage garage with all storeys constructed as open-air storeys and having no other occupancy above it is permitted to have its floor, wall, ceiling and roof assemblies constructed without a fire-resistance rating provided it is

(a)	of noncombustible construction,

(b)	not more than 22 m high, measured between grade and the ceiling level of the top storey,

(c)	not more than 10 000 m2 in building area, and

(d)	designed so that every portion of each floor area is within 60 m of an exterior wall opening.

3.2.3. Spatial Separation and Exposure Protection

3.2.3.1.  Limiting Distance and Area of Unprotected Openings

(1)  Except as permitted by Articles 3.2.3.9. to 3.2.3.11., the area of unprotected openings in an exposing building face for the applicable limiting distance shall be not more than the value determined in accordance with

(a)	Table 3.2.3.1.A. or Table 3.2.3.1.B. for an exposing building face conforming to Article 3.2.3.2. of a building or fire compartment which is not sprinklered, or

(b)	Table 3.2.3.1.C. or Table 3.2.3.1.D. for an exposing building face conforming to Article 3.2.3.2. of a sprinklered fire compartment that is part of a building which is sprinklered in conformance with Section 3.2.

(2)  The area of the unprotected openings in an exposing building face shall be the aggregate area of unprotected openings expressed as a percentage of the area of the exposing building face in Table 3.2.3.1.A., Table 3.2.3.1.B., Table 3.2.3.1.C. or Table 3.2.3.1.D.

(3)  For the purpose of determining the type of construction and cladding and the fire-resistance rating of an exterior wall

(a)	the exposing building face shall be taken as the projection of the exterior wall onto a vertical plane located so that no portion of the exterior wall of the building or of a fire compartment, if the fire compartment complies with the requirements of Sentences 3.2.3.2.(2), (4) or (6), is between the vertical plane and the line to which the limiting distance is measured, and

(b)	the area of unprotected openings shall be determined from Table 3.2.3.1.A., Table 3.2.3.1.B., Table 3.2.3.1.C. or Table 3.2.3.1.D.

Table 3.2.3.1.A.

Unprotected Opening Limits for a Building or Fire Compartment that is not Sprinklered

Forming Part of Article 3.2.3.1.

| Exposing Building Face |  | Area of Unprotected Openings for Groups A, C, D, and F, Division 3 Occupancies, % |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Maximum Area, m2 | Ratio (L/H or H/L)(1) | Limiting Distance, m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 0 | 1.2 | 1.5 | 2.0 | 2.5 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 16 | 18 | 20 | 25 | 30 | 35 | 40 | 45 | 50 |
| 10 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 8 8 11 | 10 12 18 | 18 21 32 | 29 33 48 | 46 50 68 | 91 96 100 | 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 8 10 | 9 10 15 | 14 17 26 | 22 25 39 | 33 37 53 | 63 67 87 | 100 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 20 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 8 9 | 9 10 14 | 12 15 23 | 18 21 33 | 26 30 45 | 49 53 72 | 81 85 100 | 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 25 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 8 9 | 8 9 13 | 11 13 21 | 16 19 30 | 23 26 39 | 41 45 62 | 66 70 90 | 98 100 100 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 30 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 7 8 | 8 9 12 | 11 12 19 | 15 17 27 | 20 23 36 | 35 39 56 | 56 61 79 | 83 88 100 | 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 40 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 7 8 | 8 8 11 | 10 11 17 | 13 15 24 | 17 20 31 | 28 32 47 | 44 48 66 | 64 69 88 | 89 93 100 | 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 50 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 7 8 | 8 8 10 | 9 10 15 | 12 14 21 | 15 18 28 | 24 28 41 | 37 41 57 | 53 57 76 | 72 77 97 | 96 100 100 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 60 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 7 8 | 8 8 10 | 9 10 14 | 11 13 20 | 14 16 25 | 21 25 38 | 32 36 51 | 45 49 67 | 62 66 85 | 81 85 100 | 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 80 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 7 8 | 7 8 9 | 8 9 13 | 10 11 17 | 12 14 22 | 18 21 32 | 26 29 44 | 36 40 56 | 48 52 70 | 62 67 86 | 79 84 100 | 98 100 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |
| 100 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 7 7 | 7 8 9 | 8 9 12 | 9 11 16 | 11 13 20 | 16 18 29 | 22 25 39 | 30 34 49 | 40 44 61 | 51 56 74 | 65 69 89 | 80 84 100 | 97 100 | 100 |  |  |  |  |  |  |  |  |  |  |  |
| 150 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 7 7 | 7 7 8 | 8 8 11 | 9 10 13 | 10 11 17 | 13 15 24 | 17 20 31 | 22 26 39 | 29 33 48 | 37 41 57 | 46 50 68 | 56 60 79 | 67 71 91 | 79 84 100 | 93 97 | 100 100 |  |  |  |  |  |  |  |  |  |
| 250 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 7 7 | 7 7 8 | 7 8 9 | 8 9 11 | 9 10 14 | 10 12 19 | 13 15 24 | 16 19 30 | 20 24 36 | 25 28 43 | 30 34 50 | 36 40 57 | 43 47 65 | 51 55 73 | 59 63 82 | 68 72 92 | 87 92 100 | 100 100 |  |  |  |  |  |  |  |
| 350 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 7 7 | 7 7 8 | 7 8 9 | 8 8 10 | 8 9 12 | 9 11 16 | 11 13 21 | 14 16 25 | 16 19 30 | 20 23 36 | 24 27 41 | 28 32 47 | 33 37 53 | 38 42 59 | 44 48 66 | 50 55 73 | 64 69 88 | 81 85 100 | 99 100 | 100 |  |  |  |  |  |
| 500 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 7 7 | 7 7 7 | 7 7 8 | 7 8 9 | 8 8 11 | 9 10 14 | 10 12 18 | 12 14 22 | 14 16 25 | 16 19 30 | 19 22 34 | 22 25 38 | 25 29 43 | 29 33 48 | 33 37 53 | 37 41 58 | 47 52 70 | 59 63 82 | 71 76 96 | 100 100 100 |  |  |  |  |  |
| 1 000 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 7 7 | 7 7 7 | 7 7 8 | 7 7 8 | 7 8 9 | 8 9 11 | 9 10 13 | 9 11 16 | 10 12 19 | 12 24 21 | 13 15 24 | 14 17 27 | 16 19 30 | 18 21 33 | 20 23 36 | 22 26 39 | 27 31 46 | 33 37 53 | 39 43 60 | 58 63 82 | 82 86 100 | 100 100 |  |  |  |
| 2 000 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 | 7 7 7 | 7 7 7 | 7 7 7 | 7 7 8 | 7 7 8 | 7 8 9 | 8 8 11 | 8 9 12 | 9 10 14 | 9 11 16 | 10 12 18 | 11 13 19 | 12 14 21 | 13 15 23 | 14 16 25 | 15 17 27 | 17 20 32 | 20 23 36 | 23 27 40 | 33 37 53 | 44 49 66 | 58 63 82 | 74 79 99 | 93 97 100 | 100 100 |

Note to Table 3.2.3.1.A.:

(1) Apply whichever is greater,

L = Length of exposing building face,

H = Height of exposing building face

Table 3.2.3.1.B.

Unprotected Opening Limits for a Building or Fire Compartment that is not Sprinklered

Forming Part of Article 3.2.3.1.

| Exposing Building Face |  |  | Area of Unprotected Openings for Groups E and F, Division 1 and 2 Occupancies, % |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Maximum Area, m2 | Ratio (L/H or H/L)(1) | Limiting Distance, m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 0 |  | 1.2 | 1.5 | 2.0 | 2.5 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 16 | 18 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 |
| 10 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 5 | 5 6 9 | 9 10 16 | 15 17 24 | 23 25 34 | 46 48 58 | 77 79 91 | 100 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 5 | 5 5 8 | 7 8 13 | 11 13 19 | 16 18 26 | 32 34 43 | 53 55 66 | 79 82 93 | 100 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 20 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 5 | 4 5 7 | 6 7 11 | 9 11 17 | 13 15 22 | 25 27 36 | 40 43 53 | 61 63 74 | 85 87 99 | 100 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 25 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 4 | 4 5 6 | 6 7 10 | 8 9 15 | 11 13 20 | 20 22 31 | 33 35 45 | 49 51 62 | 69 71 82 | 92 94 100 | 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 30 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 4 | 4 4 6 | 5 6 10 | 7 9 14 | 10 12 18 | 18 20 28 | 28 30 40 | 42 44 54 | 58 60 71 | 77 80 91 | 100 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 40 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 4 | 4 4 5 | 5 6 8 | 6 8 12 | 8 10 15 | 14 16 23 | 22 24 33 | 32 34 44 | 44 47 57 | 59 61 72 | 76 78 89 | 94 97 100 | 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 50 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 4 | 4 4 5 | 5 5 8 | 6 7 11 | 7 9 14 | 12 14 21 | 18 20 29 | 26 29 38 | 36 38 48 | 48 50 61 | 61 63 74 | 76 79 90 | 93 95 100 | 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 60 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 4 | 4 4 5 | 4 5 7 | 5 6 10 | 7 8 13 | 11 12 19 | 16 18 26 | 23 25 34 | 31 33 43 | 40 43 53 | 52 54 64 | 64 66 77 | 78 81 92 | 94 96 100 | 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 80 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 4 | 4 4 5 | 4 5 6 | 5 6 9 | 6 7 11 | 9 10 16 | 13 15 22 | 18 20 28 | 24 26 35 | 31 33 43 | 40 42 52 | 49 51 62 | 60 62 73 | 71 74 85 | 84 86 98 | 98 100 100 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |
| 100 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 4 | 4 4 4 | 4 4 6 | 5 5 8 | 5 6 10 | 8 9 14 | 11 13 19 | 15 17 25 | 20 22 31 | 26 28 37 | 32 35 44 | 40 42 52 | 48 51 61 | 58 60 71 | 68 70 81 | 79 81 92 | 100 100 100 |  |  |  |  |  |  |  |  |  |  |  |  |
| 150 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 4 | 4 4 4 | 4 4 5 | 4 5 7 | 5 6 8 | 6 8 12 | 8 10 16 | 11 13 20 | 14 16 24 | 18 20 29 | 23 25 34 | 28 30 39 | 33 36 46 | 40 42 52 | 46 49 59 | 54 56 67 | 70 73 84 | 89 92 100 | 100 100 |  |  |  |  |  |  |  |  |  |  |
| 250 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 4 | 4 4 4 | 4 4 5 | 4 4 6 | 4 5 7 | 5 6 9 | 7 8 12 | 8 10 15 | 10 12 18 | 12 14 21 | 15 17 25 | 18 20 28 | 22 24 32 | 25 27 37 | 29 32 41 | 34 36 46 | 44 46 56 | 55 57 68 | 68 70 81 | 100 100 100 |  |  |  |  |  |  |  |  |  |
| 350 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 4 | 4 4 4 | 4 4 4 | 4 4 5 | 4 4 6 | 5 5 8 | 6 7 10 | 7 8 13 | 8 10 15 | 10 12 18 | 12 14 21 | 14 16 23 | 16 18 26 | 19 21 30 | 22 24 33 | 25 27 36 | 32 34 44 | 40 43 53 | 49 52 62 | 77 79 90 | 100 100 100 |  |  |  |  |  |  |  |  |
| 500 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 4 | 4 4 4 | 4 4 4 | 4 4 5 | 4 4 5 | 4 5 7 | 5 6 9 | 6 7 11 | 7 8 13 | 8 9 15 | 9 11 17 | 11 13 19 | 13 14 21 | 14 16 24 | 16 18 26 | 19 21 29 | 24 26 35 | 29 31 41 | 36 38 48 | 55 57 68 | 78 80 92 | 100 100 100 |  |  |  |  |  |  |  |
| 1 000 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 4 | 4 4 4 | 4 4 4 | 4 4 4 | 4 4 5 | 4 4 6 | 4 5 7 | 5 5 8 | 5 6 9 | 6 7 11 | 6 8 12 | 7 9 13 | 8 10 15 | 9 11 16 | 10 12 18 | 11 13 20 | 14 15 23 | 16 18 26 | 20 22 30 | 29 31 41 | 41 43 53 | 55 57 68 | 71 73 84 | 89 91 100 | 100 100 |  |  |  |  |
| 2 000 | Less than 3:1 3:1 to 10:1 over 10:1 | 0 0 0 |  | 4 4 4 | 4 4 4 | 4 4 4 | 4 4 4 | 4 4 4 | 4 4 5 | 4 4 5 | 4 5 6 | 4 5 7 | 5 5 8 | 5 6 9 | 5 6 10 | 6 7 11 | 6 7 12 | 7 8 13 | 7 9 14 | 9 10 16 | 10 12 18 | 12 13 20 | 16 18 26 | 22 24 33 | 29 31 41 | 37 39 50 | 46 49 59 | 56 59 70 | 68 70 81 | 80 83 94 | 94 96 100 | 100 100 |

Note to Table 3.2.3.1.B.:

(1) Apply whichever is greater,

L = Length of exposing building face,

H = Height of exposing building face

Table 3.2.3.1.C.

Unprotected Opening Limits for a Building or Fire Compartment that is Sprinklered

Forming Part of Article 3.2.3.1.

| Exposing Building Face | Area of Unprotected Opening for Groups A, B, C, D and F, Division 3, Occupancies, % |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Maximum Area, m2 | Limiting Distance, m |  |  |  |  |  |  |  |  |  |  |  |
|  | 0 | 1.2 | 1.5 | 2.0 | 2.5 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| 10 | 0 | 16 | 24 | 42 | 66 | 100 |  |  |  |  |  |  |
| 15 | 0 | 16 | 20 | 34 | 50 | 74 | 100 |  |  |  |  |  |
| 20 | 0 | 16 | 20 | 30 | 42 | 60 | 100 |  |  |  |  |  |
| 25 | 0 | 16 | 18 | 26 | 38 | 52 | 90 | 100 |  |  |  |  |
| 30 | 0 | 14 | 18 | 24 | 34 | 46 | 78 | 100 |  |  |  |  |
| 40 | 0 | 14 | 16 | 22 | 30 | 40 | 64 | 96 | 100 |  |  |  |
| 50 | 0 | 14 | 16 | 20 | 28 | 36 | 56 | 82 | 100 |  |  |  |
| 60 | 0 | 14 | 16 | 20 | 26 | 32 | 50 | 72 | 98 | 100 |  |  |
| 80 | 0 | 14 | 16 | 18 | 22 | 28 | 42 | 58 | 80 | 100 |  |  |
| 100 | 0 | 14 | 16 | 18 | 22 | 26 | 36 | 50 | 68 | 88 | 100 |  |
| 150 or more | 0 | 14 | 14 | 16 | 20 | 22 | 30 | 40 | 52 | 66 | 82 | 100 |

Table 3.2.3.1.D.

Unprotected Opening Limits for a Building or Fire Compartment that is Sprinklered

Forming Part of Article 3.2.3.1.

| Exposing Building Face | Area of Unprotected Opening for Groups E and F, Division 1 and 2, Occupancies, % |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Maximum Area, m2 | Limiting Distance, m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 0 | 1.2 | 1.5 | 2.0 | 2.5 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |
| 10 | 0 | 10 | 12 | 20 | 34 | 15 | 96 | 100 |  |  |  |  |  |  |  |  |  |  |
| 15 | 0 | 8 | 10 | 16 | 26 | 36 | 68 | 100 |  |  |  |  |  |  |  |  |  |  |
| 20 | 0 | 8 | 10 | 14 | 22 | 30 | 54 | 86 | 100 |  |  |  |  |  |  |  |  |  |
| 25 | 0 | 8 | 10 | 14 | 18 | 26 | 44 | 70 | 100 |  |  |  |  |  |  |  |  |  |
| 30 | 0 | 8 | 8 | 12 | 18 | 24 | 40 | 60 | 88 | 100 |  |  |  |  |  |  |  |  |
| 40 | 0 | 8 | 8 | 12 | 16 | 20 | 32 | 48 | 68 | 94 | 100 |  |  |  |  |  |  |  |
| 50 | 0 | 8 | 8 | 10 | 14 | 18 | 28 | 40 | 58 | 76 | 100 |  |  |  |  |  |  |  |
| 60 | 0 | 8 | 8 | 10 | 12 | 16 | 24 | 36 | 50 | 66 | 86 | 100 |  |  |  |  |  |  |
| 80 | 0 | 8 | 8 | 10 | 12 | 14 | 20 | 30 | 40 | 52 | 66 | 84 | 100 |  |  |  |  |  |
| 100 | 0 | 8 | 8 | 8 | 10 | 12 | 18 | 26 | 34 | 44 | 56 | 70 | 84 | 100 |  |  |  |  |
| 150 | 0 | 8 | 8 | 8 | 10 | 12 | 16 | 20 | 26 | 32 | 40 | 50 | 60 | 72 | 84 | 98 | 100 |  |
| 200 or more | 0 | 8 | 8 | 8 | 8 | 10 | 14 | 18 | 22 | 28 | 34 | 42 | 50 | 60 | 68 | 80 | 92 | 100 |

(4)  For the purpose of determining the actual percentage of unprotected openings permitted in an exterior wall, the location of the exposing building face is permitted to be taken at a vertical plane located so that there are no unprotected openings between the vertical plane and the line to which the limiting distance is measured.

(5)  If a building has any storey that is not sprinklered and fire fighting facilities cannot reach it within 10 min of the alarm being received, the required limiting distance shall be doubled.

(6)  If the surface temperature on the unexposed surface of a wall assembly exceeds the temperature limit of a standard fire test as permitted by Article 3.1.7.2., an allowance shall be made for the radiation from the hot unexposed wall surface by adding an equivalent area of unprotected opening to the area of actual openings as follows:

AC = A +(AF × FEO)

where

| Ac | = | corrected area of unprotected openings including actual and equivalent openings, |
| --- | --- | --- |
| A | = | actual area of unprotected openings, |
| AF | = | area of exterior surface of the exposing building face exclusive of openings on which the temperature limit of the standard test is exceeded, and |
| FEO | = | an equivalent opening factor derived from the following expression: |

FEO = (Tu + 273)4(Te + 273)4

where

| Tu | = | average temperature in degrees Celsius of the unexposed wall surface at the time the required fire-resistance rating is reached under test conditions, |
| --- | --- | --- |
| Te | = | 892°C for a fire-resistance rating not less than 45 min, 927°C for a fire-resistance rating not less than 1 h, and 1 010°C for a fire-resistance rating not less than 2 h. |

(7)  Unless a closure used to protect an opening in an exposing building face has a protective performance equivalent to that required for the wall assembly in which it is located, an equivalent area of unprotected opening, determined in accordance with the procedures of Sentence (6) shall be added to the greater of

(a)	the actual area of unprotected openings, or

(b)	the corrected area of unprotected openings.

(8)  The required limiting distance for an exposing building face is permitted to be measured to a point beyond the property line that is not the centre line of a street, lane or public thoroughfare if

(a)	the owners of the properties on which the limiting distance is measured and the municipality enter into an agreement in which such owners agree that

(i)	each owner covenants that, for the benefit of land owned by the other covenantors, the owner will not construct a building on his or her property unless the limiting distance for exposing building faces in respect of the proposed construction is measured in accordance with the agreement,

(ii)	the covenants contained in the agreement are intended to run with the lands, and the agreement shall be binding on the parties and their respective heirs, executors, administrators, successors and assigns,

(iii)	the agreement shall not be amended or deleted from title without the consent of the municipality, and

(iv)	they will comply with such other conditions as the municipality considers necessary, including indemnification of the municipality by the other parties, and

(b)	the agreement referred to in Clause (a) is registered against the title of the properties to which it applies.

(9)  Where an agreement referred to in Sentence (8) is registered against the title of a property, the limiting distance for exposing building faces shall be measured to the point referred to in the agreement.

3.2.3.2.  Area of Exposing Building Face

(1)  Except as permitted by Sentences (2), (4), (6) and (7), the area of an exposing building face shall be calculated as the total area of exterior wall facing in one direction on any side of a building measured from the finished ground level to the uppermost ceiling.

(2)  Except as permitted by Sentence (3), if a building containing only Group A, B, C, D or Group F, Division 3 occupancies is divided by fire separations into fire compartments, the area of exposing building face is permitted to be calculated for each fire compartment provided the fire separations have a fire-resistance rating not less than 1 h.

(3)  The fire-resistance rating of the fire separations referred to in Sentence (2) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

(a)	the floor assembly above the fire compartment, or

(b)	the floor assembly below the fire compartment, if there is no floor assembly above.

(4)  Except as required by Sentence (5), if a building containing Group E or Group F, Division 1 or 2 occupancies is divided by fire separations into fire compartments, the area of exposing building face is permitted to be calculated for each fire compartment provided the fire separations have a fire-resistance rating not less than 45 min.

(5)  The fire-resistance rating of the fire separations referred to in Sentence (4) shall be not less than that required by Subsection 3.2.2. for

(a)	the floor assembly above the fire compartment, or

(b)	the floor assembly below the fire compartment, if there is no floor assembly above.

(6)  For the purposes of Sentence (1), where a horizontal fire separation is penetrated by openings that are not provided with closures, and the openings are in conformance with Article 3.2.8.2., the fire separation is permitted to be considered as enclosing construction for the purposes of determining fire compartments.

(7)  For the purposes of Sentence (1), where an interconnected floor space is in conformance with Articles 3.2.8.3. to 3.2.8.11., each storey in the interconnected floor space is permitted to be considered a fire compartment.

3.2.3.3.  Wall Enclosing Attic or Roof Space

(1)  An exterior wall enclosing an attic or roof space and located above an exposing building face, shall be constructed in conformance with the requirements for the exposing building face.

3.2.3.4.  Party Wall

(1)  A party wall shall be constructed as a firewall.

3.2.3.5.  Wall with Limiting Distance less than 1.2 m

(1)  Openings in a wall that has a limiting distance less than 1.2 m shall be protected by closures whose fire-protection rating is in conformance with the fire-resistance rating required for the wall.

(2)  Wired glass or glass block shall not be used for a closure referred to in Sentence (1).

3.2.3.6.  Combustible Projections

(1)  Except for a building containing one or 2 dwelling units only, combustible projections on the exterior of a wall that could expose an adjacent building to fire spread and are more than 1 000 mm above ground level, including balconies, platforms, canopies, eave projections and stairs, shall not be permitted within

(a)	1 200 mm of a property line or the centreline of a public way, or

(b)	2 400 mm of a combustible projection on another building on the same property.

3.2.3.7.  Construction of Exposing Building Face

(1)  Except as permitted by Articles 3.2.3.9. and 3.2.3.10., if a limiting distance shown in Table 3.2.3.1.A. or Table 3.2.3.1.C. for a Group A, B, C, D or Group F, Division 3 occupancy classification permits an exposing building face to have unprotected openings not more than 10% of the exposing building face, the exposing building face shall be

(a)	of noncombustible construction having a fire-resistance rating not less than 1 h, and

(b)	clad with noncombustible cladding.

(2)  Except as permitted by Sentence (9) and Articles 3.2.3.9. and 3.2.3.10., if a limiting distance shown in Table 3.2.3.1.A. or Table 3.2.3.1.C. for a Group A, B, C, D or Group F, Division 3 occupancy classification permits an exposing building face to have unprotected openings more than 10% but not more than 25% of the exposing building face, the exposing building face shall

(a)	have a fire-resistance rating not less than 1 h, and

(b)	be clad with noncombustible cladding.

(3)  Except as permitted by Articles 3.2.3.9. and 3.2.3.10., if a limiting distance shown in Table 3.2.3.1.A. or Table 3.2.3.1.C. for a Group A, B, C, D or Group F, Division 3 occupancy classification permits an exposing building face to have unprotected openings more than 25% but less than 100% of the exposing building face, the exposing building face shall have a fire-resistance rating not less than 45 min.

(4)  Except as permitted by Article 3.2.3.9., if a limiting distance shown in Table 3.2.3.1.B. or Table 3.2.3.1.D. for a Group E, or Group F, Division 1 or 2 occupancy classification permits an exposing building face to have unprotected openings not more than 10% of the exposing building face, the exposing building face shall be

(a)	of noncombustible construction having a fire-resistance rating not less than 2 h, and

(b)	clad with noncombustible cladding.

(5)  Except as permitted by Sentence (9) and Article 3.2.3.9., if a limiting distance shown in Table 3.2.3.1.B. or Table 3.2.3.1.D. for a Group E, or Group F, Division 1 or 2 occupancy classification permits an exposing building face to have unprotected openings more than 10% but not more than 25% of the exposing building face, the exposing building face shall

(a)	have a fire-resistance rating not less than 2 h, and

(b)	be clad with noncombustible cladding.

(6)  Except as permitted by Article 3.2.3.9., if a limiting distance shown in Table 3.2.3.1.B. or Table 3.2.3.1.D. for a Group E, or Group F, Division 1 or 2 occupancy classification permits an exposing building face to have unprotected openings more than 25% but less than 100% of the exposing building face, the exposing building face shall have a fire-resistance rating not less than 1 h.

(7)  Except as permitted by Sentence (9), in addition to the requirements of Sentences (2), (3), (5) and (6), foamed plastic insulation used in an exterior wall of a building more than 3 storeys in building height shall be protected on its exterior surface by

(a)	concrete or masonry not less than 25 mm thick, or

(b)	noncombustible material that complies with the criteria for testing and conditions of acceptance of Sentence (8) when tested in conformance with CAN/ULC-S101-M, “Standard Methods of Fire Endurance Tests of Building Construction and Materials”.

(8)  The criteria for testing and the conditions of acceptance for a wall assembly to satisfy the requirements of Clause (7)(b) are that

(a)	the fire exposed area of the wall assembly shall be not less than 9.3 m2 and have no dimension less than 2 750 mm,

(b)	the exposed surface will include typical vertical and horizontal joints,

(c)	the test shall be continued for not less than 15 min and the standard time/temperature curve of the referenced standard shall be followed,

(d)	the noncombustible protective material will remain in place and no through openings will develop that are visible when viewed normal to the face of the material, and

(e)	the noncombustible protective material will not disintegrate in a manner that would permit fire to propagate along the surface of the test assembly.

(9)  The requirements of Clauses (2) (b) and (5) (b) and Sentence (7) are waived for a wall assembly that complies with the requirements of Article 3.1.5.5.

3.2.3.8.  Protection of Structural Members

(1)  Structural members, including beams, columns and arches, placed wholly or partly outside an exterior face of a building and 3 m or more from the property line or centreline of a public thoroughfare need not be protected from exterior fires.

(2)  Structural members referred to in Sentence (1) that are less than 3 m from the property line or centreline of a public thoroughfare shall be protected from exterior fire by fire protection having a fire-resistance rating not less than that required by Articles 3.2.2.20. to 3.2.2.83. for their protection from interior fires, but not less than 1 h.

(3)  Structural members of heavy timber construction, including beams, columns and arches, placed wholly or partly outside an exterior face of a building and 3 m or more from the property line or centreline of a public thoroughfare need not be covered with noncombustible cladding.

3.2.3.9.  Unlimited Unprotected Openings

(1)  An exposing building face of an open-air storey in a storage garage is permitted to have unlimited unprotected openings provided it has a limiting distance not less than 3 m.

(2)  The exposing building face of a storey that faces a street and is at the same level as the street is permitted to have unlimited unprotected openings if the limiting distance is not less than 9 m.

3.2.3.10.  Low Fire Load, One Storey Building

(1)  An exposing building face of a building of low hazard industrial occupancy conforming to Article 3.2.2.82. is permitted to be of noncombustible construction without a fire-resistance rating provided

(a)	it is not a loadbearing wall, and

(b)	the limiting distance is not less than 3 m.

3.2.3.11.  Area Increase for Unprotected Openings

(1)  The maximum area of unprotected openings in any exposing building face is permitted to be doubled if the openings are glazed with

(a)	glass block conforming to the requirements of Article 3.1.8.14., or

(b)	wired glass assemblies conforming to the Supplementary Guidelines.

3.2.3.12.  Protection of Exit Facilities

(1)  Except as required by Sentence (3) and as permitted by Sentence 3.4.4.3.(1), if the plane of an exterior wall of an exit enclosure forms an angle less than 135° with the plane of an exterior wall of the building it serves, and an opening in the exterior wall of the exit enclosure could be exposed to fire from an opening in the exterior wall of the building, the opening in either the exterior wall of the exit or the exterior wall of the building shall be protected in conformance with the requirements of Sentence (4) where the opening in the exterior wall of the building is within 3 m horizontally and

(a)	less than 10 m below an opening in the exterior wall of the exit, or

(b)	less than 2 m above an opening in the exterior wall of the exit.

(2)  If an unenclosed exterior exit stair or ramp could be exposed to fire from an opening in the exterior wall of the building it serves, the opening in the exterior wall of the building shall be protected in conformance with the requirements of Sentence (4) where the opening in the exterior wall of the building is within 3 m horizontally and

(a)	less than 10 m below the exit stair or ramp, or

(b)	less than 5 m above the exit stair or ramp.

(3)  Except as permitted by Sentence 3.4.4.3.(1), if an exterior exit door in one fire compartment is within 3 m horizontally of an opening in another fire compartment and the exterior walls of these fire compartments intersect at an exterior angle of less than 135°, the opening shall be protected in conformance with the requirements of Sentence (4).

(4)  The opening protection referred to in Sentences (1), (2) and (3) shall consist of

(a)	glass block conforming to the requirements of Article 3.1.8.14.,

(b)	a wired glass assembly conforming to the Supplementary Guidelines, or

(c)	a closure conforming to the requirements of Subsection 3.1.8. and Articles 3.2.3.1. and 3.2.3.13.

3.2.3.13.  Wall Exposed to Another Wall

(1)  Except as required by Sentences (3) and 3.2.3.12.(1) or as permitted by Sentence 3.2.3.18.(4), if an unprotected opening in an exterior wall of a fire compartment is exposed to an unprotected opening in the exterior wall of another fire compartment, and the planes of the 2 walls are parallel or at an angle less than 135°, measured from the exterior of the building, the unprotected openings in the 2 fire compartments shall be separated by a distance not less than DO where DO = 2D - {( θ /90) x D} but in no case less than 1 000 mm, and

| D | = | the greater required limiting distance for the exposing building faces of the 2 fire compartments, and |
| --- | --- | --- |
| θ | = | the angle made by the intersecting planes of the exposing building faces of the 2 fire compartments (in the case where the exterior walls are parallel and face each other, θ = 0°). |

(2)  The exterior wall of each fire compartment referred to in Sentence (1) within the distance, DO, shall have a fire-resistance rating not less than that required for the interior vertical fire separation between the fire compartment and the remainder of the building.

(3)  Sentence (1) does not apply to unprotected openings of fire compartments within a building that is sprinklered, but shall apply to

(a)	unprotected openings of fire compartments on opposite sides of a firewall, and

(b)	exposure from unprotected openings of a fire compartment that is not protected by an automatic sprinkler system.

3.2.3.14.  Wall Exposed to Adjoining Roof

(1)  Except as permitted by Sentence 3.2.3.18.(4), if a wall in a building is exposed to a fire hazard from an adjoining roof of a separate fire compartment that is not sprinklered in the same building, and the exposed wall contains windows within 3 storeys vertically and 5 m horizontally of the roof, the roof shall contain no skylights within 5 m of the exposed wall.

3.2.3.15.  Protection of Soffits

(1)  Except as permitted by Sentences (2) and (3), where a common attic or roof space spans more than 2 suites of residential occupancy or more than 2 patients’ or residents’ sleeping rooms in a Group B, Division 2 or Division 3 occupancy, and the common attic or roof space projects beyond the exterior wall of the building, the portion of any soffit or other surface enclosing the projection which is less than 2 500 mm vertically above a window or door and less than 1 200 mm from either side of the window or door, shall have no openings and shall be protected by

(a)	noncombustible material

(i)	not less than 0.38 mm thick, and

(ii)	having a melting point not below 650°C,

(b)	not less than 12.7 mm thick gypsum soffit board or gypsum wallboard installed according to CSA A82.31-M, “Gypsum Board Application”,

(c)	not less than 11 mm thick plywood,

(d)	not less than 12.5 mm thick OSB or waferboard, or

(e)	not less than 11 mm thick lumber.

(2)  Where an attic or roof space, including its adjoining eave overhangs, is separated by construction conforming to Article 3.1.11.7. into compartments such that the resulting spaces are not common to more than 2 suites of residential occupancy or more than 2 patients’ or residents’ sleeping rooms in a Group B, Division 2 or Division 3 occupancy, the requirements in Sentence (1) do not apply.

(3)  If an eave overhang is completely separated from the remainder of the attic or roof space by fire stopping, the requirements of Sentence (1) do not apply.

(4)  The protection required by Sentence (1) for projections is permitted to be omitted if

(a)	the fire compartments behind the window and door openings are sprinklered in accordance with Article 3.2.5.13., and

(b)	all rooms, including closets and bathrooms, having openings in the wall beneath the soffit are sprinklered, notwithstanding exceptions permitted in the standards referenced in Article 3.2.5.13. for the installation of automatic sprinkler systems.

3.2.3.16.  Canopy Protection for Vertically Separated Openings

(1)  Except as permitted by Sentences (2) and (3), if a storey classified as a Group E or Group F, Division 1 or 2 major occupancy is required to be separated from the storey above by a fire separation

(a)	every opening in the exterior wall of the lower storey that is located vertically below an opening in the storey above shall be separated from the storey above by a canopy projecting not less than 1 000 mm from the face of the building at the intervening floor level, and

(b)	the canopy required by Clause (a) shall have a fire-resistance rating not less than that required for the floor assembly but need not be more than 1 h, except as required elsewhere in this Subsection.

(2)  Except as permitted by Sentence (3), the canopy required by Sentence (1) is permitted to be omitted if the exterior wall of the upper storey is recessed not less than 1 000 mm behind the exterior wall containing the opening in the lower storey.

(3)  The requirements of Sentences (1) and (2) are permitted to be waived if sprinklers are installed in

(a)	the lower storey referred to in Clause (1)(a), and

(b)	the storey immediately above the lower storey.

3.2.3.17.  Covered Vehicular Passageway

(1)  A covered vehicular passageway designed as a receiving or shipping area shall be separated from every building or part of a building adjoining it by a fire separation having a fire-resistance rating not less than 1.5 h.

(2)  A covered vehicular passageway constructed below grade shall be of noncombustible construction.

3.2.3.18.  Walkway between Buildings

(1)  Except as required by Sentence 3.2.3.19.(2), if buildings are connected by a walkway, each building shall be separated from the walkway by a fire separation with a fire-resistance rating not less than 45 min.

(2)  Except as permitted by Sentence (3), a walkway connected to a building required to be of noncombustible construction shall also be of noncombustible construction.

(3)  A walkway connected to a building required to be of noncombustible construction is permitted to be of heavy timber construction provided

(a)	not less than 50% of the area of any enclosing perimeter walls is open to the outdoors, and

(b)	the walkway is at ground level.

(4)  A walkway of noncombustible construction used only as a pedestrian thoroughfare need not conform to the requirements of Articles 3.2.3.13. and 3.2.3.14.

(5)  A walkway between buildings shall be not more than 9 m wide.

3.2.3.19.  Underground Walkway

(1)  An underground walkway shall not be designed or used for any purpose other than pedestrian travel unless

(a)	the purpose is permitted, and

(b)	sprinklers are installed in any space in the walkway containing an occupancy.

(2)  Buildings connected by an underground walkway shall be separated from the walkway by a fire separation with a fire-resistance rating not less than 1 h.

(3)  An underground walkway shall be of noncombustible construction suitable for an underground location.

(4)  In an underground walkway

(a)	smoke barrier doors shall be installed at intervals of not more than 100 m, or

(b)	the travel distance from the door of an adjacent room or space to the nearest exit shall be not more than one and a half times the least allowable travel distance to an exit for any of the adjacent occupancies as permitted by Sentence 3.4.2.5.(1).

(5)  An underground walkway between buildings shall be not more than 9 m wide.

3.2.4. Fire Alarm and Detection Systems

3.2.4.1.  Determination of Requirement for a Fire Alarm System

(1)  Reserved

(2)  Except as permitted by Sentences (3) to (5) and Sentence 3.2.4.2.(4), a fire alarm system shall be installed in a building that contains

(a)	a contained use area,

(b)	an impeded egress zone,

(c)	more than 3 storeys, including storeys below grade,

(d)	a total occupant load more than 300, other than in open air seating areas,

(e)	an occupant load more than 150 above or below the first storey, other than in open air seating areas,

(f)	a school, college, or child care facility, with an occupant load more than 40,

(g)	a licensed beverage establishment or a restaurant, with an occupant load more than 150,

(h)	a medium hazard industrial occupancy or a low hazard industrial occupancy with an occupant load more than 75 above or below the first storey,

(i)	a residential occupancy with sleeping accommodation for more than 10 persons,

(j)	a high hazard industrial occupancy with an occupant load more than 25,

(k)	an occupant load more than 300 below an open air seating area,

(l)	an interconnected floor space required to conform to Articles 3.2.8.3. to 3.2.8.11,

(m)	a care and treatment occupancy for more than 10 persons receiving care or treatment, or

(n)	a care occupancy for more than 10 persons receiving care.

(3)  If each dwelling unit has direct access to an exterior exit facility leading to ground level, a fire alarm system is not required in an apartment building

(a)	in which not more than 4 dwelling units share a common means of egress, or

(b)	which is not more than 3 storeys in building height.

(4)  A fire alarm system is not required in a hotel 3 storeys or less in building height provided each suite has direct access to an exterior exit facility leading to ground level.

(5)  A fire alarm system is not required in a storage garage conforming to Article 3.2.2.83. provided there are no other occupancies in the building.

3.2.4.2.  Continuity of Fire Alarm System

(1)  If there are openings through a firewall, other than those for piping, tubing, wiring and totally enclosed noncombustible raceways, the requirements in this Subsection shall apply to the floor areas on both sides of the firewall as if they were in the same building.

(2)  Except as permitted by Sentence (4), if a building contains more than one major occupancy and a fire alarm system is required, a single system shall serve all occupancies.

(3)  Except as permitted by Sentence (4), if a fire alarm system is required in any portion of a building, it shall be installed throughout the building.

(4)  Except as required by Sentence (5), the requirements in this Subsection are permitted to be applied to each portion of a building not more than 3 storeys in building height, in which a vertical fire separation having a fire-resistance rating not less than 1 h separates the portion from the remainder of the building as if it were a separate building, provided there are no openings through the fire separation, other than those for piping, tubing, wiring and totally enclosed noncombustible raceways.

(5)  The permission in Sentence (4) to consider separated portions of a building as separate buildings does not apply to service rooms and storage rooms.

3.2.4.3.  Types of Fire Alarm Systems

(1)  A fire alarm system shall be

(a)	a single stage system in a Group F, Division 1 occupancy,

(b)	a 2 stage system in a Group B occupancy other than those described in Clause (c),

(c)	a single or 2 stage system in a building 3 storeys or less in building height which contains a Group B, Division 3 occupancy,

(d)	a single stage system in elementary and secondary schools, except for a special needs facility, and

(e)	a single or 2 stage system in all other cases.

3.2.4.4.  Description of Fire Alarm Systems

(1)  A single stage fire alarm system shall, upon the operation of any manual pull station or fire detector, cause an alarm signal to sound on all audible signal devices in the system.

(2)  A 2 stage fire alarm system shall

(a)	cause an alert signal to sound upon the operation of any manual pull station or fire detector,

(b)	except for a Group B, Division 2 occupancy, automatically cause an alarm signal to sound if the alert signal is not acknowledged within 5 min of its initiation,

(c)	have each manual pull station equipped so that the use of a key or other similar device causes an alarm signal to sound and continue to sound upon the removal of the key or similar device from the manual pull station, and

(d)	in a building containing a hotel

(i)	cause an alarm signal to sound in the initiating fire zone in the hotel, and

(ii)	cause an alert signal to sound throughout the hotel and such parts of the building as is necessary to alert hotel staff.

(3)  A 2 stage fire alarm system is permitted to be zone coded so that, upon the operation of any manual pull station or fire detector

(a)	a coded alert signal is sounded indicating the zone of alarm initiation,

(b)	the coded alert signal is repeated in its entirety not less than 4 times, and

(c)	a continuous alert signal is sounded upon completion of the coded signals referred to in Clause (b) and Sentence (4).

(4)  If a second manual pull station or fire detector is operated in a fire alarm system with zone coding as permitted by Sentence (3), in a zone other than that for which the first alert signal was sounded, the coded alert signal for the first zone shall be completed before the coded alert signal for the second zone is repeated not less than 4 times.

3.2.4.5.  Installation and Testing of Fire Alarm Systems

(1)  Fire alarm and voice communication systems shall be installed in conformance with CAN/ULC-S524-M, “Standard for the Installation of Fire Alarm Systems”.

(2)  A fire alarm system shall be tested in conformance with CAN/ULC-S537-M, “Standard for the Verification of Fire Alarm Systems”, to ensure satisfactory operation.

3.2.4.6.  Silencing of Alarm Signals

(1)  Except as permitted by Sentence (3), a fire alarm system shall be designed so that when an alarm signal is actuated, it cannot be silenced automatically before a period of time has elapsed that is not less than

(a)	5 min for a building not required to be equipped with an annunciator, and

(b)	20 min for any other building.

(2)  Except as permitted by Sentences 3.2.4.19.(9), and 3.2.4.22.(2) and (3), a fire alarm system shall not incorporate manual silencing switches other than those installed inside the fire alarm control unit.

(3)  Except as provided in Clause 3.2.4.22.(2)(a), in a care and treatment occupancy an alert signal is permitted to be silenced automatically after 1 min.

3.2.4.7.  Signals to Fire Department

(1)  If a fire alarm system is required to be installed and a single stage system is provided, the system shall be designed to notify the fire department in conformance with Sentence (4) that an alarm signal has been initiated in

(a)	a Group A occupancy having an occupant load more than 300,

(b)	a Group B occupancy,

(c)	a Group F, Division 1 occupancy,

(d)	a building regulated by the provisions of Subsection 3.2.6., or

(e)	a building containing interconnected floor space required to conform to Articles 3.2.8.3. to 3.2.8.11.

(2)  If a fire alarm system is installed, an automatic sprinkler system shall be designed to notify the fire department, in conformance with Sentence (4), that a waterflow switch has been actuated.

(3)  If a fire alarm system is required to be installed and a 2 stage system is provided, the system shall be designed to notify the fire department, in conformance with Sentence (4), that an alert signal has been initiated.

(4)  Except as permitted by Sentence (5), signals to the fire department shall be by way of

(a)	an independent central station conforming to NFPA-71, “Standard for the Installation, Maintenance, and Use of Signaling Systems for Central Station Service”,

(b)	a proprietary control centre conforming to Chapter 4 of NFPA-72, “Standard for the Installation, Maintenance, and Use of Protective Signaling Systems”,

(c)	a central station conforming to ULC/ORD-C693-1994, “Central Station Fire Protective Signaling Systems and Services”, or

(d)	the municipal fire alarm system.

(5)  If the facilities referred to in Sentence (4) are not available in the municipality in which the building is to be built, an independent system is permitted to be used to transmit signals to the fire department.

(6)  If a single stage fire alarm system or a local group of sprinklers has been installed and Sentence (1) does not require provision to transmit a signal to the fire department, a legible notice, that is not easily removed, shall be affixed to the wall near each manual pull station with wording that the fire department is to be notified in the event of a fire emergency and including the emergency telephone number for the municipality or the telephone number of the fire department.

3.2.4.8.  Annunciator and Zone Indication

(1)  Except as permitted in Sentences (3) to (5), an annunciator shall be installed in close proximity to a building entrance that faces a street or an access route for fire department vehicles that complies with Sentence 3.2.5.5.(1).

(2)  Except as permitted by Sentence (6), the annunciator required by Sentence (1) shall have separate zone indication of the actuation of the alarm initiating devices in each

(a)	floor area so that in a building that is not sprinklered, the area of coverage for each zone is neither more than

(i)	one storey, nor

(ii)	2 000 m2,

(b)	floor area so that in a building that is sprinklered, the area of coverage for each zone is neither more than

(i)	one storey, nor

(ii)	the system area limits as specified in NFPA 13, “Standard for the Installation of Sprinkler Systems”,

(c)	shaft required to be equipped with smoke detectors,

(d)	air handling system required to be equipped with smoke detectors,

(e)	contained use area,

(f)	impeded egress zone,

(g)	fire compartment required in Sentence 3.3.3.5.(2), and

(h)	fire compartment required to be separated by vertical fire separations having a fire-resistance rating not less than 2 h, other than dwelling units described in Subsection 3.3.4.

(3)  An annunciator need not be provided for a fire alarm system if not more than one zone indicator is required in Sentence (2).

(4)  If an annunciator is not installed as part of a fire alarm system in conformance with Sentence (1), a visual and audible trouble signal device shall be provided inside the main entrance of the building.

(5)  The requirements in Sentence (1) are waived in a building

(a)	Reserved

(b)	that has an aggregate area for all storeys of not more than 2 000 m2, and

(c)	that is not more than 3 storeys in building height.

(6)  The area limits of Clause (2)(a) are waived for an interior undivided open space used as an arena, a rink or a swimming pool provided that other spaces in the building that are separated from the open space are individually zoned in accordance with the requirements of Sentence (2).

(7)  Notwithstanding the requirements for an annunciator in this Article

(a)	all fire alarm systems shall include a main control unit to which all signal and supervision circuits shall report, either directly or by means of transponders, and

(b)	each annunciator or trouble signal device shall be connected to the main control unit.

(8)  Reserved

(9)  In a building containing a hotel in which a trouble signal sounding device has a silencing switch, a trouble light shall be installed in

(a)	the main reception area serving the hotel, or

(b)	another continually-supervised location.

(10)  In a nursing home, a remote audiovisual fire alarm trouble signal shall be located at the main nursing station.

3.2.4.9.  Electrical Supervision

(1)  Electrical supervision shall be provided for a fire alarm system.

(2)  If a fire alarm system is installed in a building, an automatic sprinkler system shall be electrically supervised to indicate a supervisory signal on the building fire alarm system annunciator for each of the following:

(a)	movement of a valve handle that controls the supply of water to sprinklers,

(b)	loss of excess water pressure required to prevent false alarms in a wet pipe system,

(c)	loss of air pressure in a dry pipe system,

(d)	loss of air pressure in a pressure tank,

(e)	a significant change in water level in any water storage container used for fire fighting purposes,

(f)	loss of power to any automatically starting fire pump, and

(g)	a temperature approaching the freezing point in any dry pipe valve enclosure or water storage container used for fire fighting purposes.

3.2.4.10.  Fire Detectors

(1)  Fire detectors required by this Article shall be connected to the fire alarm system.

(2)  Except as provided in Article 3.2.4.15., if a fire alarm system is required, fire detectors shall be installed in

(a)	storage rooms not within dwelling units,

(b)	service rooms not within dwelling units,

(c)	janitors’ rooms,

(d)	rooms in which hazardous substances are to be used or stored,

(e)	elevator and dumbwaiter shafts,

(f)	a laundry room in a building of residential occupancy, but not one within a dwelling unit, and

(g)	hazardous classrooms and change rooms in elementary and secondary schools.

3.2.4.11.  Smoke and Heat Detectors

(1)  If a fire alarm system is required, smoke detectors shall be installed in

(a)	each sleeping room and each corridor serving as part of a means of egress from sleeping rooms in portions of a building classified as Group B major occupancy,

(b)	each room in a contained use area and corridors serving those rooms,

(c)	each corridor in portions of a building classified as Group A, Division 1 major occupancy,

(d)	each public corridor in portions of a building classified as Group C major occupancy,

(e)	each exit stair shaft, and

(f)	Reserved

(g)	each corridor serving classrooms in elementary and secondary schools.

(2)  Except as provided in Article 3.2.4.15, if a fire alarm system is required, heat detectors shall be installed in

(a)	every room in portions of buildings classified as Group A, Division 1,

(b)	except in a hotel, in every suite, and every room not located within a suite, in portions of buildings classified as Group C major occupancy and more than 3 storeys in building height, and

(c)	in a floor area containing a hotel, in every room in a suite and in every room not located in a suite other than washrooms within a suite, saunas, refrigerated areas and swimming pools.

3.2.4.12.  Prevention of Smoke Circulation

(1)  If a fire alarm system is installed, an air handling system shall be designed to prevent the circulation of smoke upon a signal from a duct-type smoke detector if the air handling system

(a)	serves more than one storey,

(b)	serves more than one suite in a storey,

(c)	serves more than one fire compartment required by Sentence 3.3.3.5.(2), or

(d)	is not provided with fire dampers as permitted by Sentence 3.1.8.8.(8).

3.2.4.13.  Vacuum Cleaning System Shutdown

(1)  A central vacuum cleaning system in a building equipped with a fire alarm system shall be designed to shut down upon actuation of the fire alarm system.

3.2.4.14.  Elevator Emergency Return

(1)  Except as permitted by Sentence (3), in a building having elevators that serve storeys above the first storey and that are equipped with an automatic emergency recall feature, smoke detectors shall be installed in the elevator lobbies on the recall level so that when these smoke detectors are actuated, the elevators will automatically return directly to an alternate floor level.

(2)  Smoke detectors required by Sentence (1) shall be designed as part of the building fire alarm system.

(3)  The alternate floor recall feature required by Sentence (1) is not required if the floor area containing the recall level is sprinklered.

3.2.4.15.  Sprinklers in Lieu of Fire Detectors

(1)  Fire detectors required by Article 3.2.4.10. and heat detectors required by Sentence 3.2.4.11.(2) need not be provided within a floor area if the floor area is sprinklered and the sprinkler system is electrically supervised in conformance with Sentence 3.2.4.9.(2).

3.2.4.16.  System Monitoring

(1)  An automatic sprinkler system shall be equipped with waterflow detecting devices and, if an annunciator is required by Article 3.2.4.8., shall be installed so that each device serves

(a)	not more than one storey, and

(b)	an area on each storey that is not more than the system area limits as specified in NFPA 13, “Standard for the Installation of Sprinkler Systems”.

(2)  Waterflow detecting devices required by Sentence (1) shall be connected to initiate an alert signal or an alarm signal on the fire alarm system if a fire alarm is provided.

3.2.4.17.  Manual Pull Stations

(1)  Except as permitted by Sentences (2) and (3), if a fire alarm system is installed, a manual pull station shall be installed

(a)	near the principal entrance to the building, and

(b)	near every required exit.

(2)  In a building that is sprinklered, a manual pull station is not required at an exterior egress doorway from a suite that does not lead to an interior shared means of egress in a hotel not more than 3 storeys in building height, provided each suite is served by an exterior exit facility leading directly to ground level.

(3)  In a building that is sprinklered, a manual pull station is not required at an exterior egress doorway from a dwelling unit that does not lead to an interior shared means of egress in a building not more than 3 storeys in building height containing only dwelling units, provided each dwelling unit is served by an exterior exit facility leading directly to ground level.

(4)  In a building referred to in Sentences (2) or (3), manual pull stations shall be installed near doorways leading from shared interior corridors to the exterior.

(5)  In a building containing a hotel, a manual pull station shall be installed in the main reception area serving the hotel.

(6)  Except as permitted by Sentence (3), in Group C apartment buildings, if a pull station is not installed on a floor area in accordance with Sentences (1) or (4)

(a)	a manual pull station shall be installed in every dwelling unit in the floor area near each egress door leading from the dwelling unit,

(b)	smoke detectors shall be installed in the floor area in public corridors and stairwells, and

(c)	fire detectors shall be installed in the floor area in all common public areas and in rooms not located within dwelling units.

(7)  In floor areas where the manual pull stations are located in dwelling units, a legible sign stating FIRE ALARM PULL STATIONS LOCATED IN APARTMENT UNITS shall be posted near every exit in a public corridor.

(8)  Key switch activated pull stations are permitted in an impeded egress zone and a contained use area in Group B, Division 1 and Division 2 occupancies.

3.2.4.18.  Alert and Alarm Signals

(1)  In a 2 stage fire alarm system described in Sentence 3.2.4.4.(2), the same audible signal devices are permitted to be used to sound the alert signals and the alarm signals.

(2)  If audible signal devices with voice reproduction capabilities are intended for paging and similar voice message use, other than during a fire emergency, they shall be installed so that alert signals and alarm signals take priority over all other signals.

(3)  Audible signal devices forming part of a fire alarm or voice communication system shall not be used for playing music or background noise.

(4)  In a building or portion thereof intended for use primarily by persons with hearing impairment, visual signal devices shall be installed in addition to audible signal devices.

(5)  Visual signal devices are permitted to be installed in lieu of audible signal devices in the compartments referred to in Article 3.3.3.6.

3.2.4.19.  Audibility of Alarm Systems

(1)  Except as permitted in Sentence 3.2.4.18.(5), audible signal devices forming part of a fire alarm system shall be installed in a building so that alert signals and alarm signals are clearly audible throughout the floor area in which they are installed.

(2)  The temporal pattern of an alarm signal shall conform to the temporal pattern defined in Clause 4.2 of International Standard ISO 8201, “Acoustics — Audible emergency evacuation signal”.

(3)  The signals from smoke alarms and the patterns of alert signals shall be sufficiently different from the signals or patterns of alarm signals that there is no possibility of confusion.

(4)  In all normally occupied spaces, the fire alarm signal sound pressure level

(a)	shall be not more than 100 dBA when measured at a distance of 3 m from the device, or

(b)	is permitted to be more than 100 dBA provided the sound pressure level measured 2 000 mm above the floor level is not more than 100 dBA.

(5)  The sound pressure level in a sleeping room from a fire alarm audible signal device shall be not less than 75 dBA in a building of residential occupancy when any intervening doors between the device and the sleeping room are closed.

(6)  The sound pressure level from a fire alarm audible signal device in a floor area used for occupancies other than residential occupancies shall be not less than 10 dBA above the ambient noise level, but with a minimum value not less than 65 dBA.

(7)  Fire alarm audible signal devices shall be supplemented by visual signal devices in any floor area in which

(a)	the ambient noise level is more than 87 dBA, or

(b)	the occupants of the floor area

(i)	use ear protective devices,

(ii)	are located within an audiometric booth, or

(iii)	are located within sound insulated enclosures.

(8)  Sentence (7) shall also apply in an assembly occupancy in which music and other sounds associated with performances could exceed 100 dBA.

(9)  A fire alarm audible signal device located within a dwelling unit shall incorporate a means that enables the device to be silenced for a period of not more than 10 min, after which the device shall restore to normal operation.

(10)  A fire alarm audible signal device located within a dwelling unit or a suite of residential occupancy shall be connected to the fire alarm system in a manner that disconnection of, or damage to, that device will not interfere with the ability of devices in other dwelling units, public corridors, or suites to sound an alarm.

(11)  Reserved

(12)  Fire alarm audible signal devices shall be installed in a service space referred to in Sentence 3.2.1.1.(7) and shall be connected to the fire alarm system.

3.2.4.20.  Visual Signals

(1)  Visual signal devices required by Sentences 3.2.4.18.(4) and 3.2.4.19.(7) and (8) shall be installed so that the signal from at least one device is visible throughout the floor area or portion thereof in which they are installed.

(2)  In addition to the requirements for fire alarm and detection systems in this Subsection, visual signals from smoke detectors required in sleeping rooms of Group B occupancy shall be provided so that staff serving those rooms can easily identify the room or location of fire alarm initiation.

(3)  Visual signal devices permitted by Sentence 3.2.4.18.(5) shall be installed so that the signal from not less than one device is visible throughout the compartment in which they are installed.

3.2.4.21.  Smoke Alarms

(1)  Smoke alarms conforming to CAN/ULC-S531-M, “Standard for Smoke-Alarms”, shall be installed in each dwelling unit and, except for care or detention occupancies required to have a fire alarm system, in each sleeping room not within a dwelling unit.

(2)  At least one smoke alarm shall be installed on each storey and mezzanine of a dwelling unit.

(3)  On any storey of a dwelling unit containing sleeping rooms, a smoke alarm shall be installed in a location between the sleeping rooms and the remainder of the storey, and if the sleeping rooms are served by a hallway, the smoke alarm shall be located in the hallway.

(4)  A smoke alarm shall be installed on or near the ceiling.

(5)  A smoke alarm shall be installed with permanent connections to an electrical circuit and shall have no disconnect switches between the overcurrent device and the smoke alarm.

(6)  If more than one smoke alarm is required in a dwelling unit, the smoke alarms shall be wired so that the actuation of one smoke alarm will cause all smoke alarms within the dwelling unit to sound.

(7)  A smoke alarm required by Sentence (1) shall be installed in conformance with CAN/ULC-S553-M, “Standard for the Installation of Smoke-Alarms”.

(8)  A manually operated device is permitted to be incorporated within the circuitry of a smoke alarm installed in a dwelling unit so that it will silence the signal emitted by the smoke alarm for a period of not more than 10 min, after which the smoke alarm will reset and again sound the alarm if the level of smoke in the vicinity is sufficient to reactuate the smoke alarm.

3.2.4.22.  Voice Communication Systems

(1)  A voice communication system required by Subsection 3.2.6 or Clause 3.3.2.4. (11.2) (f) shall consist of

(a)	a 2-way communication system in each floor area, with connections to the central alarm and control facility and to the mechanical control centre, and

(b)	loudspeakers operated from the central alarm and control facility which are designed and located so as to be audible and the messages intelligible in all parts of the building, except that this requirement does not apply to elevator cars.

(2)  The voice communication system referred to in Sentence (1) shall include provision for silencing the alarm signal in a single stage fire alarm system when voice messages are being transmitted, but only after the alarm signal has sounded initially for not less than

(a)	30 s in Group B, Division 2 or 3 major occupancy, and

(b)	60 s in all other occupancies

(3)  The voice communication system referred to in Sentence (1) shall include provision for silencing the alert signal and the alarm signal in a 2 stage fire alarm system when voice messages are being transmitted, but only after the alert signal has sounded initially for not less than

(a)	30 s in Group B, Division 2 or 3 major occupancy, or

(b)	60 s for all other occupancies.

(4)  The voice communication system referred to in Clause (1)(b) shall be designed so that voice instructions can be transmitted selectively to any zone or zones while maintaining an alert signal or alarm signal to other zones in the building.

(5)  The 2-way communication system referred to in Clause (1)(a) shall be installed so that emergency telephones are located in each floor area near exit stair shafts.

3.2.5. Provisions for Fire-fighting

3.2.5.1.  Access to Above Grade Storeys

(1)  Except for storeys below the first storey, direct access for fire-fighting shall be provided from the outdoors to every storey that is not sprinklered and whose floor level is less than 25 m above grade, by at least one unobstructed window or access panel for each 15 m of wall in each wall required to face a street by Subsection 3.2.2.

(2)  An opening for access required by Sentence (1) shall

(a)	have a sill no higher than 900 mm above the inside floor, and

(b)	be not less than 1 100 mm high by not less than

(i)	550 mm wide for a building not designed for the storage or use of dangerous goods, or

(ii)	750 mm wide for a building designed for the storage or use of dangerous goods.

(3)  Access panels above the first storey shall be readily openable from both inside and outside, or the opening shall be glazed with plain glass.

3.2.5.2.  Access to Basements

(1)  Direct access from at least one street shall be provided from the outdoors to each basement

(a)	that is not sprinklered, and

(b)	that has horizontal dimension more than 25 m.

(2)  The access required by Sentence (1) is permitted to be provided by

(a)	doors, windows or other means that provide an opening not less than 1 100 mm high and 550 mm wide, with a sill no higher than 900 mm above the inside floor, or

(b)	an interior stairway immediately accessible from the outdoors.

3.2.5.3.  Roof Access

(1)  On a building more than 3 storeys in building height where the slope of the roof is less than 1 in 4, all main roof areas shall be provided with direct access from the floor areas immediately below, either by

(a)	a stairway, or

(b)	a hatch not less than 550 mm by 900 mm with a fixed ladder.

(2)  Clearance and access around roof signs or other obstructions shall provide

(a)	a passage not less than 900 mm wide by 1 800 mm high, clear of all obstructions except for necessary horizontal supports not more than 600 mm above the roof surface,

(i)	around every roof sign, and

(ii)	through every roof sign at locations not more than 15 m apart, and

(b)	a clearance of not less than 1 200 mm between any portion of a roof sign and any opening in the exterior wall face or roof of the building in which it is erected.

3.2.5.4.  Access Routes

(1)  A building which is more than 3 storeys in building height or more than 600 m2 in building area shall be provided with access routes for fire department vehicles

(a)	to the principal entrance, and

(b)	to each building face having access openings for fire-fighting as required by Articles 3.2.5.1. and 3.2.5.2.

3.2.5.5.  Location of Access Routes

(1)  Access routes required by Article 3.2.5.4. shall be located so that the principal entrance and every access opening required by Articles 3.2.5.1. and 3.2.5.2. are located not less than 3 m and not more than 15 m from the closest portion of the access route required for fire department use, measured horizontally from the face of the building.

(2)  Access routes shall be provided to a building so that

(a)	for a building provided with a fire department connection, a fire department pumper vehicle can be located adjacent to the hydrants referred to in Article 3.2.5.16.,

(b)	for a building not provided with a fire department connection, a fire department pumper vehicle can be located so that the length of the access route from a hydrant to the vehicle plus the unobstructed path of travel for the firefighter from the vehicle to the building is not more than 90 m, and

(c)	the unobstructed path of travel for the firefighter from the vehicle to the building is not more than 45 m.

(3)  The unobstructed path of travel for the firefighter required by Sentence (2) from the vehicle to the building shall be measured from the vehicle to the fire department connection provided for the building, except that if no fire department connection is provided, the path of travel shall be measured to the principal entrance of the building.

(4)  If a portion of a building is completely cut off from the remainder of the building so that there is no access to the remainder of the building, the access routes required by Sentence (2) shall be located so that the unobstructed path of travel from the vehicle to one entrance of each portion of the building is not more than 45 m.

3.2.5.6.  Access Route Design

(1)  A portion of a roadway or yard provided as a required access route for fire department use shall

(a)	have a clear width not less than 6 m, unless it can be shown that lesser widths are satisfactory,

(b)	have a centreline radius not less than 12 m,

(c)	have an overhead clearance not less than 5 m,

(d)	have a change of gradient not more than 1 in 12.5 over a minimum distance of 15 m,

(e)	be designed to support the expected loads imposed by fire fighting equipment and be surfaced with concrete, asphalt or other material designed to permit accessibility under all climatic conditions,

(f)	have turnaround facilities for any dead-end portion of the access route more than 90 m long, and

(g)	be connected with a public thoroughfare.

3.2.5.7.  Water Supply

(1)  An adequate water supply for fire-fighting shall be provided for every building.

(2)  Hydrants shall be located within 90 m horizontally of any portion of a building perimeter which is required to face a street in Subsection 3.2.2.

3.2.5.8.  Reserved

3.2.5.9.  Reserved

3.2.5.10.  Reserved

3.2.5.11.  Reserved

3.2.5.12.  Reserved

3.2.5.13.  Automatic Sprinkler Systems

(1)  Except as permitted by Sentences (2), (3) and (4), an automatic sprinkler system shall be designed, constructed, installed and tested in conformance with NFPA 13, “Standard for the Installation of Sprinkler Systems”.

(2)  Instead of the requirements of Sentence (1), NFPA 13R, “Standard for the Installation of Sprinkler Systems in Residential Occupancies up to and Including Four Storeys in Height”, is permitted to be used for the design, construction, installation and testing of an automatic sprinkler system installed in a building

(a)	of residential occupancy that is not more than 4 storeys in building height, or

(b)	of Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than 6 occupants requiring assistance in evacuation in case of an emergency.

(3)  Instead of the requirements of Sentence (1), NFPA 13D, “Standard for the Installation of Sprinkler Systems in One- and Two-Family Dwellings and Mobile Homes”, is permitted to be used for the design, construction, installation and testing of an automatic sprinkler system installed in a building of residential occupancy that contains not more than 2 dwelling units.

(4)  If a building contains fewer than 9 sprinklers, the water supply for these sprinklers is permitted to be supplied from the domestic water system for the building provided the required flow for the sprinklers can be met by the domestic system.

(5)  If a water supply serves both an automatic sprinkler system and a system serving other equipment, control valves shall be provided so that either system can be shut off independently.

(6)  Notwithstanding the requirements of the standards referenced in Sentences (1), (2) and (3) for the installation of automatic sprinkler systems, sprinklers shall not be omitted in any room or closet in the storey immediately below a roof assembly if the fire-resistance rating of the roof assembly is waived as permitted by Article 3.2.2.17.

(7)  Fast response sprinklers shall be installed in care or detention occupancies and in sprinklered residential occupancies.

(8)  Sprinklers in elevator machine rooms shall have a temperature rating not less than that required for an intermediate temperature classification and shall be protected against physical damage.

3.2.5.14.  Combustible Sprinkler Piping

(1)  Combustible sprinkler piping shall be used only for wet systems in residential occupancies and other light hazard occupancies.

(2)  Combustible sprinkler piping shall meet the requirements of ULC/ORD-199P-M, “Guide for the Investigation of Combustible Piping for Sprinkler Systems”.

(3)  Combustible sprinkler piping shall be separated from the area served by the sprinkler system and from any other fire compartment by ceilings, walls, or soffits consisting of, as a minimum

(a)	lath and plaster,

(b)	gypsum board not less than 9.5 mm thick,

(c)	plywood not less than 13 mm thick, or

(d)	a suspended membrane ceiling with

(i)	steel suspension grids, and

(ii)	lay-in panels or tiles having a mass not less than 1.7 kg/m2.

(4)  If combustible sprinkler piping is located above a ceiling, an opening through the ceiling that is not protected in conformance with Sentence (3) shall be located so that the distance between the edge of the opening and the nearest sprinkler is not more than 300 mm.

3.2.5.15.  Sprinklered Service Space

(1)  An automatic sprinkler system shall be installed in a service space referred to in Sentence 3.2.1.1.(7) if flooring for access within the service space is other than catwalks.

(2)  The sprinkler system required by Sentence (1) shall be equipped with waterflow detecting devices, with each device serving not more than one storey.

(3)  The waterflow detecting devices required by Sentence (2) shall be connected to the fire alarm system, to

(a)	initiate an alert signal in a 2 stage system or an alarm signal in a single stage system, and

(b)	indicate separately on the fire alarm system annunciator the actuation of each device.

(4)  If a building is sprinklered, sprinkler protection need not be provided in the space below a raised floor in a computer room

(a)	if the optical fibre cables and electrical wires and cables in this space conform to the test requirements in Article 3.1.5.20.,

(b)	if the building is of noncombustible construction and other combustible components are limited to those permitted in Subsection 3.1.5.,

(c)	if this space is used to circulate conditioned air and the air handling system is designed to prevent the circulation of smoke upon a signal from a smoke detector,

(d)	if all of this space is easily accessible by providing access sections or panels in the raised floor, and

(e)	if the computer room is more than 2 000 m2 and the annunciator has separate zone indicators of the actuation of smoke detectors located in this space so that the coverage for each zone is not more than 2 000 m2.

(5)  Where a room, chute or bin is required to be sprinklered as indicated in Sentence 3.3.4.3.(1), Article 3.6.2.6. and Sentence 3.6.3.3.(6), the sprinklers may be supplied with water from the fire standpipe system provided that

(a)	except for a chute, not more than 8 sprinkler heads are required to protect any room or bin based on a maximum coverage of 12 m2 per sprinkler head,

(b)	the standpipe riser is

(i)	not less than 6 in. in diameter, or

(ii)	hydraulically designed to meet combined water supply as specified in Clause (c),

(c)	the water supply for a standpipe system, pumping capability and water storage facility, if required, is increased to supply 95 L/min for each sprinkler head over and above the requirements for the standpipe system up to maximum 760 L/min for sprinklers,

(d)	a waterflow detecting device shall be installed in the sprinkler main adjacent to the point of connection to the standpipe riser, and

(e)	the activation of each waterflow detecting device in Clause (d) shall be indicated separately on the fire alarm system annunciator.

3.2.5.16.  Fire Department Connections

(1)  The fire department connection for a standpipe system shall be located so that the distance from the fire department connection to a hydrant is not more than 45 m and is unobstructed.

(2)  The fire department connection for an automatic sprinkler system shall be located so that the distance from the fire department connection to a hydrant is not more than 45 m and is unobstructed.

(3)  The fire department connections required in Sentences (1) and (2) shall be

(a)	located on the outside of a building adjacent to a street or an access route, not less than 300 mm and not more than 900 mm above ground level, and

(b)	provided with two 65 mm hose connections with female swivel hose couplings.

3.2.5.17.  Portable Fire Extinguishers

(1)  Portable fire extinguishers shall be installed in all buildings, except within dwelling units, in conformance with the provisions of Part 6 of the Ontario Fire Code made under the Fire Marshals Act.

(2)  In a Group B, Division 1 major occupancy, portable fire extinguishers are permitted to be located in secure areas, or in lockable cabinets provided

(a)	identical keys for all cabinets are located at all supervisory or security stations, or

(b)	electrical remote release devices are provided and are connected to an emergency power supply.

3.2.5.18.  Protection from Freezing

(1)  Equipment forming part of a fire protection system shall be protected from freezing if

(a)	it could be adversely affected by freezing temperatures, and

(b)	it is located in an unheated area.

3.2.5.19.  Fire Pumps

(1)  A fire pump having a rated net head pressure greater than 280 kPa shall be installed in accordance with the requirements of NFPA 20, “Standard for the Installation of Centrifugal Fire Pumps”.

3.2.6. Additional Requirements for High Buildings

3.2.6.1.  Application

(1)  This Subsection applies to a building

(a)	of Group A, D, E or F major occupancy classification that is more than

(i)	36 m high, measured between grade and the floor level of the top storey, or

(ii)	18 m high, measured between grade and the floor level of the top storey, and in which the cumulative or total occupant load on or above any storey above grade, other than the first storey, divided by 1.8 times the width in metres of all exit stairs at that storey, exceeds 300,

(b)	containing a Group B major occupancy in which the floor level of the highest storey of that major occupancy is more than 18 m above grade,

(c)	containing a floor area or part of a floor area located above the third storey designed or intended as a Group B, Division 2 or 3 occupancy, and

(d)	containing a Group C major occupancy whose floor level is more than 18 m above grade.

3.2.6.2.  Limits to Smoke Movement

(1)  Except as permitted in Sentence 3.2.6.6.(2), a building to which this Subsection applies shall be designed in accordance with Sentences (2) to (4) and Articles 3.2.6.3. to 3.2.6.7 to limit the danger to occupants and firefighters from exposure to smoke in a building fire.

(2)  Except as provided in Articles 3.2.6.4. to 3.2.6.6., a building referred to in Sentence (1), shall be designed so that, during a period of 2 h after the start of a fire, all floor areas that are above the lowest exit storey will not contain more than 1% by volume of contaminated air from the fire floor, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in conformance with Subsection 2.5.1.

(3)  Except as provided in Articles 3.2.6.4 and 3.2.6.6., a building referred to in Sentence (1), shall be designed so that during a period of 2 h after the start of a fire, the limit described in Sentence (2) on the movement of contaminated air into other floor areas is not exceeded in

(a)	each exit stair serving storeys above the lowest exit level, and

(b)	each exit stair serving storeys below the lowest exit level.

(4)  Except as provided in Articles 3.2.6.4. and 3.2.6.6., a building referred to in Sentence (1), shall be designed so that during a period of 2 h after the start of a fire, the limit described in Sentence (2) on the movement of contaminated air into other floor areas is not exceeded in a shaft that contains an elevator for use by firefighters required by Article 3.2.6.9.

3.2.6.3.  Areas of Refuge

(1)  In a building of Group C major occupancy classification, the requirements of Sentence 3.2.6.2.(2) are waived in buildings where occupants above the first storey can enter and be safely accommodated in floor areas or parts of floor areas that are designated as areas of refuge on the plans and are identified as such in the building.

(2)  Except as required in Sentence (3), the areas of refuge referred to in Sentence (1) shall be located on every fifth storey.

(3)  The areas of refuge referred to in Sentence (1) shall be located on every storey if the building is more than 75 m high, measured between grade and the floor level of the top storey.

(4)  The areas of refuge referred to in Sentence (1) shall

(a)	provide not less than 0.5 m2 of floor space per ambulatory occupant and 1.5 m2 of floor space per non-ambulatory occupant,

(b)	have access corridors and doors leading to each designated part of a floor area on the same storey sufficient to provide 3.67 mm of width for every person who may have to use these passages to reach the designated part of a floor area,

(c)	have access stairs from intervening storeys leading to each designated part of a floor area sufficient to provide 5.5 mm of width for every person who may have to use these stairs to reach the designated part of a floor area, and

(d)	not contain more than 1% by volume of contaminated air from the fire floor during a period of 2 h after the start of a fire, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in conformance with Subsection 2.5.1.

3.2.6.4.  Sprinklered Buildings

(1)  The requirements of Sentences 3.2.6.2.(2) and (4), and Clause 3.2.6.2.(3)(a) are waived when a building is sprinklered, and

(a)	the sprinkler system is equipped with a water flow and supervisory signal system that will

(i)	transmit automatically a waterflow signal directly to the fire department, or through an independent central station,

(ii)	transmit automatically other supervisory signals to a proprietary control centre or to an independent central station, and

(iii)	actuate a signal at the central alarm and control facility described in Article 3.2.6.12.,

(b)	each stairway that serves storeys above the lowest exit level is vented to the outdoors at or near the bottom of the stair shaft,

(c)	measures are taken to limit movement of smoke from a fire in a floor area below the lowest exit storey into upper storeys, and

(d)	except for exhaust fans in kitchens, washrooms and bathrooms in dwelling units, and except for fans used for smoke venting in Article 3.2.6.10., air moving fans in a system that serves more than 2 storeys shall be designed and installed so that in the event of a fire these fans can be stopped by means of a manually operated switch at the central alarm and control facility.

3.2.6.5.  Exception for Lower Buildings

(1)  The requirements of Sentence 3.2.6.2.(2) are waived in a building of Group C major occupancy classification where

(a)	the building is not more than 75 m high measured between grade and the floor level of the top storey, and

(b)	the number of occupants of storeys above grade is not more than 3.6 times the area in square metres of treads and landings in the exit stairs serving these storeys.

3.2.6.6.  Residential Buildings

(1)  The requirements of Sentences 3.2.6.2.(2) and (4) and Clause 3.2.6.2.(3)(a) are waived in a building of Group C major occupancy classification

(a)	where each suite above grade has direct access to an exterior balcony that

(i)	is not less than 1 500 mm deep from the outside face of the exterior wall to the inside edge of the balcony, and

(ii)	provides not less than 0.5 m2 of balcony space for each occupant of the suite,

(b)	where each stairway that serves storeys above the lowest exit level is vented to the outdoors at or near the bottom of the stair shaft,

(c)	where measures are taken to limit movement of smoke from a fire in a floor area below the lowest exit storey into upper storeys, and

(d)	where, except for exhaust fans in kitchens, washrooms and bathrooms in dwelling units, air moving fans are designed and installed so that in the event of a fire such fans can be stopped by means of a manually operated switch at the central alarm and control facility where the system serves more than 2 storeys.

(2)  The requirements of Sentences 3.2.6.2.(2) and (3) are waived in a Group C major occupancy apartment building.

3.2.6.7.  Connected Buildings

(1)  If a building described in Sentence 3.2.6.1.(1) is connected to any other building, measures shall be taken to limit movement of contaminated air from one building into another during a fire.

3.2.6.8.  Emergency Operation of Elevators

(1)  Manual emergency recall shall be provided for all elevators serving storeys above the first storey.

(2)  Key-operated switches for emergency recall described by Sentence (1) shall be provided in a conspicuous location at

(a)	each elevator lobby on the recall level, and

(b)	the central alarm and control facility required in Article 3.2.6.12.

(3)  In-car emergency service switches shall be provided in all elevator cars.

(4)  Keys to operate the switches required by Sentences (2) and (3) shall be

(a)	provided in a suitably identified box conspicuously located on the outside of an elevator hoistway near the central alarm and control facility required by Article 3.2.6.12., and

(b)	at the central alarm and control facility.

(5)  Automatic emergency recall operation shall be provided for all elevators serving storeys above the first storey in unsprinklered buildings.

(6)  The automatic emergency recall feature in Sentence (5) shall be actuated by

(a)	smoke detectors installed in each elevator lobby on each storey, or

(b)	the building fire alarm system.

(7)  Smoke detectors in Sentence (6) shall be designed as part of the building fire alarm system.

3.2.6.9.  Elevator for Use by Firefighters

(1)  At least one elevator shall be provided for use by firefighters in conformance with Sentences (2) to (6).

(2)  The elevator referred to in Sentence (1) shall have a usable platform area not less than 2.2 m2 and shall be capable of carrying a load of 900 kg to the top floor that it serves from a landing on the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. within 1 min.

(3)  Except when Measure K of the Supplementary Guidelines is used, each elevator for use by firefighters shall

(a)	be provided with a closure at each shaft opening so that the interlock mechanism remains mechanically engaged and electrical continuity is maintained in the interlock circuits and associated wiring is operational for a period of not less than 1 h when the assembly is subjected to the standard fire exposure described in CAN4-S104-M, “Standard Method for Fire Tests of Door Assemblies”,

(b)	be protected with a vestibule containing no occupancy and separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 45 min, or

(c)	be protected with a corridor containing no occupancy and separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(4)  Except as permitted in Sentence (5), an elevator referred to in Sentence (1) shall be capable of providing transportation from the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. to every floor that is above grade in the building and that is normally served by the elevator system.

(5)  If it is necessary to change elevators to reach any floor referred to in Sentence (4), the system shall be designed so that not more than one change of elevator is required when travelling to any floor in the building from the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5.

(6)  Electrical conductors for the operation of the elevator referred to in Sentence (1) shall be

(a)	installed in service spaces conforming to Section 3.6. that do not contain other combustible material, or

(b)	protected against exposure to fire from the service entrance of the emergency power supply, or the normal service entrance of the normal power supply, to the equipment served, to ensure operation for a period of 1 h when subjected to the standard fire exposure described in CAN4-S101-M, “Standard Methods of Fire Endurance Tests of Building Construction and Materials”.

3.2.6.10.  Venting to Aid Fire-fighting

(1)  Means of venting each floor area to the outdoors shall be provided by windows, wall panels or smoke shafts, except that in a sprinklered floor area, the floor area is permitted to be vented by the building exhaust system.

(2)  Venting described in Sentence (1) shall conform to the requirements in the Supplementary Guidelines.

(3)  Fixed glass windows shall not be used for the venting required by Sentence (1) if the breaking of the windows could endanger pedestrians below.

(4)  Openable windows used for the venting required by Sentence (1) shall be permanently marked so that they are easily identifiable.

(5)  Elevator hoistways shall not be designed for the venting required by Sentence (1).

3.2.6.11.  Reserved

3.2.6.12.  Central Alarm and Control Facility

(1)  A central alarm and control facility shall be provided on the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. in a location that

(a)	is readily accessible to firefighters entering the building, and

(b)	takes into account the effect of background noise likely to occur under fire emergency conditions, so that the facility can properly perform its required function under such conditions.

(2)  The central alarm and control facility required in Sentence (1) shall include

(a)	means to control the voice communication system required by Article 3.2.6.13., so that messages can be sent to

(i)	all loudspeakers simultaneously,

(ii)	to individual floor areas, and

(iii)	exit stairwells,

(b)	means to indicate audibly and visually alert signals and alarm signals and a switch to

(i)	silence the audible portion of these signals, and

(ii)	indicate visually that the audible portion has been silenced,

(c)	means to indicate visually that elevators are on emergency recall,

(d)	an annunciator conforming to Article 3.2.4.8.,

(e)	means to transmit alert signals and alarm signals to the fire department in conformance with Article 3.2.4.7.,

(f)	means to release hold-open devices on doors to vestibules,

(g)	means to manually actuate alarm signals in the building selectively to any zone or zones,

(h)	means to silence the alarm signals referred to in Clause (g) in conformance with Sentences 3.2.4.22.(2) and (3),

(i)	means, as appropriate to the measure for fire safety provided in the building, to

(i)	actuate auxiliary equipment, or

(ii)	communicate with a continually staffed auxiliary equipment control centre,

(j)	means to communicate with telephones in elevator cars, separate from connections to firefighters’ telephones, if elevator cars are required by the Elevating Devices Act to be equipped with a telephone,

(k)	means to indicate visually, individual sprinkler system waterflow signals,

(l)	means to indicate audibly and visually, sprinkler system supervisory signals,

(m)	a switch to silence the audible portion of a supervisory signal, and

(n)	visual indication that the audible portion of a supervisory signal has been silenced.

3.2.6.13.  Voice Communication System

(1)  A voice communication system or systems conforming to Article 3.2.4.22. shall be provided in a building if

(a)	the floor of the top storey, is more than 36 m above grade, or

(b)	a floor area or part of a floor area located above the third storey is designed or intended for use as a Group B, Division 2 or 3 occupancy.

3.2.6.14.  Protection of Electrical Conductors

(1)  Electrical conductors which supply power to emergency equipment described in Articles 3.2.6.2. to 3.2.6.8. and 3.2.6.10 to 3.2.6.13. and to the mechanical air supply required by Clause 3.3.3.6.(1)(b), shall be protected against exposure to fire in accordance with Sentence (4) and the protection shall extend from the main emergency power to

(a)	the equipment served,

(b)	the distribution equipment supplying power to the equipment served, where both are in the same room, or

(c)	the emergency equipment necessary to maintain the air supply required in Clause 3.3.3.6.(1)(b).

(2)  Where a fire alarm transponder is connected to, but located in a different room than, the central processing unit or other transponder, all wiring between the transponder and the central processing unit or the other transponder shall be protected against exposure to fire in accordance with Sentence (4).

(3)  Where a panelboard supplies power to emergency lighting required by Article 3.2.7.3., the supply conductors to the panelboard shall be protected against exposure to fire in accordance with Sentence (4).

(4)  To ensure continued operation for a period not less than that required by Subsection 3.2.7., the electrical conductors described in Sentences (1), (2) and (3)

(a)	shall be protected against fire exposure by a fire separation having a fire-resistance rating, or

(b)	shall meet the fire endurance tests when tested in accordance with ULC-S101, “Standard Methods of Fire Endurance Tests of Building Construction and Materials”.

(5)  Every fire alarm system control unit and transponder shall be installed in an electrical service room which does not contain other combustible material and which is separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

3.2.6.15.  Testing

(1)  The systems for control of smoke movement and mechanical venting required by Articles 3.2.6.2. and 3.2.6.10. shall be tested to ensure satisfactory operation in accordance with the procedures described in the Supplementary Guidelines.

3.2.7. Lighting and Emergency Power Systems

3.2.7.1.  Minimum Lighting Requirements

(1)  An exit, a public corridor, a corridor providing access to exit for the public, a corridor serving patients or residents in a Group B, Division 2 or Division 3 occupancy, a corridor serving classrooms, an electrical equipment room, a transformer vault and a hoistway pit shall be equipped to provide illumination to an average level not less than 50 lx at floor or tread level and at angles and intersections at changes of level where there are stairs or ramps.

(2)  Rooms and spaces used by the public shall be illuminated as described in Article 9.34.2.7.

(3)  Lighting outlets in a building of residential occupancy shall be provided in conformance with Subsection 9.34.2.

(4)  Elevator machine rooms shall be equipped to provide illumination to an average level of not less than 100 lx at floor level.

(5)  Every place of assembly intended for the viewing of motion pictures or the performing arts, shall be equipped to provide an average level of illumination at floor level in the aisles of not less than 2 lx during the viewing.

(6)  Every area where food is intended to be processed, prepared or manufactured and where equipment or utensils are intended to be cleaned shall be equipped to provide illumination to a level of not less than 500 lx measured at the floor level.

(7)  Every storage room, dressing room, sanitary facility, service area and corridor serving the areas in Sentence (6) shall be equipped to provide illumination to a level of not less than 300 lx measured at the floor level.

3.2.7.1.A.  Motion Sensors

(1)  Lighting installed to provide the minimum illumination levels required by this Part may be controlled by motion sensors except where the lighting

(a)	is installed in an exit,

(b)	is installed in a corridor serving patients or residents in a Group B, Division 2 or Division 3 occupancy, or

(c)	is required to conform to Sentence 3.2.7.1.(5).

(2)  Where motion sensors are used to control minimum lighting in a public corridor or corridor providing access to exit for the public, the motion sensors shall be installed with switch controllers equipped for fail-safe operation and illumination timers set for a minimum 15-minute duration.

(3)  A motion sensor shall not be used to control emergency lighting.

3.2.7.2.  Recessed Lighting Fixtures

(1)  A recessed lighting fixture shall not be located in an insulated ceiling unless the fixture is designed for this type of installation.

3.2.7.3.  Emergency Lighting

(1)  Emergency lighting shall be provided to an average level of illumination not less than 10 lx at floor or tread level in

(a)	exits,

(b)	Reserved

(c)	corridors used by the public,

(d)	corridors serving patients’ or residents’ sleeping rooms in a Group B, Division 2 or Division 3 occupancy,

(e)	corridors serving classrooms,

(f)	underground walkways,

(g)	public corridors,

(h)	floor areas or parts thereof where the public may congregate in

(i)	Group A, Division 1 occupancies, or

(ii)	Group A, Division 2 and 3 occupancies having an occupant load of 60 or more,

(i)	principal routes providing access to exit in a floor area that is not subdivided into rooms or suites of rooms served by corridors in a business and personal services occupancy, a mercantile occupancy or an industrial occupancy, and

(j)	internal corridors or aisles serving as principal routes to exits in a business and personal services occupancy, a mercantile occupancy or an industrial occupancy that is subdivided into rooms or suites of rooms, and is not served by a public corridor.

(2)  Emergency lighting to provide an average level of illumination of not less than 10 lx at floor or catwalk level shall be included in a service space referred to in Sentence 3.2.1.1.(7).

(3)  The minimum value of the illumination required by Sentences (1) and (2) shall be not less than 1 lx.

3.2.7.4.  Emergency Power for Lighting

(1)  An emergency power supply shall be

(a)	provided to maintain the emergency lighting required by this Subsection from a power source such as batteries or generators that will continue to supply power in the event that the regular power supply to the building is interrupted, and

(b)	so designed and installed that upon failure of the regular power it will assume the electrical load automatically for a period of

(i)	2 h for a building within the scope of Subsection 3.2.6.,

(ii)	1 h for a building of Group B major occupancy classification that is not within the scope of Subsection 3.2.6., and

(iii)	30 min for a building of any other occupancy.

(2)  If self-contained emergency lighting units are used, they shall conform to CSA C22.2 No. 141-M, “Unit Equipment for Emergency Lighting”.

3.2.7.5.  Emergency Power Supply Installation

(1)  Except as required by Articles 3.2.7.6. and 3.2.7.7., an emergency electrical power system shall be installed in conformance with CAN/CSA-C282-M, “Emergency Electrical Power Supply for Buildings”.

3.2.7.6.  Emergency Power for Hospitals

(1)  Except as required by Article 3.2.7.7., an emergency electrical power system for emergency equipment required by this Part for hospitals shall be installed in conformance with CAN/CSA-Z32.4-M, “Essential Electrical Systems for Hospitals”.

3.2.7.7.  Fuel Supply Shut-off Valves and Exhaust Pipes

(1)  If a liquid or gas fuel-fired engine or turbine for an emergency electric power supply is dependent on a fuel supply from outside the building, the fuel supply shall be provided with a suitably-identified separate shut-off valve outside the building.

(2)  Where pipes for exhaust gases from emergency power systems penetrate required fire separations, they shall be enclosed in a separate service space having a fire-resistance rating equal to that of the penetrated floor assembly, but not less than 45 min.

3.2.7.8.  Emergency Power for Fire Alarm Systems

(1)  An emergency power supply conforming to Sentences (2), (3) and (4) shall be provided for fire alarm systems.

(2)  The emergency power supply required by Sentence (1) shall be supplied from

(a)	a generator,

(b)	batteries, or

(c)	a combination thereof.

(3)  The emergency power supply required by Sentence (1) shall be capable of providing

(a)	supervisory power for not less than 24 h, and

(b)	immediately following, emergency power under full load for not less than

(i)	2 h for a building within the scope of Subsection 3.2.6.,

(ii)	1 h for a building classified as Group B major occupancy that is not within the scope of Subsection 3.2.6.,

(iii)	5 min for a building not required to be equipped with an annunciator, and

(iv)	30 min for any other building.

(4)  The emergency power supply required by Sentence (1) shall be designed so that there will be automatic transfer to emergency power in the event of a failure of the normal power source.

(5)  An emergency power supply shall be provided for the voice communication system required by Article 3.2.6.13.

(6)  The emergency power supply required by Sentence (5) for the voice communication system shall be capable of

(a)	full operation immediately upon the failure of the normal source of power, and

(b)	maintaining operation of the system for not less than 2 h.

(7)  If the emergency power supply required by Sentence (5) is provided by batteries, the batteries shall be sized to provide the total energy consumed by the maximum possible electrical supervision current plus the trouble signal current for a period of 24 h followed by 30 min of continuous voice communication.

3.2.7.9.  Emergency Power for Building Services

(1)  An emergency power supply capable of operating under a full load for not less than 2 h shall be provided by an emergency generator for

(a)	every elevator serving storeys above the first storey in a building that is more than 36 m high measured between grade and the floor level of the top storey and every elevator for firefighters in conformance with Sentence (2),

(b)	water supply for fire-fighting in conformance with Article 3.2.5.7., if the supply is dependent on electrical power supplied to the building, and the building is within the scope of Subsection 3.2.6.,

(c)	fans and other electrical equipment that are installed to maintain the air quality specified in Article 3.2.6.2., and

(d)	fans required for venting by Article 3.2.6.10.

(2)  Except as permitted by Sentence (3), the emergency power supply for elevators required by Clause (1)(a) shall be capable of operating all elevators for firefighters plus one additional elevator simultaneously.

(3)  Sentence (2) does not apply if the time to recall all elevators under emergency power supply is not more than 5 min, each from its most remote storey to

(a)	the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4 and 3.2.5.5., or

(b)	to a transfer lobby.

(4)  Except as provided by Sentence (5), an emergency power supply capable of operating under a full load for not less than 30 min shall be provided by emergency generator for water supply for fire-fighting in conformance with Article 3.2.5.7., if the supply is dependent on electrical power supplied to the building, and the building is not within the scope of Subsection 3.2.6.

(5)  Sentence (4) does not apply to the water supply for a standpipe system.

3.2.8. Mezzanines and Openings through Floor Assemblies

3.2.8.1.  Application

(1)  Except as permitted by Article 3.2.8.2. and Sentence 3.3.4.2.(3), the portions of a floor area or a mezzanine that do not terminate at an exterior wall, a firewall or a vertical shaft shall

(a)	terminate at a vertical fire separation having a fire-resistance rating not less than that required for the floor assembly and extending from the floor assembly to the underside of the floor or roof assembly above, or

(b)	be protected in conformance with the requirements of Articles 3.2.8.3. to 3.2.8.11.

(2)  The penetration of a floor assembly by an exit or a vertical service space shall conform to the requirements of Sections 3.4., 3.5. and 3.6.

(3)  A floor area containing sleeping rooms in a building of Group B, Division 2 or 3 major occupancy shall not be constructed as part of an interconnected floor space.

(4)  Except as permitted in Sentence (5), an elementary or secondary school shall not

(a)	contain an interconnected floor space, or

(b)	be located in an interconnected floor space.

(5)  An interconnected floor space is permitted in an elementary or secondary school provided

(a)	the interconnected floor space consists of the first storey, and the storey next above or below it, but not both,

(b)	the interconnected floor space is sprinklered,

(c)	the portions of the upper floor area that do not terminate at an exterior wall, a firewall or a vertical shaft shall terminate at a vertical fire separation extending from the floor assembly to the underside of the floor or roof assembly above,

(d)	except as provided in Clause (e), the fire separation required in Clause (c) need not have a fire-resistance rating,

(e)	where a corridor is located immediately adjacent to the fire separation required in Clause (c), the fire separation shall have a fire-resistance rating of not less than 30 min, and

(f)	where a portion of a floor area is not within the interconnected floor space, the required access to exit from this portion of the floor area shall not lead through the interconnected floor space.

3.2.8.2.  Exceptions to Special Protection

(1)  A mezzanine need not terminate at a vertical fire separation nor be protected in conformance with the requirements of Articles 3.2.8.3. to 3.2.8.11. provided the mezzanine

(a)	serves a Group A, Division 1 major occupancy,

(b)	serves a Group A, Division 3 major occupancy in a building not more than 2 storeys in building height, or

(c)	is not considered as a storey in Sentences 3.2.1.1.(3) or 3.2.1.1.(5) in calculating building height provided

(i)	every point on the mezzanine is within 25 m of a point or points on the mezzanine perimeter from which, in the aggregate, an occupant may view 60% of the area of the room or storey in which the mezzanine is located, and

(ii)	the mezzanine does not contain a Group B occupancy,

(d)	is not considered a storey in Sentence 3.2.1.1.(4) in calculating building height provided the mezzanine is not more than 500 m2 in area and does not contain a Group B occupancy, or

(e)	is not considered a storey in calculating building height in Sentence 3.2.1.1.(8).

(2)  Except for floors referred to in Sentence 3.1.10.3.(1) and Article 3.2.1.2., openings through a horizontal fire separation for vehicular ramps in a storage garage are not required to be protected with closures and need not conform to this Subsection.

(3)  If a closure in an opening in a fire separation would disrupt the nature of a manufacturing process, such as a continuous flow of material from storey to storey, the closure for the opening is permitted to be omitted provided precautions are taken to offset the resulting hazard.

(4)  An interconnected floor space in a Group B, Division 1 occupancy need not conform to the requirements of Articles 3.2.8.3. to 3.2.8.11. provided the interconnected floor space does not interconnect more than 2 adjacent storeys.

(5)  Except as permitted by Sentence (6), openings for stairways, escalators and inclined moving walks need not conform to the requirements in Articles 3.2.8.3. to 3.2.3.11. provided

(a)	the opening for each stairway, escalator or walk does not exceed 10 m2,

(b)	the building is sprinklered throughout, and

(c)	the interconnected floor space contains only Group A, Division 1, 2 or 3, Group D or Group E occupancies.

(6)  An interconnected floor space need not conform to the requirements of Articles 3.2.8.3. to 3.2.8.11. provided

(a)	the interconnected floor space consists of the first storey and the storey next above or below it, but not both,

(b)	the interconnected floor space is sprinklered, and

(c)	the interconnected floor space contains only Group A, Division 1, 2 or 3, Group D, Group E, or Group F, Division 3 occupancies.

3.2.8.3.  Configuration

(1)  In buildings constructed in conformance with Articles 3.2.8.4. to 3.2.8.11., the unprotected openings through floor assemblies in an interconnected floor space shall be of sufficient size and shall be positioned relative to each other so as to be capable of containing, within the full height of the interconnected floor space, a cylinder conforming to Sentence (2).

(2)  The cylinder referred to in Sentence (1) shall have a cross-section that, where taken at a right angle to the longitudinal axis of such cylinder, is

(a)	a circle at least 9 m in diameter, or

(b)	an ellipse at least 7 m wide along the minor axis and at least 65 m2 in area.

3.2.8.4.  Exits

(1)  A building that is more than 18 m in height, measured between grade and the floor level of the top storey, and that contains an interconnected floor space, shall be designed to limit the passage of smoke from a fire into exit stairshafts opening into an interconnected floor space so that during a 2 h period after the start of fire, such stairshafts will not contain more than 1% by volume of contaminated air from the fire floor, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis.

(2)  Where a building containing an interconnected floor space is more than 75 m in height, measured between grade and the floor level of the top storey, the exit stairshaft protection required in Sentence (1) shall be accomplished by the provision, between each floor area and each exit stairshaft, of a vestibule provided with a mechanical air supply or with a vent opening to the outdoors.

(3)  Where a vestibule protecting an exit stairshaft is incorporated into the design of the building to meet the requirements of Sentences (1) or (2), such vestibule shall

(a)	be designed so that each doorway for a door opening into the vestibule is located at least 1 800 mm from a door or doors opening outward from the vestibule,

(b)	be separated from the remainder of the floor area by a fire separation having a fire-resistance rating at least equal to that required for the exit which it serves except that the fire-resistance rating of a fire separation between the vestibule and a public corridor need not exceed 45 min, and

(c)	not have a door or doors opening into more than one exit stairshaft.

(4)  Except where exits serving the floor area are at ground level, the increased travel distance to exits permitted by Clause 3.4.2.5.(1)(c) shall not apply to a floor area within an interconnected floor space.

(5)  Where a portion of a floor area is not within an interconnected floor space, required access to exit from such portion of a floor area shall not lead through an interconnected floor space.

(6)  Except as provided in Sentences (7) and (8), portions of an interconnected floor space that have floor levels more than 18 m above grade shall be served by exits that provide at least 0.3 m2 of area of treads, landings and floor surface for each occupant of such portions of an interconnected floor space.

(7)  The requirements of Sentence (6) need not be applied where a floor area that is a portion of an interconnected floor space and that has a floor level more than 18 m above grade is separated from the remainder of the interconnected floor space by a fire separation having a fire-resistance rating of at least 1 h, except that no fire-resistance rating is required for such fire separation where all of the major occupancies contained within the interconnected floor space may be classified as light hazard occupancies in conformance with Appendix A of NFPA 13 “Standard for the Installation of Sprinkler Systems”.

(8)  The requirements of Sentence (6) need not be applied where the exit stairs that serve interconnected floor spaces are designed so that the required width of each stair is cumulative.

3.2.8.5.  Elevators

(1)  Except as provided in Sentence (2), where an elevator shaft opens into an interconnected floor space and into storeys that are above such space and that have floor levels more than 18 m above grade, either the elevator doors opening into the interconnected floor space or the elevator doors opening into the storeys above the interconnected floor space shall be protected by vestibules that

(a)	are designed to restrict the passage of contaminated air to the limit described in Sentence 3.2.8.4.(1), and

(b)	conform to the requirements of Sentence 3.2.8.4.(3).

(2)  Where elevator doors opening into an interconnected floor space are protected by vestibules in conformance with Sentence (1), the elevator doors opening into the lowest storey of the interconnected floor space need not be protected by such vestibules.

3.2.8.6.  Group B Sleeping Rooms

(1)  Openings provided for access between an interconnected floor space and a building or a portion of a building containing Group B major occupancy sleeping rooms shall be provided with vestibules that are provided with a mechanical air supply and that are designed

(a)	to restrict the passage of smoke from the interconnected floor space into the area containing sleeping rooms in accordance with the limits described in Sentence 3.2.8.4.(1), and

(b)	in conformance with Clause 3.2.8.4.(3)(a).

3.2.8.7.  Sprinklers

(1)  In a building containing an interconnected floor space, storeys that are wholly or partially within an interconnected floor space and all storeys below an interconnected floor space shall be sprinklered.

(2)  In a building containing an interconnected floor space

(a)	waterflow alarm signals from sprinkler systems shall be transmitted to the fire department in conformance with Sentence 3.2.4.7.(4), and

(b)	sprinkler systems shall be electrically supervised as required in Sentence 3.2.4.9.(2).

3.2.8.8.  Fire Alarm and Detection System

(1)  A building containing an interconnected floor space shall be provided with

(a)	a fire alarm system and electrically supervised annunciator conforming to Subsection 3.2.4.,

(b)	a system of smoke detectors located

(i)	on the ceiling of each storey in the vicinity of the openings through floor assemblies described in Article 3.2.8.3., except within dwelling units, heat detectors may be installed instead of smoke detectors, and

(ii)	as required for the activation of the smoke control system described in Sentences (5), (6) and (7) of Article 3.2.8.9., and

(c)	facilities for transmitting a signal to the fire department in conformance with Article 3.2.4.7.

3.2.8.9.  Smoke Control

(1)  A smoke control system conforming to Sentences (2) to (8) shall be designed to control the movement of smoke within a building containing an interconnected floor space.

(2)  The design of the smoke control system shall assume an outdoor temperature equal to the January design temperature on a 2.5% basis.

(3)  Upon activation of the sprinkler system or automatic detection of smoke by at least two smoke detectors in a single zone within an interconnected floor space, the system shall

(a)	stop air moving fans which provide for the normal exhausting or re-circulating of air in an interconnected floor space,

(b)	activate exit stairshaft protection required in Article 3.2.8.4.,

(c)	activate elevator protection required in Article 3.2.8.5., and

(d)	activate the vestibule air supply required in Sentence 3.2.8.6.(1).

(4)  A building containing an interconnected floor space may be designed so that, in the event of a fire arising in a floor area or part of a floor area within the interconnected floor space, automatic detection of such fire will activate air handling equipment that

(a)	extracts air directly from such floor area or part of a floor area at the rate of at least 6 air changes per hour, and

(b)	supplies air in sufficient quantities and at appropriate locations to prevent smoke from passing out of such floor area into other portions of the interconnected floor space.

(5)  For purposes of Sentences (6) and (7), the volume of an interconnected floor space need not include the aggregate volume of those floor areas or portions of floor areas designed to have zoned air extraction in accordance with Sentence (4).

(6)  A mechanical exhaust shall be provided to remove air at the top of an interconnected floor space at the rate of at least 6 air changes per hour, except that where the volume of the interconnected floor space exceeds 17 000 m3, only 4 air changes per hour need be provided.

(7)  Except where zoned mechanical exhaust described in Sentence (4) has been activated, upon automatic detection of smoke within the volume of the interconnected floor space, the mechanical exhaust described in Sentence (6) shall be automatically activated and supply air shall be provided in sufficient quantity and at appropriate locations to allow a consistent rate of removal of smoke throughout the volume of the interconnected floor space.

(8)  Overriding manual controls for the smoke control system shall be provided for fire department use at an acceptable location in the vicinity of the fire alarm annunciator.

3.2.8.10.  Emergency Power Supply

(1)  In a building that is more than 18 m in height, measured between grade and the floor level of the top storey, an emergency power supply capable of operating under a full load for at least 2 h shall be provided by an emergency generator or by a separate service not supplied by the same substation as the primary source for fans required for smoke control purposes in Articles 3.2.8.4., 3.2.8.5., 3.2.8.6. and 3.2.8.9.

3.2.8.11.  Testing

(1)  The systems for smoke control and venting described in Articles 3.2.8.4., 3.2.8.5., 3.2.8.6. and 3.2.8.9. shall be tested to ensure satisfactory operation.

3.2.9. Standpipe Systems

3.2.9.1.  Where Required

(1)  Except as provided in Sentences (4) to (7), a standpipe system shall be installed in every building that

(a)	is more than 3 storeys in building height,

(b)	is more than 14 m high measured between grade and the ceiling of the top storey, or

(c)	is not more than 14 m high measured between grade and the ceiling of the top storey but has a building area exceeding the area shown in Table 3.2.9.1. for the applicable building height if the building is not sprinklered.

(2)  A standpipe system shall be installed in every basement of a building that requires a standpipe system above grade.

(3)  A standpipe system shall be installed in every basement of a building that is regulated by Sentence 3.2.2.15.(2).

(4)  A standpipe system is not required to be installed in the lowest storey in a building if this storey is a service room which has an area not more than 50 m2.

(5)  A standpipe system is not required to be installed in a roof-top enclosure if this enclosure has an area not more than 50 m2.

Table 3.2.9.1.

Building Limits without Standpipe Systems

Forming Part of Sentence 3.2.9.1.(1)

| Occupancy Classification | Building Area, m2 |  |  |
| --- | --- | --- | --- |
|  | 1 Storey | 2 Storeys | 3 Storeys |
| A | 2 500 | 2 000 | 1 500 |
| C | 2 000 | 1 500 | 1 000 |
| D | 4 000 | 3 000 | 2 000 |
| F, Division 2 | 2 000 | 1 500 | 1 000 |
| F, Division 3 | 3 000 | 2 000 | 1 000 |
| Column 1 | 2 | 3 | 4 |

(6)  A standpipe system is not required to be installed in a storage garage conforming to Article 3.2.2.83. provided the building is not more than 15 m high.

(7)  A standpipe system is not required to be installed in a dwelling unit which

(a)	extends not more than 3 storeys above adjacent ground level,

(b)	is completely cut off from the remainder of the building so that there is no access to the remainder of the building, and

(c)	has direct access to its interior by means of an exterior doorway located not more than 1 500 mm above or below adjacent finished ground level.

3.2.9.2.  Standpipe System Design

(1)  Except as otherwise provided in this Subsection, if a standpipe system is required, the design, construction, installation and testing of the system shall be in conformance with NFPA 14, “Standard for the Installation of Standpipe and Hose Systems”.

(2)  A dry standpipe that is not connected to a water supply shall not be considered as fulfilling the requirements of this Article.

(3)  If more than one standpipe is provided, the total water supply need not be more than 30 L/s.

(4)  The residual water pressure at the design flow rate at the hydraulically most remote hose connection of a standpipe system that is required to be installed in a building is permitted to be less than 450 kPa provided that

(a)	the building is sprinklered,

(b)	the water supply at the base of the sprinkler riser is capable of meeting the design flow rate and pressure demand of the sprinkler system, including the inside and outside hose allowance, and

(c)	fire protection equipment is available to deliver, by means of the fire department connection, the full demand flow rate at a residual water pressure of 450 kPa at the hydraulically most remote hose connection of the standpipe system.

(5)  A fire department connection shall be provided for every standpipe system.

(6)  Pumps required to have a rated net head pressure greater than 280 kPa and their controllers shall be listed and labelled.

(7)  Couplings for hoses or other fittings used in connection with such couplings shall conform to ULC-S513, “Standard for Threaded Couplings for 38 mm and 65 mm Fire Hose” or ULC-S543, “Standard for Internal Lug Quick Connect Couplings for Fire Hose”.

(8)  If freezing of piping may occur, a dry standpipe system may be provided and so arranged through the use of listed devices to

(a)	automatically admit water to the system by opening of a hose valve, and

(b)	transmit a signal to an attended location.

(9)  A standpipe riser shall be located in

(a)	an exit stair shaft, or

(b)	a service space.

3.2.9.3.  Hose Connections

(1)  If a standpipe system is required in a building, 38 mm diam hose connections shall be provided in each storey in the building.

(2)  In addition to the requirements in Sentence (1),if a standpipe system is required, 65 mm diam hose connections shall be installed in each storey in the building if the building

(a)	is more than 25 m high, measured between grade and the ceiling of the top storey, or

(b)	has a building area of more than 4 000 m2.

3.2.9.4.  Hose Stations

(1)  If a standpipe system is required in a building, hose stations shall be provided in each storey in the building.

(2)  Each hose station shall be equipped with a hose rack filled with not more than 30 m of 38 mm diam fire hose and the hose rack and fire hose shall be

(a)	listed, or

(b)	approved by the Factory Mutual Research Corporation.

(3)  Except in a Group F occupancy, at each hose station, hose connections, valves, fire hose, nozzle and hose rack shall be in a hose cabinet.

(4)  A hose cabinet referred to in Sentence (3) shall be of sufficient size to

(a)	contain the equipment referred to in Sentence (3),

(b)	contain a listed fire extinguisher, and

(c)	provide sufficient clearance to permit the use of a standard fire department hose key.

(5)  Hose stations shall be located

(a)	so that every portion of the building can be reached by a hose stream and is within 3 m of a nozzle attached to the hose required in Sentence (2),

(b)	not more than 5 m from every required exit serving a floor area, except

(i)	for the first storey, or

(ii)	if additional hose stations are required to achieve full coverage of the floor area, and

(c)	in a conspicuous location where they are not likely to be obstructed.

(6)  Except as permitted in Sentence (7), hose stations shall be located so that it is not necessary to penetrate an exit with a hose in order to provide the design coverage required in Clause (5)(a).

(7)  A hose is permitted to penetrate an exit in order to provide the required coverage to

(a)	a service room referred to in Sentence 3.2.9.1.(4),

(b)	a roof-top enclosure referred to in Sentence 3.2.9.1.(5),

(c)	a room not more than 50 m2 in area, or

(d)	a room or group of rooms not more than 200 m2 in area in a sprinklered floor area.

(8)  A hose station located on one side of a horizontal exit shall be considered to serve only the floor area on that side of the horizontal exit.

(9)  A hose cabinet shall be located so that its door, when fully opened, will not obstruct the required width of a means of egress.

(10)  A hose station in a Group B, Division 1 major occupancy is permitted to be located in a secure area, or in a lockable cabinet provided that

(a)	identical keys for all cabinets are located at all guard stations, or

(b)	electrical remote release devices are provided and are connected to an emergency power supply.

3.2.9.5.  Supervisory Signal Annunciation for Valves

(1)  If a fire alarm system in a building is required to have an annunciator by Sentence 3.2.4.8.(1), except for hose valves, each valve controlling water supplies in a standpipe system shall be equipped with an electrically supervised switch for transmitting a signal for individual annunciation in the event of movement of the valve handle.

3.2.9.6.  Water Supply for 38 mm Hose Connections

(1)  If a standpipe and hose system is required, the water supply shall be sufficient to provide a flow, measured at each of the two hydraulically most remote 38 mm diam hose connections

(a)	of not less than 380 L/min,

(b)	for not less than 30 min,

(c)	at a pressure of not less than 450 kPa, and

(d)	of not less than 190 L/min from each of the two outlets simultaneously.

3.2.9.7.  Water Supply for 65 mm Hose Connections

(1)  If 65 mm diam hose connections are required, the water supply shall be sufficient to provide a flow, measured at each of the two hydraulically most remote 65 mm diam hose connections

(a)	of not less than 1 890 L/min,

(b)	for not less than 30 min,

(c)	at a pressure of not less than 450 kPa, and

(d)	of not less than 945 L/min from each of the two outlets simultaneously.

(2)  If the building is less than 84 m high, measured between grade and the ceiling level of the top storey, the water supply required in Sentence (1) is permitted to be supplied through the fire department connection.

(3)  If the building is 84 m or more high, measured between grade and the ceiling level of the top storey, the water supply required in Sentence (1) shall be provided by sufficient pumping capacity.

(4)  If the building is 84 m or more high, measured between grade and the ceiling level of the top storey, the building shall be served by not less than two sources of water supply from a public water system.

Section 3.3. Safety within Floor Areas

3.3.1. All Floor Areas

3.3.1.1.  Separation of Suites

(1)  Except as permitted by Sentences (2) and (3), each suite in other than business and personal services occupancies shall be separated from adjoining suites by a fire separation having a fire-resistance rating not less than 1 h.

(2)  The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(3)  Occupancies that are served by public corridors conforming to Sentence 3.3.1.4.(5) in a building that is sprinklered, are not required to be separated from one another by fire separations provided the occupancies are

(a)	suites of business and personal services occupancy,

(b)	fast food vending operations that do not provide seating for customers, and

(c)	suites of mercantile occupancy.

3.3.1.2.  Hazardous Substances, Equipment and Processes

(1)  If hazardous substances are used in connection with the activities of any occupancy other than as permitted by Subsection 3.3.5. for a high hazard industrial occupancy, the storage, handling and use of the hazardous substances shall be in conformance with

(a)	the Ontario Fire Code, or

(b)	the National Fire Code of Canada 1995, in the absence of regulations referred to in Clause (a).

(2)  Cooking equipment, not within a dwelling unit, used in processes producing grease-laden vapours shall be designed and installed in conformance with Part 6.

(3)  A fuel-fired appliance shall not be installed in a corridor serving as an access to exit.

3.3.1.3.  Means of Egress

(1)  Access to exit within floor areas shall conform to Subsections 3.3.2. to 3.3.5., in addition to the requirements of this Subsection.

(2)  If a podium, terrace, platform or contained open space is provided, egress requirements shall conform to the appropriate requirements of Sentence 3.3.1.5.(1) for rooms and suites.

(3)  Means of egress shall be provided from every roof which is intended for occupancy, and from every podium, terrace, platform or contained open space.

(4)  If a roof is used or intended for an occupant load more than 60, at least 2 separate means of egress shall be provided from the roof to stairs

(a)	designed in conformance with the requirements for exit stairs, and

(b)	located so that the distance between the stairs conforms to the requirements of Article 3.4.2.3. for exits.

(5)  A rooftop enclosure shall be provided with an access to exit that leads to an exit

(a)	at the roof level, or

(b)	on the storey immediately below the roof.

(6)  A rooftop enclosure which is more than 200 m2 in area shall be provided with at least 2 means of egress.

(7)  Two points of egress shall be provided for a service space referred to in Sentence 3.2.1.1.(7) if

(a)	the area is more than 200 m2, or

(b)	the travel distance measured from any point in the service space to a point of egress is more than 25 m.

(8)  Except as permitted by Sentences 3.3.4.4.(6) and (7), each suite in a floor area that contains more than one suite shall have

(a)	an exterior exit doorway, or

(b)	a doorway

(i)	into a public corridor, or

(ii)	to an exterior passageway.

(9)  Except as permitted by this Section and by Sentence 3.4.2.1.(2), at the point where a doorway referred to in Sentence (8) opens onto a public corridor or exterior passageway, it shall be possible to go in opposite directions to each of 2 separate exits.

(10)  Means of egress for a below ground service room which is not normally occupied, is permitted to be provided by stairways or fixed ladders.

3.3.1.4.  Public Corridor Separations

(1)  Except as otherwise required by this Part or permitted by Sentences (2) to (7), a public corridor shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(2)  The fire-resistance rating of a fire separation between a public corridor and the remainder of a floor area is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(3)  If a floor area is sprinklered, no fire-resistance rating is required for a fire separation between a public corridor and the remainder of the floor area provided the corridor does not serve a care or detention occupancy or a residential occupancy.

(4)  If a floor area is sprinklered, no fire separation is required between a public corridor and the remainder of the floor area provided the public corridor

(a)	is more than 5 m in unobstructed width, and

(b)	does not serve

(i)	a care or detention occupancy, or

(ii)	a residential occupancy.

(5)  If a floor area is sprinklered, no fire separation is required between a room or a suite and a public corridor that serves it provided the public corridor complies with Sentence 3.3.1.9.(6).

(6)  A floor assembly of a public corridor above a crawl space that conforms to Sentence 3.2.2.9.(2) is not required to be a fire separation.

(7)  If a floor area is sprinklered, no fire separation is required between a public corridor and a room containing water closets and lavatories provided the room and the public corridor are separated from the remainder of the floor area by a fire separation that has a fire-resistance rating not less than that required between the public corridor and the remainder of the floor area.

(8)  The sprinkler system in Sentences (3), (4), (5) and (7) shall be electrically supervised in conformance with Sentence 3.2.4.9.(2) and, upon operation, shall cause a signal to be transmitted to the fire department in conformance with Sentence 3.2.4.7.(4) when the corridor serves a Group E or Group F, Division 1 or 2 occupancy.

3.3.1.5.	 Egress Doorways

(1)  Except for dwelling units, a minimum of 2 egress doorways located so that one doorway could provide egress from the room or suite as required by Article 3.3.1.3. if the other doorway becomes inaccessible to the occupants due to a fire which originates in the room or suite, shall be provided for every room and every suite

(a)	whose area is more than 15 m2 and is used for

(i)	a high hazard industrial occupancy, or

(ii)	a hazardous room,

(b)	intended for an occupant load more than 60,

(c)	in a floor area that is not sprinklered, and

(i)	the area of a room or suite is more than the value in Table 3.3.1.5.A., or

(ii)	the travel distance within the room or suite to the nearest egress doorway, is more than the value in Table 3.3.1.5.A.,

(d)	in a floor area that is sprinklered and does not contain a high hazard industrial occupancy and

(i)	the travel distance to an egress doorway is more than 25 m, or

(ii)	the area of the room or suite is more than the value in Table 3.3.1.5.B., or

(e)	where the area of the room is more than 100 m2 and it is a hazardous classroom in elementary or secondary school.

Table 3.3.1.5.A.

Egress in Floor Area not Sprinklered

Forming Part of Sentence 3.3.1.5.(1)

| Occupancy of Room or Suite | Maximum Area of Room or Suite, m2 | Maximum Distance to Egress Doorway, m |
| --- | --- | --- |
| Group A | 150 | 15 |
| Group C | 150(1) | 25(1) |
| Group D | 200 | 25 |
| Group E | 200 | 25 |
| Group F, Division 2 | 200 | 25 |
| Group F, Division 3 | 200 | 25 |
| Column 1 | 2 | 3 |

Note to Table 3.3.1.5.A.:

(1) See Article 3.3.4.4. for dwelling units.

Table 3.3.1.5.B.

Egress in Floor Area Sprinklered

Forming Part of Sentence 3.3.1.5.(1)

| Occupancy of Room or Suite | Maximum Area of Room or Suite, m2 |
| --- | --- |
| Group A | 200 |
| Group B, Division 1 | 100 |
| Group B, Division 2 or 3 |  |
| sleeping rooms | 100 |
| other than sleeping rooms | 200 |
| Group C | 150(1) |
| Group D | 300 |
| Group E | 200 |
| Group F, Division 2 | 200 |
| Group F, Division 3 | 300 |
| Column 1 | 2 |

Note to Table 3.3.1.5.B.:

(1) See Article 3.3.4.4. for dwelling units.

(2)  Except for a mezzanine within a dwelling unit, every mezzanine that is not required to terminate at a vertical fire separation in Article 3.2.8.2. shall have 2 egress facilities placed in such a manner that one facility could provide egress from the mezzanine if the other facility becomes inaccessible to the occupants of the mezzanine due to a fire which might originate in the room or suite in which the mezzanine is located where

(a)	the occupancy of the mezzanine, room or suite is classified as Group F, Division 1,

(b)	the mezzanine is intended for an occupant load of more than 60 persons,

(c)	in a floor area that is not sprinklered,

(i)	the area of a mezzanine is more than the value in Table 3.3.1.5.A., or

(ii)	the travel distance to an egress doorway or an egress facility is more than the value in Table 3.3.1.5.A., or

(d)	in a floor area that is sprinklered,

(i)	the travel distance to an egress doorway or an egress facility is more than 25 m, or

(ii)	the area of the mezzanine is more than the value in Table 3.3.1.5.B.

(3)  For the purpose of Clause (2)(c) and Clause 2(d)

(a)	if the room or suite in which the mezzanine is located is permitted to have one egress doorway, the travel distance is measured from any point on the mezzanine to that doorway, or

(b)	if the room or suite in which the mezzanine is located is required to have more than one egress doorway, the travel distance is measured from any point on the mezzanine to the nearest egress facility leading from the mezzanine.

(4)  Except for a mezzanine which is not considered as a storey in calculating building height in Sentence 3.2.1.1.(4), where the space below a mezzanine is enclosed, an egress facility from the mezzanine shall not lead into the enclosed space.

3.3.1.6.  Travel Distance

(1)  If more than one egress doorway is required from a room or suite referred to in Article 3.3.1.5., the travel distance within the room or suite to the nearest egress doorway shall not exceed the maximum travel distances specified in Clauses 3.4.2.5.(1)(a), (b), (c) and (f) for exits.

3.3.1.7.  Protection on Floor Areas with a Barrier-Free Path of Travel

(1)  Except as provided in Sentences (2) and (3), every floor area above or below the first storey that has a barrier-free path of travel shall

(a)	be served by an elevator

(i)	conforming to Sentences 3.2.6.9.(4) to (6),

(ii)	protected against fire in conformance with Clauses 3.2.6.9.(3)(b) or (c), and

(iii)	in a building over 3 storeys in building height, protected against smoke movement so that the hoistway will not contain more than 1% by volume of contaminated air from a fire floor during a period of 2 h after the start of a fire, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in conformance with Subsection 2.5.1., or

(b)	be divided into at least 2 zones by fire separations conforming to Sentences (4), (5) and (6) so that

(i)	persons with physical disabilities can be accommodated in each zone,

(ii)	the travel distance from any point in one zone to a doorway leading to another zone shall be not more than the value for travel distance permitted by Sentence 3.4.2.5.(1) for the occupancy classification of the zone, and

(iii)	a barrier-free path of travel is provided to an exit.

(2)  In residential occupancies, the requirements of Sentence (1) are waived if a balcony conforming to Sentence (7) is provided for each suite, except for suites on the storey containing the barrier-free entrance described in Article 3.8.1.2.

(3)  The requirements of Sentences (1) and (2) are waived when the building is sprinklered.

(4)  Except as permitted by Sentence (5), the fire separations referred to in Clause (1)(b) shall have a fire-resistance rating not less than 1 h.

(5)  The fire-resistance rating of the fire separations referred to in Clause (1)(b) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(6)  A door acting as a closure in a fire separation referred to in Clause (1)(b) shall be weatherstripped or otherwise designed and installed to retard the passage of smoke.

(7)  A balcony required by Sentence (2) shall

(a)	Reserved

(b)	be not less than 1500 mm deep from the outside face of the exterior wall to the inside edge of the balcony, and

(c)	provide not less than 0.5 m2 for each occupant of the suite.

3.3.1.8.  Headroom Clearance

(1)  Except within the floor area of a storage garage, the minimum headroom clearance in every access to exit shall conform to the requirements of Article 3.4.3.6. for exits.

3.3.1.9.  Corridors

(1)  The minimum width of a public corridor shall be 1 100 mm.

(2)  Except as required by Sentences 3.3.3.3.(2) and (3), the minimum unobstructed width shall be 1 100 mm for every

(a)	corridor used by the public,

(b)	corridor serving classrooms, and

(c)	corridor in a Group B, Division 2 or 3 occupancy where the corridor

(i)	serves a service room,

(ii)	serves an administrative area,

(iii)	will not be used by non-ambulatory outpatients, or

(iv)	will not be used by non-ambulatory residents.

(3)  Except as permitted by Sentence (4), obstructions located within 1 980 mm of the floor shall not project more than 100 mm horizontally in a manner that would create a hazard for a person with a visual disability travelling adjacent to the walls in

(a)	an exit passageway,

(b)	a public corridor,

(c)	a corridor used by the public,

(d)	a corridor serving classrooms, or

(e)	a corridor serving patients’ or residents’ sleeping rooms in a Group B, Division 2 or Division 3 occupancy.

(4)  The horizontal projection of an obstruction referred to in Sentence (3) is permitted to be more than 100 mm provided the clearance between the obstruction and the floor is less than 680 mm.

(5)  If a public corridor, a corridor used by the public, a corridor serving classrooms or a corridor serving patients’ or residents’ sleeping rooms in a Group B, Division 2 or Division 3 occupancy, contains an occupancy, the occupancy shall not reduce the unobstructed width of the corridor to less than its required width.

(6)  If a public corridor conforming to Clause 3.4.2.5.(1)(d) contains an occupancy

(a)	the occupancy shall be located so that for pedestrian travel there is an unobstructed width not less than 3 m at all times adjacent and parallel to all rooms and suites that front onto the public corridor, and

(b)	the combined area of all occupancies in the public corridor shall be not more than 15% of the area of the public corridor.

(7)  Except as provided in Sentence 3.3.3.3.(1), a dead end corridor shall conform to Sentences (8) to (14).

(8)  A dead end corridor is permitted in an assembly occupancy where there is a second and separate egress doorway from each room or suite not leading into a dead end corridor.

(9)  In a residential occupancy, except for corridors served by a single exit as described in Sentence 3.3.4.4.(7), a dead end public corridor is permitted provided it is not more than 6 m long.

(10)  Dead end corridors in Sentence (9) shall contain no door openings to service rooms containing fuel-fired appliances or rooms which may be considered a hazard.

(11)  A dead end public corridor is permitted in a business and personal services occupancy where

(a)	the dead end corridor

(i)	serves an occupant load of not more than 30 persons,

(ii)	is not more than 9 m long, and

(iii)	is provided with doors having self-closing devices, or

(b)	there is a second and separate egress doorway from each room or suite not leading into a dead end corridor.

(12)  A dead end corridor is permitted in a mercantile occupancy where

(a)	the dead end corridor

(i)	serves an occupant load of not more than 30 persons,

(ii)	is not more than 9 m long, and

(iii)	is provided with doors having self-closing devices, or

(b)	there is a second and separate egress doorway from each room or suite not leading into a dead end corridor.

(13)  A dead end corridor is permitted in a low or medium hazard industrial occupancy where

(a)	the dead end corridor

(i)	serves an occupant load of not more than 30 persons,

(ii)	is not more than 9 m long, and

(iii)	is provided with doors having self-closing devices, or

(b)	there is a second and separate egress doorway from each room or suite not leading into a dead end corridor.

(14)  A dead end corridor is permitted in a high hazard industrial occupancy where there is a second and separate egress doorway from each room or suite not leading into a dead end corridor.

3.3.1.10.  Door Swing

(1)  Except as permitted by Article 3.3.1.11., a door that opens into a corridor or other facility providing access to exit from a suite, or a room not located within a suite, shall swing on a vertical axis.

(2)  Except as permitted by Article 3.3.1.11., a door that opens into a corridor or other facility providing access to exit from a room or suite shall swing in the direction of travel to the exit if the room or suite is used or intended for

(a)	an occupant load more than 60,

(b)	a high hazard industrial occupancy, or

(c)	a hazardous classroom in an elementary or secondary school.

(3)  Every door that divides a corridor that is not wholly contained within a suite shall swing on a vertical axis in the direction of travel to the exit where the corridor provides access to exit for

(a)	an occupant load more than 60,

(b)	a high hazard industrial occupancy,

(c)	a hazardous classroom in an elementary or secondary school, or

(d)	a Group B, Division 2 or 3 occupancy.

(4)  If a pair of doors is installed in a corridor that provides access to exit in both directions, the doors shall swing in opposite directions, with the door on the right hand side swinging in the direction of travel to the exit.

3.3.1.11.  Sliding Doors

(1)  Except as permitted by Sentence (2), a sliding door provided in the locations described in Article 3.3.1.10. shall

(a)	be designed and installed to swing on the vertical axis in the direction of travel to the exit when pressure is applied, and

(b)	be identified as a swinging door by means of a label or decal affixed to it.

(2)  In a Group B, Division 1 occupancy, or in an impeded egress zone in other occupancies, sliding doors used in an access to exit need not conform to Sentence (1) and Article 3.3.1.10.

(3)  Movable partitions used to separate a public corridor from an adjacent business and personal services occupancy or a mercantile occupancy need not conform to Sentence (1) and Sentences 3.3.1.10.(1) and (2) provided the partitions are not located in the only means of egress.

3.3.1.12.  Doors and Door Hardware

(1)  A door that opens into or is located within a public corridor or other facility that provides access to exit from a suite shall

(a)	provide a clear opening of not less than 800 mm if there is only one door leaf,

(b)	in a doorway with multiple leaves, have the active leaf providing a clear opening of not less than 800 mm, and

(c)	not open onto a step.

(2)  A door in an access to exit shall be readily openable in travelling to an exit without requiring keys, special devices or specialized knowledge of the door opening mechanism, except that this requirement does not apply to a door serving a contained use area, or an impeded egress zone, provided the locking devices conform to Sentence (6).

(3)  Except as permitted by Sentence (4), door release hardware shall be operable by one hand and the door shall be openable with not more than one releasing operation.

(4)  An egress door from an individual dwelling unit or from a suite of residential occupancy is permitted to be provided with additional devices that require a releasing operation additional to the main door release hardware, provided the devices are readily operable from the inside without the use of keys, special devices or specialized knowledge.

(5)  Door release hardware shall be installed not more than 1 200 mm above the finished floor.

(6)  An egress door in an access to exit serving a contained use area or an impeded egress zone is permitted to be equipped with locking devices that can be released either locally or remotely in conformance with Sentence (7) or Sentence (8).

(7)  Local locking devices permitted by Sentence (6) shall be operable by a key from both sides of the door.

(8)  Controls for the remote release of door locking devices permitted by Sentence (6) shall be located in an area readily available to security personnel.

(9)  Locking devices permitted by Sentence (6) that are electrically operated shall be

(a)	designed to operate on emergency power, and

(b)	capable of manual release by security personnel.

(10)  A door in an access to exit is permitted to be equipped with an electromagnetic locking device conforming to Sentence 3.4.6.15.(4), except that this permission does not apply to a door

(a)	in an elementary or secondary school,

(b)	a door leading from a Group F, Division 1 occupancy, or

(c)	except as provided in Sentence (10.1), requiring a latch release device by Article 3.3.2.6.

(10.1)  A door in an access to exit in a gaming premise is permitted to be equipped with an electromagnetic locking device conforming to Sentences 3.4.6.15.(4) and (6.1).

(11)  Except as required in Article 3.3.3.4., in a Group B, Division 2 or 3 occupancy, every door that opens into or is located within a corridor or other facility that provides access to exit shall comply with Sentences (1) and (2) where the door

(a)	serves a service room,

(b)	serves an administrative area,

(c)	will not be used by non-ambulatory outpatients,

(d)	is located within a patient’s or resident’s sleeping room, or

(e)	is in a nursing home or home for the aged which will accommodate only ambulatory residents.

3.3.1.13.  Ramps and Stairways

(1)  Except as permitted by Sentence (2), Article 3.3.4.7., and Subsection 3.3.2., ramps and stairways shall conform to the dimensional, guard and handrail requirements in Section 3.4. for exit ramps and stairways.

(2)  Ramps and stairways that do not conform to the requirements of Sentence (1) are permitted to serve service rooms and service spaces and in industrial occupancies, provided the ramps and stairways are intended only for occasional use for servicing equipment and machinery.

3.3.1.14.  Exterior Passageways

(1)  An exterior passageway leading to a required exit shall conform to the requirements of Section 3.4. for exterior exit passageways.

3.3.1.15.  Curved or Spiral Stairs

(1)  A curved or spiral stair is permitted in a stairway not required as an exit provided the stair has

(a)	treads with

(i)	a minimum run not less than 150 mm, and

(ii)	an average run not less than 200 mm, and

(b)	risers in conformance with Sentence 3.4.6.7.(2).

3.3.1.16.  Capacity of Access to Exits

(1)  The capacity of an access to exit shall be based on the occupant load of the portion of the floor area served.

(2)  In an access to exit the required width of ramps with a slope not more than 1 in 8, doorways, and corridors shall be based on not less than 6.1 mm per person.

(3)  In an access to exit the required width of a ramp with a slope more than 1 in 8 shall be based on not less than 9.2 mm per person.

(4)  In an access to exit from a floor area used or intended to be used for patients or residents in a Group B, Division 2 or Division 3 occupancy, the required width of corridors, doorways, and ramps shall be based on not less than 18.4 mm per person.

(5)  The capacity of stairs in an access to exit shall conform to the requirements for stairs in Article 3.4.3.4.

3.3.1.17.  Guards

(1)  Except for the front edges of stages, floor pits in repair garages and loading docks, a guard not less than 1 070 mm high shall be provided

(a)	around each roof to which access is provided for other than maintenance,

(b)	at openings into smoke shafts referred to in Subsection 3.2.6. that are less than 1 070 mm above the floor, and

(c)	at each raised floor, mezzanine, balcony, gallery, interior or exterior vehicular ramp, and at other locations where the difference in level is more than 600 mm.

(2)  Except as provided in Sentence (3) and Sentence 3.3.2.8.(4), openings through any guard which is required by Sentence (1) shall be of a size which will prevent the passage of a sphere having a diameter more than 100 mm unless it can be shown that the location and size of openings which exceed this limit do not represent a hazard.

(3)  Openings through any guard which is required by Sentence (1) and which is installed in a building of industrial occupancy shall be of a size which will prevent the passage of a sphere having a diameter more than 200 mm unless it can be shown that the location and size of openings which exceed this limit do not represent a hazard.

(4)  Openings through any guard which is not required by Sentence (1) and which serves a building of other than industrial occupancy, shall be of a size which

(a)	will prevent the passage of a sphere having a diameter more 100 mm, or

(b)	will permit the passage of a sphere having a diameter more than 200 mm unless it can be shown that the location and size of openings which exceed these limits do not represent a hazard.

(5)  Unless it can be shown that the location and size of openings do not present a hazard, a guard shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above the level protected by the guard will facilitate climbing.

3.3.1.18.  Transparent Doors and Panels

(1)  Except for dwelling units and as permitted by Sentence (4), a glass or transparent door shall be designed and constructed so that the existence and position of the door is readily apparent, by attaching non-transparent hardware, bars or other permanent fixtures to it.

(2)  A glass door shall be constructed of

(a)	laminated or tempered safety glass conforming to CAN/CGSB-12.1-M, “Tempered or Laminated Safety Glass”, or

(b)	wired glass conforming to CAN/CGSB-12.11-M, “Wired Safety Glass”.

(3)  Except as permitted by Sentence (4), transparent panels used in an access to exit which, because of their physical configuration or design, could be mistaken as a means of egress shall be made inaccessible by barriers or railings.

(4)  Sliding glass partitions which separate a public corridor from an adjacent occupancy and which are intended to be open during normal working hours need not conform to Sentences (1) and (3), provided the partitions are suitably marked to indicate their existence and position.

(5)  Glass in doors and in sidelights that could be mistaken for doors, within or at the entrances to dwelling units and in public areas, shall conform to the requirements of Article 9.6.6.2.

(6)  A window in a public area that extends to less than 1 070 mm above the floor and is located above the second storey in a building of residential occupancy, shall be protected by a barrier or railing from the floor to not less than 1 070 mm above the floor, or the window shall be non-openable and designed to withstand the lateral design loads for balcony guards required by Article 4.1.10.1.

3.3.1.19.  Exhaust Ventilation

(1)  An exhaust ventilation system designed in conformance with the appropriate requirements of Part 6 shall be provided in a building or part of a building in which dust, fumes, gases, vapour or other impurities or contaminants have the potential to create a fire or explosion hazard.

(2)  Explosion relief devices, vents or other protective measures conforming to Subsection 6.2.2. shall be provided for a space in which substances or conditions that have the potential to create an explosion hazard are present as a result of the principal use of a building.

3.3.1.20.  Janitors’ Rooms

(1)  Except as permitted by Sentences (2) and (3), a room or space within a floor area for the storage of janitorial supplies shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(2)  The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(3)  The fire separation required by Sentence (1) is not required to have a fire-resistance rating if the floor area in which the room or space is located is sprinklered.

3.3.1.21.  Common Laundry Rooms

(1)  Except as permitted by Sentences (2) and (3), in a building of residential occupancy, a laundry room in a floor area that is not within a dwelling unit shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(2)  The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(3)  The fire separation required by Sentence (1) is not required to have a fire-resistance rating if the floor area in which the laundry room is located is sprinklered.

3.3.1.22.  Obstructions

(1)  No obstruction shall be permitted in any occupancy that would restrict the width of a normal means of egress from any part of a floor area to less than 750 mm unless an unobstructed alternative means of egress is provided adjacent to, accessible from, and plainly visible from the obstructed means of egress.

3.3.1.23.  Signs in Service Spaces

(1)  Illuminated signs conforming to Sentences 3.4.5.1.(3) and (5) shall be provided to indicate the direction to egress points in a service space referred to in Sentence 3.2.1.1.(7).

3.3.1.24.  Welding and Cutting

(1)  If a room in other than an industrial major occupancy is used for welding and cutting operations, it shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h, except that this requirement does not apply to a room that is protected by an automatic fire extinguishing system.

3.3.2. Assembly Occupancy

3.3.2.1.  Scope

(1)  This Subsection applies to floor areas or parts thereof used or intended for use as assembly occupancies.

3.3.2.2.  Fire Separations

(1)  Except as permitted by Sentence (2), the seating area of a Group A, Division 1 occupancy shall be separated from adjacent occupancies in the floor area by a fire separation having a fire-resistance rating not less than 1 h if the occupant load in the seating area exceeds 200.

(2)  The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(3)  If usable space exists under tiers of seats in arena type buildings, a fire separation with a fire-resistance rating not less than 45 min shall be provided between the space and the seats or the space shall be sprinklered.

(4)  Except as required in Sentences (5), (6) and (7), in an elementary or secondary school, a hazardous classroom shall be separated from the remainder of the building by a fire-separation having a fire-resistance rating not less than

(a)	1 h where the building is not sprinklered, or

(b)	30 min where the building is sprinklered.

(5)  Except as provided in Sentence (6), in an elementary or secondary school, a hazardous classroom containing an auto repair shop shall be separated from the remainder of the building by a fire-separation having a fire-resistance rating not less than

(a)	2 h where the building is not sprinklered, or

(b)	1 h where the building is sprinklered.

(6)  In an elementary or secondary school, if there is a group of hazardous classrooms or a group of hazardous classrooms and ancillary rooms of a complementary use, the fire separation required by Sentence (4) or (5) need not be provided within the group but the fire separation is required between the group and the remainder of the building.

(7)  In an elementary or secondary school, a hazardous classroom containing a spray painting operation shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than

(a)	2 h, or

(b)	1 h where the spray painting operation is separated from the classroom by a fire-separation having a fire-resistance rating not less than 1 h.

(8)  Except as required in Sentence (9), in an elementary or secondary school, where the occupant load of a room exceeds 200 persons, the room and any ancillary rooms of a complementary use shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than

(a)	1 h where the building is not sprinklered, or

(b)	30 min where the building is sprinklered.

(9)  A kitchen shall not be located within the fire compartment required in Sentence (8).

3.3.2.3.  Fixed Seats

(1)  Except for the requirements of Article 3.3.2.7. for bench-type seats and except as required or permitted by Sentence (2) and Articles 3.3.2.9. and 3.3.2.10., fixed seats in places of assembly shall be

(a)	attached or secured to the floor, platform or platform riser,

(b)	provided with arms and back, and

(c)	arranged in rows having an unobstructed passage not less than 400 mm wide measured horizontally between plumb lines from the backs of the seats in one row and the edges of the furthest forward projection of the seats in the next row in the unoccupied position.

(2)  For fixed seats with backs and with folding tablet arms, the value of 400 mm required by Clause (1)(c) shall be measured when the tablet arms are in the use position, but is permitted to be measured in the stored position provided

(a)	there are not more than 7 seats between any seat and the nearest aisle,

(b)	the seats are located in a lecture hall or an auditorium used for instructional purposes, and

(c)	the tablet arm, when raised manually to a vertical position, falls by the force of gravity to the stored position.

(3)  Except as permitted by Sentences (4) and (5), aisles shall be located so that there are not more than 7 seats with backs or 20 seats without backs between any seat and the nearest aisle.

(4)  The requirements of Sentence (3) do not apply if

(a)	egress doorways are provided to serve both ends of rows of seats,

(b)	each doorway referred to in Clause (a) serves not more than 3 rows of seats, and

(c)	each row contains not more than 100 seats.

(5)  The requirements of Sentence (3) do not apply if

(a)	there are not more than 7 seats between any seat and the nearest aisle, where the seats are served by a single aisle,

(b)	there are not more than 20 seats between any seat and the nearest aisle, where the seats are served by two aisles,

(c)	each row has an unobstructed passage with minimum width of 400 mm plus 6.1 mm for each additional seat above 16 seats in the row, and

(d)	the travel distance is not more than 45 m measured along the path of travel from any seat to an exit or to an egress doorway.

(6)  Seating arrangements that do not conform to the requirements of Sentences (3) to (5) are permitted provided the standard of safety is not reduced and the time required for egress is not increased.

3.3.2.4.  Aisles

(1)  Except as required by Articles 3.3.2.7., 3.3.2.9. and 3.3.2.10., aisles leading to egress doors or exits shall be provided in conformance with Sentences (2) to (24) in places of assembly which contain fixed seats.

(2)  In this Subsection, a converging aisle is an aisle into which the occupants of 2 or more aisles converge in travelling to an exit.

(3)  An aisle shall terminate at

(a)	a converging aisle,

(b)	an egress doorway from the seating area, or

(c)	an exit from the seating area.

(4)  A converging aisle shall terminate at

(a)	an egress doorway from the seating area, or

(b)	an exit from the seating area.

(5)  The minimum clear width of aisles shall be not less than 1 100 mm, except that the width is permitted to be reduced to not less than

(a)	750 mm if serving not more than 60 seats, and

(b)	900 mm if serving seats on one side only.

(6)  The minimum clear width of each aisle shall be measured at the point in the aisle furthest from

(a)	an egress doorway referred to in Clause (12)(a),

(b)	an exit referred to in Clause (12)(b), or

(c)	an exit referred to in Sentence (13).

(7)  Except for an aisle serving bleacher seats, where rows of seats discharge into an aisle, the minimum clear width required by Sentence (6) shall be increased by 25 mm for each metre of length of the aisle measured in the direction towards an exit.

(8)  The width of a converging aisle shall be not less than the required width of the widest aisle plus 50% of the total required width of the remaining aisles that it serves.

(9)  If rows of seats discharge directly into the converging aisle, the width required by Sentence (8) shall be increased by 25 mm for each metre of length of the aisle where the rows of seats discharge into the aisle.

(10)  The width of an egress doorway or an exit leading directly from the seating area shall be not less than the required width of the widest aisle or converging aisle plus 50% of the total required width of the remaining aisles and converging aisles that it serves.

(10.1)  The requirements in Sentences (5) to (10) and Sentence (14) do not apply if

(a)	the minimum clear width of an aisle is in accordance with Article 3.3.1.16., but is not less than 900 mm if serving seats on one side only,

(b)	the minimum clear width of an aisle is in accordance with Article 3.3.1.16., but is not less than 1 200 mm if serving seats on both sides,

(c)	the minimum clear width of a converging aisle is in accordance with Article 3.3.1.16., but not less than the width of the widest aisle leading to the converging aisle,

(d)	the minimum clear width of an exit leading directly from the seating area is in accordance with Article 3.4.3.4.,

(e)	except as provided in Clause (f), the minimum clear width of an egress doorway leading directly from the seating area is in accordance with Article 3.3.1.16., but not less than the required width of the aisle or the converging aisle leading to the doorway, and

(f)	if more than one vomitory is provided

(i)	the minimum total clear width of the egress doorways leading from one vomitory is not less than the required width of the aisle or the converging aisle leading to the doorways, and

(ii)	the minimum clear width of egress doorways from additional vomitories is in accordance with Article 3.3.1.16.

(11)  Except as provided in Sentences (11.1) and (11.2), dead-end aisles shall be not more than 6 m long.

(11.1)  Dead-end aisles are permitted to be more than 6 m long, but not more than 10 m long if

(a)	the seating area is separated from other seating areas and adjacent occupancies, including a corridor serving any seating area, by a fire separation in accordance with Sentences 3.3.2.2. (1) and (2),

(b)	the travel distance is not more than 25 m measured along the path of travel from any seat to an exit, to an egress doorway or to an opening into a vomitory,

(c)	at least one means of egress, comprising not less than 30% of the required exit capacity, is through an exterior exit, an exit stairway or a corridor not containing an occupancy,

(d)	each row served by the dead-end aisle has a minimum unobstructed width of 400 mm plus 6.1 mm for each additional seat above 7 seats in a row, but not more than 550 mm,

(e)	the minimum ceiling height above the seating area is 3 m,

(f)	the activation of a fire detector or a sprinkler head in the seating area will

(i)	cause the shutdown of the projection system serving the seating area, and

(ii)	turn on the normal lighting in the seating area, and

(g)	the floor area is sprinklered.

(11.2)  Dead-end aisles are permitted to be more than 10 m long, but not more than 13 m long if

(a)	the seating area is separated from other seating areas and adjacent occupancies, including a corridor serving any seating area, by a fire separation in accordance with Sentences 3.3.2.2. (1) and (2),

(b)	the travel distance is not more than 25 m measured along the path of travel from any seat to an exit, to an egress doorway or to an opening into a vomitory,

(c)	at least one means of egress, comprising not less than 30% of the required exit capacity, is through an exterior exit, an exit stairway or a corridor not containing an occupancy,

(d)	each row served by a dead-end aisle has a minimum unobstructed width of 400 mm plus 6.1 mm for each additional seat above 7 seats in a row, but not more than 550 mm,

(e)	the activation of a fire detector or a sprinkler head in the seating area will

(i)	cause the shutdown of the projection system serving the seating area, and

(ii)	turn on the normal lighting in the seating area,

(f)	a voice communication system is installed in conformance with Article 3.2.4.22.,

(g)	a smoke control system is installed to control movement of smoke in the seating area or a smoke exhaust system is provided so that, in the event of detection of smoke by a smoke detector in the seating area, air handling equipment is activated to extract air directly from the seating area at the rate of at least 6 air changes per hour, and

(h)	the floor area is sprinklered.

(12)  Where a seating area is separated as required by Sentences 3.3.2.2.(1) and (2) or 3.3.2.2.(8), the length of travel by any aisle shall be not more than 45 m measured from the most remote point of the aisle to

(a)	an egress doorway in the required separation, or

(b)	an exit leading directly from the seating area.

(13)  Where a seating area is not required to be separated by Sentences 3.3.2.2.(1) and (2) or 3.3.2.2.(8), the travel distance shall be not more than 45 m measured from the most remote point of the aisle to an exit.

(14)  Side aisles shall be not less than 1 100 mm wide if seating is provided in conformance with Sentence 3.3.2.3.(4).

(15)  An aisle that has a slope not more than 1 in 8 shall not be stepped.

(16)  An aisle that slopes more than 1 in 8 shall be stepped.

(17)  The passageway between rows of seats served by a stepped aisle shall be level at right angles to the line of travel.

(18)  The riser of a step in an aisle shall be

(a)	not less than 110 mm high, and

(b)	not more than 200 mm high.

(19)  Variations are permitted in riser height provided

(a)	the height of adjacent risers does not vary by more than 6 mm, and

(b)	the depth of a tread or a platform in the direction of travel is not less than 430 mm.

(20)  Steps in an aisle shall

(a)	have a run not less than 230 mm exclusive of nosings,

(b)	have a tread depth not less than 250 mm,

(c)	extend to the adjacent rows of seats in a manner that will not create a hazard from tripping, and

(d)	have a finish on the treads conforming to Sentence 3.4.6.1.(1).

(21)  The location of every riser in an aisle shall be made apparent from both directions of travel by strategically placed lighting or contrasting marking stripes.

(22)  A platform in an aisle shall be level, except that a slope not more than 1 in 50 is permitted for a platform that is not less than 430 mm deep in the direction of exit travel.

(23)  If a step is used at the entry to a row of seats from a stepped aisle, an unobstructed platform not less than 800 mm square shall be provided adjacent to the aisle.

(24)  The finish of the surface of a platform in or adjacent to a stepped aisle shall conform to Sentence 3.4.6.1.(1).

3.3.2.5.  Corridors

(1)  Except as permitted by Sentences (2) to (4), a corridor used by the public in an assembly occupancy as an access to exit shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(2)  The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(3)  The fire-resistance rating required by Sentence (1) is permitted to be waived if the floor area in which the corridor is located is sprinklered.

(4)  The fire separation required by Sentence (1) is permitted to be waived if the distance from any point in the floor area to an exit measured along the path of travel to an exit does not exceed the travel distance permitted by Article 3.4.2.5.

3.3.2.6.  Doors

(1)  A door equipped with a latching mechanism in an access to exit from a room or suite of assembly occupancy containing an occupant load more than 100 shall be equipped with a device that will release the latch and allow the door to swing wide open when a force not more than that specified in Sentence 3.8.3.3.(7) is applied to the device in the direction of travel to the exit.

3.3.2.7.  Fixed Bench-Type Seats without Arms

(1)  If fixed bench-type seats without arms are provided, the seat width per person shall be assumed to be 450 mm.

(2)  The centre-to-centre spacing between rows of bench-type seats shall be not less than 760 mm if back rests are provided, and not less than 550 mm if back rests are not provided.

(3)  A clear space of not less than 300 mm shall be provided between the back of each seat and the front of the seat immediately behind it.

3.3.2.8.  Guards

(1)  Except as required by Sentences (2) to (4) for bleacher seats, guards shall be installed in outdoor and indoor places of assembly with fixed seats so that

(a)	at the fascia of every box, balcony or gallery where the seats extend to the edge, the height of guards is not less than

(i)	760 mm in front of the seats, and

(ii)	920 mm if located at the end of aisles or at the foot of steps,

(b)	the height of guards along every cross aisle other than those adjacent to the fascia of every box, balcony or gallery is not less than 660 mm, except that guards need not be provided if the backs of the seats along the front side of the aisle are not less than 600 mm above the floor of the aisle, and

(c)	where the seating is arranged in successive tiers and the height of rise between platforms is more than 450 mm, the height of guards is not less than 660 mm along the entire row of seats at the edge of the platform.

(2)  The backs and ends of bleacher seats more than 1 200 mm above the ground or floor that are not adjacent to a wall shall be protected with a guard

(a)	not less than 1 070 mm high above an adjacent aisle surface or foot rest, and

(b)	not less than 920 mm high above the centre of an adjacent seat board.

(3)  If the front of a bleacher is more than 600 mm above the ground or floor, it shall be protected with a guard not less than 840 mm high above the front foot rest.

(4)  Openings through any guard which is required by Sentences (2) and (3) shall be of a size which will prevent the passage of a sphere having a diameter more than 300 mm.

3.3.2.9.  Outdoor Places of Assembly

(1)  A Group A, Division 4 occupancy and each tier or balcony that has a capacity of more than

(a)	1 000 persons shall have not less than 3 separate exits, or

(b)	4 000 persons shall have not less than 4 separate exits.

(2)  In a Group A, Division 4 occupancy, every seat shall be located so that the travel distance is not more than 45 m measured along the path of travel from the seat to

(a)	the ground,

(b)	an exit,

(c)	an opening to a passageway leading from the seating area, or

(d)	a portal, a vomitory or any other opening through the seating deck structure.

(3)  Exits from outdoor stadia or grandstands shall be located not more than 25 m apart.

(4)  The capacity of a means of egress for a Group A, Division 4 occupancy shall conform to the requirements of Sentence 3.4.3.4.(3).

(5)  Aisles in a Group A, Division 4 occupancy

(a)	shall be located so that there are not more than 20 seats between any seat and the nearest aisle,

(b)	shall be not less than 1 200 mm wide, except that an aisle serving less than 60 persons is permitted to be 750 mm wide, and

(c)	shall not have steps unless the slope of the aisle is more than 1 in 8.

(6)  Except as permitted by Sentences 3.3.2.10.(1), (2) and (3), steps provided in an aisle shall

(a)	extend the full width of the aisle,

(b)	have risers not more than 230 mm high, and

(c)	have treads with a run not less than 250 mm.

3.3.2.10.  Bleachers

(1)  Steps provided in aisles of bleachers of the telescopic type shall

(a)	have risers not more than 250 mm high, and

(b)	have treads with a run not less than 280 mm.

(2)  If the vertical distance between seating platforms in bleachers is more than 280 mm, an intermediate step shall be provided the full width of the aisle and proportioned to provide 2 equal risers between platforms.

(3)  If the vertical distance between seating platforms in bleachers is more than 450 mm, 2 intermediate steps shall be provided the full width of the aisle so that there are 3 equal risers between platforms.

(4)  If the passageway between rows of seats is not a closed deck, footboards shall be provided so that

(a)	the total width of the footboards shall be not less than three quarters of the centre-to-centre spacing between rows of seats, and

(b)	the spacing between footboard members shall be not more than 25 mm.

3.3.2.11.  Libraries

(1)  Except as permitted by Sentence (2), a library book storage room that is not normally accessible to the public shall be separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 2 h if it

(a)	is more than 250 m2 in area, or

(b)	contains book stacks that

(i)	are more than 10 m high, or

(ii)	penetrate more than one floor assembly.

(2)  The fire separation required by Sentence (1) is not required if the book storage room is sprinklered.

(3)  Open book shelves are permitted above and below a mezzanine floor in a library building provided the height of the shelves is not more than 2 100 mm but not more than 75% of the floor-to-ceiling height of the space above or below the mezzanine floor assembly.

3.3.2.12.  Stages for Theatrical Performances

(1)  A stage for theatrical performances and ancillary spaces, including workshops, dressing rooms and storage areas, shall be sprinklered.

(2)  A fire separation with a fire-resistance rating not less than 1 h shall be provided between a stage for theatrical performances and ancillary spaces, including workshops, dressing rooms and storage areas.

(3)  Except as permitted by Sentence (6), a stage for theatrical performances and ancillary spaces, including workshops, dressing rooms and storage areas, shall be separated from the seating area by a fire separation having a fire-resistance rating not less than 1 h, except for a proscenium opening protected with

(a)	a sprinkler deluge system conforming to the requirements of NFPA 13 “Standard for the Installation of Sprinkler Systems”,

(b)	an unframed fire curtain if the opening is not more than 20 m wide, or

(c)	a semi-rigid fire curtain if the opening is more than 20 m wide.

(4)  A fire curtain required by Sentence (3) shall be of a type designed to close

(a)	automatically upon the actuation of the sprinkler system,

(b)	automatically upon actuation of the fire alarm system,

(c)	manually by remote control devices located at the curtain control panel and at each side of the stage, and

(d)	automatically by heat-actuated devices.

(5)  At least 2 vents for the purpose of venting fire and smoke to the outside of a building shall be provided above a stage designed for theatrical performances and shall

(a)	have an aggregate area not less than one eighth of the area of the stage behind the proscenium opening, and

(b)	be arranged to open automatically upon actuation of the sprinkler system.

(6)  The fire separation referred to in Sentence (3) is not required between a stage and a seating area in a floor area that is sprinklered, provided a sprinkler deluge system is installed at the boundary between the stage and the seating area.

3.3.2.13.  Risers for Stairs

(1)  In a Group A, Division 2 occupancy used for the serving of food and beverages, an interior flight of stairs with fewer than 3 risers is permitted provided it

(a)	is not less than 900 mm wide,

(b)	is illuminated at all times that occupants are on the premises, and

(c)	has a handrail on each side.

3.3.3. Care or Detention Occupancy

3.3.3.1.  Scope

(1)  This Subsection applies to floor areas or parts thereof used or intended for use as a care or detention occupancy.

3.3.3.2.  Fire Separations

(1)  The fire separation required by Sentence 3.3.5.5.(1) between a care or detention occupancy and a repair garage shall have no openings.

(2)  Except as permitted by Sentence (4), in a Group B, Division 3 occupancy, walls between sleeping rooms and adjacent rooms shall be constructed as fire separations having a fire-resistance rating not less than 1 h, except that the fire-resistance rating need not be more than 45 min where the floor assembly is not required to be more than 45 min.

(3)  Except as permitted by Sentence (4), in a Group B, Division 3 occupancy, walls separating corridors serving sleeping rooms from adjacent rooms shall be constructed as fire separations having a fire-resistance rating not less than 1 h, except that the fire-resistance rating need not be more than 45 min where the floor assembly is not required to be more than 45 min.

(4)  In a Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than 6 occupants requiring assistance in evacuation in case of an emergency, the walls separating sleeping rooms from adjacent rooms and corridors shall be constructed as fire separations but are not required to have a fire-resistance rating.

(5)  The door in the fire separation required in Sentence (4) is permitted to be equipped with a roller latch and need not be provided with a self-closing device.

3.3.3.3.  Corridors

(1)  A corridor used by the public or serving patients or residents shall have no dead-end portion unless the area served by the dead-end portion has a second and separate means of egress.

(2)  A corridor serving patients in a hospital shall be not less than 2 400 mm wide.

(3)  Except as permitted in Sentence (5), a corridor serving residents who are not ambulatory in a Group B, Division 2 or 3 occupancy shall be not less than 1 650 mm wide.

(4)  Paired doors in a corridor serving patients or residents shall

(a)	swing in opposite directions, the right hand door swinging in the direction of travel, and

(b)	be not less than 1 100 mm wide.

(5)  A corridor in a Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than 6 occupants requiring assistance in evacuation in case of an emergency need not comply with Sentence (3).

3.3.3.4.  Doorway Width

(1)  Except as permitted in Sentence 3.3.1.12.(11), the minimum clear width of doorways serving patients or residents shall be 1 050 mm.

3.3.3.5.  Hospitals and Nursing Homes

(1)  Floor areas containing patients’ or residents’ sleeping rooms in a hospital or nursing home shall conform to Sentences (2) to (14).

(2)  Except as permitted by Sentence (3), a floor area containing patients’ or residents’ sleeping rooms in a hospital or nursing home shall be divided into not less than 2 fire compartments, each not more than 1 000 m2 in area.

(3)  The floor area on either side of a horizontal exit conforming to Article 3.4.6.9. is permitted to be considered as a fire compartment in applying the requirements of this Article.

(4)  Except as permitted by Sentence (5), fire separations separating fire compartments required by Sentence (2) shall have a fire-resistance rating not less than 1 h.

(5)  The fire-resistance rating of a fire separation referred to in Sentence (4) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(6)  A closure in a fire separation between fire compartments referred to in Sentence (2) shall be weatherstripped or otherwise designed and installed to retard the passage of smoke.

(7)  The travel distance from any point within each fire compartment referred to in Sentence (2) to a door to an adjoining fire compartment shall be not more than 45 m.

(8)  Each fire compartment referred to in Sentence (2) shall be capable of accommodating, in addition to its own occupants, the occupants of the largest adjacent fire compartment based on a clear floor space of 2.5 m2 per patient or resident in the adjacent fire compartment.

(9)  Except as permitted by Sentences (11) and (12), walls between patients’ or residents’ sleeping rooms and adjacent rooms shall be constructed as fire separations but are not required to have a fire-resistance rating.

(10)  Except as permitted by Sentence (12), walls separating corridors serving patients’ or residents’ sleeping rooms from adjacent rooms shall be constructed as fire separations but are not required to have a fire-resistance rating.

(11)  The fire separation requirements of Sentence (9) do not apply to walls within a group of intercommunicating patients’ or residents’ rooms, provided the group of rooms does not

(a)	contain more than 5 patients or residents, or

(b)	include storage, bathing or toilet facilities serving persons not occupying the group of rooms.

(12)  A door in a fire separation required by Sentence (9) or Sentence (10) is permitted to be equipped with a roller latch.

(13)  A fire separation required by Sentence (9) or Sentence (10) shall not contain any grilles, louvres or other openings.

3.3.3.6.  Protection for Special Care and Treatment Facilities

(1)  Compartments containing rooms such as operating rooms, recovery rooms, delivery rooms, intensive care units and critical care units, from which it is impracticable to move patients in an emergency, shall be

(a)	separated from adjacent spaces by fire separations having a fire-resistance rating not less than 1 h, and

(b)	provided with a mechanical air supply so that during a period of 2 h after the start of a fire in another space, the compartments will not contain more than 1% by volume of contaminated air from the fire area.

3.3.3.7.  Contained Use Areas

(1)  A contained use area shall conform to Sentences (2) to (4).

(2)  A contained use area shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(3)  Except as permitted by Sentence (4), a building that includes a contained use area shall be sprinklered.

(4)  A contained use area, in a building for which Articles 3.2.2.20. to 3.2.2.83. do not require the installation of an automatic sprinkler system, is not required to be sprinklered as required by Sentence (3) provided

(a)	the building is designed so that during a period of 2 h after the start of a fire in the contained use area, other fire compartments will not contain more than 1% by volume of contaminated air from the contained use area,

(b)	the building is designed so that during a period of 2 h after the start of a fire in another part of the building, the contained use area will not contain more than 1% by volume of contaminated air from the other part of the building,

(c)	all doors are designed to be remotely released in conformance with Sentence 3.3.1.12.(6), and

(d)	the contained use area does not contain any rooms lined with combustible padding.

3.3.3.8.  Handrails

(1)  Corridors and ramps used by residents in a nursing home shall be equipped with handrails on each side conforming to Sentences 3.4.6.4.(3), (4), (6), (7) and (8).

3.3.4. Residential Occupancy

3.3.4.1.  Scope

(1)  This Subsection applies to floor areas or parts thereof used or intended for use as residential occupancies.

3.3.4.2.  Fire Separations

(1)  Except as permitted by Sentences (2) and 3.2.2.9.(2), suites of residential occupancy shall be separated from each other and the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(2)  The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(3)  Floor assemblies within a dwelling unit need not be constructed as fire separations provided

(a)	the distance between the lowest floor level and the uppermost floor level within the dwelling unit is not more than 6 m, and

(b)	the dwelling unit is separated from the remainder of the building by a fire separation having a fire-resistance rating not less than

(i)	45 min if the building is sprinklered and is not more than 3 storeys in building height,

(ii)	1 h if the building is sprinklered and is more than 3 storeys in building height,

(iii)	1 h if the building is not sprinklered and is not more than 6 storeys in building height, or

(iv)	2 h if the building is not sprinklered and is more than 6 storeys in building height.

(4)  The fire-resistance rating of the fire separation located between a dwelling unit and an attached storage garage need not conform to that required by Sentence 3.3.5.6.(1) provided

(a)	the storage garage contains not more than 5 vehicles,

(b)	the dwelling unit and the attached storage garage are sprinklered,

(c)	the dwelling unit is separated from the remainder of the building in conformance with Sentences (1), (2) and (3),

(d)	there are no air duct systems connecting the storage garage and the dwelling unit,

(e)	the construction between the storage garage and the dwelling unit provides an effective barrier to gas and exhaust fumes, and

(f)	every door between the storage garage and the dwelling unit is

(i)	tight fitting and weather-stripped to provide an effective barrier against the passage of gas and exhaust fumes,

(ii)	fitted with a self-closing device, and

(iii)	not located in a room intended for sleeping.

(5)  The fire separation required by Sentence 3.3.5.6.(1) is not required between a dwelling unit and an attached storage garage, serving that dwelling unit only, provided

(a)	the dwelling unit and its attached storage garage are separated from the remainder of the building in conformance with Sentences (1), (2) and (3),

(b)	there are no air duct systems connecting the storage garage and the dwelling unit,

(c)	the construction between the storage garage and the dwelling unit provides an effective barrier to gas and exhaust fumes, and

(d)	every door between the storage garage and the dwelling unit is

(i)	tight fitting and weather-stripped to provide an effective barrier against the passage of gas and exhaust fumes,

(ii)	fitted with a self-closing device, and

(iii)	not located in a room intended for sleeping.

3.3.4.3.  Storage Rooms

(1)  Sprinklers shall be installed in a storage room provided for the use of tenants in a residential occupancy within a floor area but not contained within a suite.

(2)  Except as permitted by Sentence (3), a storage room referred to in Sentence (1) shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(3)  The fire-resistance rating of the fire separation required by Sentence (2) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

3.3.4.4.  Egress from Dwelling Units

(1)  Single storey dwelling units in an apartment building need not lead to a public corridor or exterior passageway on the same storey provided the dwelling units are served by private stairways leading directly to a public access to exit on the storey

(a)	immediately above, and

(b)	immediately below.

(2)  Except as permitted by Sentences (3), (4) and (5), a dwelling unit containing more than one storey shall have an exit door or an egress door opening directly into a public access to exit from the uppermost storey and from the lowest storey of the dwelling unit so that each storey is served by an exit or egress door located not more than 1 500 mm above or below its floor level.

(3)  A single exit is permitted from a dwelling unit provided the exit is an exterior doorway not more than 1 500 mm above adjacent ground level and

(a)	it is not necessary to travel up or down more than one storey to reach the exit door, or

(b)	the uppermost floor level opens to a balcony not more than 6 m above adjacent ground level.

(4)  An egress door from either the uppermost storey or the lowest storey in a dwelling unit, as required in Sentence (2), need not be provided

(a)	if that storey is served by a stairway that

(i)	leads to a public access to exit,

(ii)	has no direct access to any other storey in the dwelling unit, and

(iii)	is separated from the other storeys in the dwelling unit by a fire separation having a fire-resistance rating of not less than 45 min,

(b)	if the dwelling unit has not more than 2 storeys above the first storey of the building, or

(c)	if it is not necessary to travel either more than 18 m, or more than 1 storey up or down to reach the egress door.

(5)  An egress door from either the uppermost storey or the lowest storey in a dwelling unit, as required in Sentence (2), need not be provided

(a)	on the uppermost storey of a dwelling unit having not more than 2 storeys above the first storey of the building,

(b)	on each storey from which it is not necessary to travel either more than 18 m or more than 1 storey up or down within the dwelling unit to reach an egress door, or

(c)	where that storey is

(i)	provided with a balcony conforming to Sentence (8),

(ii)	not more than 2 storeys above or below the dwelling unit egress door, and

(iii)	in a building that is not more than 6 storeys in building height.

(6)  In a building of residential occupancy not more than 3 storeys in building height, a doorway from a dwelling unit is permitted to open directly into an exit stairway provided the dwelling unit has a second and separate means of egress.

(7)  If a dwelling unit has a second and separate means of egress, one means of egress from a dwelling unit is permitted to pass through

(a)	an interior corridor served by a single exit,

(b)	an exterior balcony served by a single exit stairway, or

(c)	an exterior passageway served by a single exit stairway.

(8)  Where a balcony is provided to meet the requirements of Sentence (3) or (5), the balcony shall have

(a)	a solid floor having a fire-resistance rating not less than that required for a floor assembly between suites, and

(b)	an area providing not less than 1.5 m2 per suite occupant, based on occupant load, and a minimum dimension of 1 200 mm.

3.3.4.5.  Automatic Locking Prohibition

(1)  Except for hotels, a door opening onto a public corridor which provides access to exit from a suite shall be designed not to lock automatically.

3.3.4.6.  Sound Transmission

(1)  Sound transmission class ratings shall be determined in accordance with ASTM E413, “Classification for Rating Sound Insulation”, using results from measurements in accordance with

(a)	ASTM E90, “Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions”, or

(b)	ASTM E336, “Test Method for Measurement of Airborne Sound Insulation in Buildings”.

(2)  Except as required by Sentence (3), a dwelling unit shall be separated from every other space in the building in which noise may be generated by construction providing a sound transmission class rating not less than 50, measured in accordance with the standards referenced in Sentence (1).

(3)  Construction separating a dwelling unit from an elevator hoistway or a refuse chute shall have a sound transmission class rating not less than 55, measured in accordance with the standards referenced in Sentence (1).

3.3.4.7.  Stairs, Handrails and Guards for Dwelling Units

(1)  Stairs, handrails and guards within a dwelling unit shall conform to the appropriate requirements in Section 9.8.

3.3.5. Industrial Occupancy

3.3.5.1.  Scope

(1)  This Subsection applies to floor areas or parts thereof used or intended for use as industrial occupancies.

3.3.5.2.  Fire Extinguishing Systems

(1)  In addition to other requirements in this Code for the installation of automatic fire extinguishing systems, an appropriate fire extinguishing system shall be installed in every industrial occupancy floor area to provide protection if required by

(a)	the Ontario Fire Code, or

(b)	the National Fire Code of Canada 1995, in the absence of provisions in the Ontario Fire Code.

3.3.5.3.  Basements

(1)  A basement shall not be used for the storage, manufacture or handling of volatile solids, liquids or gases that generate explosive air-vapour mixtures or for processes that involve explosive dusts.

(2)  Entrances and exits to a basement and to rooms containing building services shall be separate from the remainder of the building in a building in which

(a)	the storage, manufacture or handling of volatile materials can generate explosive air-vapour mixtures, or

(b)	processes occur that produce explosive dusts.

(3)  Basements and rooms referred to in Sentence (2) shall be separated from the remainder of the building with a vapour-tight separation.

3.3.5.4.  Repair and Storage Garages

(1)  If access is provided from a storage garage to a stair tower or elevator serving occupancies above the level of the storage garage, the access shall be through a vestibule conforming to Sentence 3.3.5.7.(3).

(2)  Treads and landings in interior stairs that extend to the roof of a storage garage shall be designed to be free of accumulations of ice and snow.

(3)  A mechanical storage garage not more than 4 storeys in building height, in which no persons other than parking attendants are permitted above the street floor level, need not have a fire separation between the exits and the remainder of the building.

(4)  A garage shall be provided with natural or mechanical ventilation in conformance with the requirements of Subsection 6.2.2. to prevent excessive accumulation of carbon monoxide, exhaust fumes or flammable and toxic vapours.

(5)  The clear height in a storage garage shall be not less than 2 000 mm.

(6)  A continuous curb not less than 150 mm high and a guard not less than 1 070 mm high shall be provided at every garage floor opening and around the perimeter of every floor where the exterior walls are omitted.

(7)  Except for open-air storeys, every storey of a storage garage or repair garage located below grade shall be sprinklered.

3.3.5.5.  Repair Garage Separation

(1)  A repair garage and any ancillary spaces serving it, including waiting rooms, reception rooms, tool and parts storage areas and supervisory office space, shall be separated from other occupancies by a fire separation having a fire-resistance rating not less than 2 h.

3.3.5.6.  Storage Garage Separation

(1)  Except as permitted by Sentences 3.3.4.2.(4) and (5), a storage garage shall be separated from other occupancies by a fire separation with a fire-resistance rating not less than 1.5 h.

3.3.5.7.  Vestibules

(1)  If access is provided through a fire separation between a storage garage and a Group A, Division 1 or Group B occupancy, the access shall be through a vestibule conforming to Sentence (3).

(2)  In a building more than 3 storeys in building height, access through a fire separation between a storage garage and a Group A, Division 2, 3 or 4, or a Group C occupancy, shall be through a vestibule conforming to Sentence (3).

(3)  If access is provided through a vestibule, as required by Sentences (1), (2) and 3.3.5.4.(1), the vestibule shall

(a)	be not less than 1 800 mm long,

(b)	be ventilated

(i)	naturally to outside air by a vent that has an unobstructed area of not less than 0.1 m2 for each door that opens into the vestibule but not less than 0.4 m2, or

(ii)	mechanically at a rate of 14 m3/h for each square metre of vestibule floor surface area, and

(c)	have openings between the vestibule and an adjoining occupancy provided with self-closing doors with no hold-open devices.

3.3.5.8.  Reserved

3.3.5.9.  Reserved

3.3.5.10.  Toe-Boards Required

(1)  Where tools or other objects could fall from the floor of an upper level to a lower level in a room or space intended for use as a Group F occupancy, the edge of the floor at the upper level shall be provided with a toe-board extending from the floor surface to a height at least 125 mm above the floor surface.

Section 3.4. Exits

3.4.1. General

3.4.1.1.  Scope

(1)  Exit facilities complying with this Section shall be provided from every floor area which is intended for occupancy.

3.4.1.2.  Separation of Exits

(1)  Except as permitted by Sentence (2), if more than one exit is required from a floor area, each exit shall be separate from every other exit leading from that floor area.

(2)  If more than 2 exits are provided from a floor area, exits are permitted to converge in conformance with Sentence 3.4.3.2.(2), provided the cumulative capacity of the converging exits does not contribute more than 50% of the total required exit width for the floor area.

3.4.1.3.  Access to Exits

(1)  Access to exits shall conform to Section 3.3.

3.4.1.4.  Types of Exit

(1)  Subject to the requirements of this Section, an exit from any floor area shall be one of the following, used singly or in combination:

(a)	an exterior doorway,

(b)	an exterior passageway,

(c)	an exterior ramp,

(d)	an exterior stairway,

(e)	a fire escape (conforming to Subsection 3.4.7.),

(f)	a horizontal exit,

(g)	an interior passageway,

(h)	an interior ramp, or

(i)	an interior stairway.

3.4.1.5.  Exterior Exit Passageways

(1)  Access to an exterior exit passageway from a floor area shall be through exit doors at the floor level.

(2)  Every exterior exit passageway which has a drop of more than 500 mm on any side shall have guards on the open sides not less than 1 070 mm high.

3.4.1.6.  Restricted Use of Horizontal Exits

(1)  Except as permitted by Sentence (2), horizontal exits shall not comprise more than one half of the required number of exits from any floor area.

(2)  In a hospital or nursing home, horizontal exits serving patients’ or residents’ sleeping rooms shall comprise not more than two thirds of the required number of exits from any floor area.

(3)  Where an elementary or secondary school is subdivided by a firewall, a horizontal exit shall not serve as an exit but is permitted to serve as an access to exit.

3.4.1.7.  Slide Escapes

(1)  A slide escape shall not be erected on any building as a required exit, but is permitted to be provided as an additional egress facility if unusual hazards are foreseen.

3.4.1.8.  Transparent Doors and Panels

(1)  Glass and transparent panels in an exit shall conform to the appropriate requirements of Article 3.3.1.18. for glass and transparent panels in an access to exit.

3.4.1.9.  Mirrors near Exits

(1)  No mirror shall be placed in or adjacent to any exit in a manner that would confuse the direction of exit.

3.4.1.10.  Combustible Glazing in Exits

(1)  Combustible glazing is not permitted in wall or ceiling assemblies or in closures used to construct an exit enclosure.

3.4.1.11.  Exterior Stairway for Nursing Home

(1)  No open exterior stairway shall serve as a means of egress for residents above the second floor of a nursing home.

3.4.2. Number and Location of Exits from Floor Areas

3.4.2.1.  Minimum Number of Exits

(1)  Except as permitted by Sentences (2) to (4) and (6), every floor area intended for occupancy shall be served by at least 2 exits.

(2)  A floor area in a building not more than 2 storeys in building height, is permitted to be served by one exit provided the total occupant load served by the exit is not more than 60, and

(a)	in a floor area that is not sprinklered, the floor area and the travel distance are not more than the values in Table 3.4.2.1.A., or

(b)	in a floor area that is sprinklered,

(i)	the travel distance is not more than 25 m, and

(ii)	the floor area is not more than the value in Table 3.4.2.1.B.

Table 3.4.2.1.A.

Criteria for One Exit, Floor Area not Sprinklered

Forming Part of Sentence 3.4.2.1.(2)

| Occupancy of Floor Area | Maximum Floor Area, m2 | Maximum Travel Distance, m |
| --- | --- | --- |
| Group A | 150 | 15 |
| Group C | 125 | 25 |
| Group D | 200 | 25 |
| Group E | 200 | 25 |
| Group F, Division 2 | 200 | 25 |
| Group F, Division 3 | 200 | 25 |
| Column 1 | 2 | 3 |

Table 3.4.2.1.B.

Criteria for One Exit, Floor Area Sprinklered

Forming Part of Sentence 3.4.2.1.(2)

| Occupancy of Floor Area | Maximum Floor Area, m2 |
| --- | --- |
| Group A | 200 |
| Group B | 100 |
| Group C | 150 |
| Group D | 300 |
| Group E | 200 |
| Group F, Division 2 | 200 |
| Group F, Division 3 | 300 |
| Column 1 | 2 |

(3)  Except as permitted by Sentence (4), if Sentence (2) permits a single exit from a floor area classified as Group B or Group C occupancy, the exit shall be an exterior doorway not more than 1 500 mm above adjacent ground level.

(4)  A floor area containing only dwelling units having access to exit conforming to Sentences 3.3.4.4.(1) to (4) need not comply with Sentences (1) or (3).

(5)  Exits are not required directly from rooftop enclosures that are provided with access to exits in conformance with Sentences 3.3.1.3.(5) and (6).

(6)  Every room containing an assembly occupancy serving a hotel, and located in the building containing the hotel, shall be provided with not less than

(a)	3 separate egress doorways from the room where the occupant load is more than 600 persons, and

(b)	4 separate egress doorways from the room where the occupant load is more than 1000 persons.

(7)  Each egress doorway in Sentence (6) shall be considered as contributing not more than

(a)	one third of the required width where 3 egress doorways are required, and

(b)	one fourth of the required width where 4 egress doorways are required.

3.4.2.2.  Mezzanine Exiting

(1)  Except as permitted by Sentences (2), (3) or (4), a mezzanine shall be provided with exits on the same basis as required for floor areas by this Section.

(2)  A mezzanine need not conform to Sentence (1) provided Article 3.2.8.1. does not require it to terminate at a vertical fire separation.

(3)  In a floor area that is not sprinklered, a mezzanine need not conform to Sentence (1) where Article 3.2.8.1. does require it to terminate at a vertical fire separation provided the total occupant load of the mezzanine is not more than 60 and

(a)	the area of the mezzanine does not exceed the area limits for rooms and suites in Table 3.3.1.5.A., and

(b)	the distance limits in Table 3.3.1.5.A. are not exceeded from any point on the mezzanine to

(i)	the egress doorway from the room in which the mezzanine is located if that room has a single egress doorway, or

(ii)	an egress facility leading from the mezzanine if the room in which the mezzanine is located has 2 egress doorways provided in conformance with Subsection 3.3.1.

(4)  In a floor area that is sprinklered, a mezzanine need not conform to Sentence (1) where Article 3.2.8.1. does require it to terminate at a vertical fire separation provided the total occupant load of the mezzanine is not more than 60 and

(a)	the area of the mezzanine does not exceed the area limits for rooms and suites in Table 3.3.1.5.B., and

(b)	the distance of travel is not more than 25 m when measured from any point on the mezzanine to

(i)	the egress doorway from the room in which the mezzanine is located if that room has a single egress doorway, or

(ii)	an egress facility leading from the mezzanine if the room in which the mezzanine is located has 2 egress doorways provided in conformance with Subsection 3.3.1.

3.4.2.3.  Distance between Exits

(1)  Except for a floor area that is divided so that not less than one third of the floor area is on one side of a fire separation and it is necessary to pass through the fire separation to travel from one exit to another exit, the least distance between 2 required exits from a floor area shall be

(a)	one half the maximum diagonal dimension of the floor area, but need not be more than 9 m for a floor area having a public corridor, or

(b)	one half the maximum diagonal dimension of the floor area, but not less than 9 m for all other floor areas.

(2)  The minimum distance between exits referred to in Sentence (1) shall be the shortest distance that smoke would have to travel between the exits, assuming that the smoke will not penetrate an intervening fire separation.

3.4.2.4.  Travel Distance

(1)  Except as permitted by Sentence (2), for the purposes of this Subsection, travel distance means the distance from any point in the floor area to an exit measured along the path of travel to the exit.

(2)  The travel distance from a suite or a room not within a suite is permitted to be measured from an egress door of the suite or room to the nearest exit provided

(a)	the suite or room is separated from the remainder of the floor area by a fire separation

(i)	having a fire-resistance rating not less than 45 min in a floor area that is not sprinklered, or

(ii)	which is not required to have a fire-resistance rating, in a floor area that is sprinklered, and

(b)	the egress door opens onto

(i)	an exterior passageway,

(ii)	a corridor used by the public that is separated from the remainder of the floor area in conformance with the requirements in Article 3.3.1.4. for the separation of public corridors, or

(iii)	a public corridor that is separated from the remainder of the floor area in conformance with Article 3.3.1.4.

(3)  Travel distance to an exit shall be not more than 50 m from any point in a service space referred to in Sentence 3.2.1.1.(7).

(4)  If there is a firewall in an elementary or secondary school, the travel distance shall not be measured to a door in the firewall, but shall be measured to an exterior exit door or an exit door to a stairway.

3.4.2.5.  Location of Exits

(1)  Except as permitted by Sentences (2), (3) and 3.3.2.4.(6), if more than one exit is required from a floor area, the exits shall be located so that the travel distance to at least one exit shall be not more than

(a)	25 m in a high hazard industrial occupancy,

(b)	40 m in a business and personal services occupancy,

(c)	45 m in a floor area that contains an occupancy other than a high hazard industrial occupancy, provided it is sprinklered,

(d)	105 m in any floor area, served by a public corridor, in which rooms and suites are not separated from the remainder of the floor area by a fire separation, provided

(i)	the public corridor is not less than 9 m wide,

(ii)	the ceiling height in the public corridor is not less than 4 m above all floor surfaces,

(iii)	the building is sprinklered, and

(iv)	not more than one half of the required egress doorways from a room or suite open into the public corridor if the room or suite is required to have more than one egress doorway,

(e)	except as permitted by Sentence (5), 60 m in any storage garage that conforms to the requirements of Article 3.2.2.83., and

(f)	30 m in any floor area other than those referred to in Clauses (a) to (e).

(2)  Except for a high hazard industrial occupancy, Sentence (1) need not apply if exits are placed along the perimeter of the floor area and are not more than 60 m apart, measured along the perimeter, provided each main aisle in the floor area leads directly to an exit.

(3)  If more than one exit is required, every exit shall be considered as contributing not more than one half of the required exit width.

(4)  Exits shall be located and arranged so that they are clearly visible or their locations are clearly indicated and they are accessible at all times.

(5)  Not more than 2 exits located remote from each other are required in a storage garage conforming to Article 3.2.2.83. provided persons other than parking attendants are not permitted above the street floor level.

3.4.3. Width and Height of Exits

3.4.3.1.  Exit Width

(1)  The aggregate width of required exits shall be not less than the value determined in conformance with Sentence (2) and Articles 3.4.3.2. to 3.4.3.5.

(2)  The required width of an exit shall be not less than

(a)	1 100 mm for

(i)	corridors and passageways, and

(ii)	stairs and ramps that serve more than 3 storeys above grade or more than one storey below grade,

(b)	900 mm for stairs and ramps that serve not more than 3 storeys above grade or not more than one storey below grade,

(c)	1 650 mm for stairs and ramps serving patients’ or residents’ sleeping rooms in a Group B, Division 2 or 3 occupancy,

(d)	1 050 mm for doorways serving patients’ or residents’ sleeping rooms, and

(e)	790 mm for doorways not serving patients’ or residents’ sleeping rooms.

(3)  Except as required by Article 3.4.3.3., the required exit width need not be cumulative in an exit serving 2 or more floor areas located one above the other.

3.4.3.2.  Exit Width Based on Occupant Load

(1)  For the purpose of determining aggregate width of required exits, the occupant load of every room or floor area shall be determined in conformance with Subsection 3.1.16.

(2)  Except as permitted by Sentence 3.4.3.1.(3), the required exit width shall be cumulative if 2 or more exits converge.

3.4.3.3.  Exits from Interconnected Floor Space

(1)  The required exit width for an exit stair in an assembly hall or theatre serving more than one balcony level shall conform to the appropriate requirements for stairs serving interconnected floor spaces in Article 3.2.8.4.

(2)  Exit stairs that serve interconnected floor spaces as provided in Articles 3.2.8.3. to 3.2.8.11. shall conform to the requirements in Article 3.2.8.4. and in this Section.

3.4.3.4.  Exit Capacity

(1)  Except as permitted by Sentence (3), the aggregate required width of exits serving floor areas intended for assembly occupancies, residential occupancies, business and personal services occupancies, mercantile occupancies, and industrial occupancies shall be determined by multiplying the occupant load of the area served by

(a)	6.1 mm per person for ramps with a slope not more than 1 in 8, doorways, corridors and passageways,

(b)	8 mm per person for a stair consisting of steps whose rise is not more than 180 mm and whose run is not less than 280 mm, or

(c)	9.2 mm per person for

(i)	ramps with a slope more than 1 in 8, or

(ii)	stairs, other than stairs conforming to Clause (b).

(2)  The aggregate required width of exits serving floor areas intended for care or detention occupancy shall be determined by multiplying the occupant load of the area served by 18.4 mm per person.

(3)  The required width of means of egress serving a Group A, Division 4 occupancy shall be determined by multiplying the occupant load of the area served by

(a)	1.8 mm per person for

(i)	aisles,

(ii)	stairs other than exit stairs, and

(iii)	ramps and passageways in vomitories and exits, and

(b)	2.4 mm per person for exit stairs.

3.4.3.5.  Exit Width Reduction

(1)  Except as permitted by Sentences (2) to (4), no fixture, turnstile or construction shall project into or be fixed within the required width of an exit.

(2)  Exit doors shall be hung so that, when open, they shall neither diminish nor obstruct the required width of the exit by more than 50 mm for each door leaf.

(3)  Swinging doors in their swing shall not reduce the required width of exit stairs or landings to less than 750 mm or reduce the width of an exit passageway to less than the minimum required width.

(4)  Handrails and construction below handrails are permitted to project into the required width of means of egress but the projections shall be not more than 100 mm on each side of the required width.

(5)  In an elementary or secondary school, where a stair lift is installed in an exit stair, an intermediate handrail shall be installed between the path of travel of the stair lift and the remainder of the stair to ensure that the stair lift will not reduce the required width of the exit stair.

3.4.3.6.  Headroom Clearance

(1)  Except as permitted by Sentences (2) to (4), every exit shall have a headroom clearance of not less than 2 100 mm.

(2)  The headroom clearance for stairways measured vertically above any landing or the nosing of any stair tread shall be not less than 2 050 mm.

(3)  The headroom clearance for doorways shall be not less than 2 030 mm.

(4)  No door closer or other device shall be installed so as to reduce the headroom clearance of a doorway to less than 1 980 mm.

3.4.4. Fire Separation of Exits

3.4.4.1.  Fire-Resistance Rating of Exit Separations

(1)  Except as permitted by Sentences (2), (4), 3.3.5.4.(3), 3.4.4.2.(2) and 3.4.4.3.(1), every exit shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than that required by Subsection 3.2.2., but not less than 45 min, for

(a)	the floor assembly above the storey, or

(b)	the floor assembly below the storey, if there is no floor assembly above.

(2)  The fire-resistance rating of the fire separation referred to in Sentence (1) need not be more than 2 h.

(3)  If an exit stair in an assembly hall or theatre serves more than one balcony level, the exit stair shall be separated from the remainder of the building in conformance with Sentence (1).

(4)  The path of exit travel may lead from an exit door or exit enclosure through open air parking that is located below a roof or floor assembly that is part of the building served by the exit door or exit enclosure where

(a)	the portion of the path of exit travel that leads through the open air parking is not more than 9 m in length measured from the exit door to a point at ground level at the perimeter of the building,

(b)	measures are taken to prevent vehicles intended to park in spaces adjacent to the path of exit travel from encroaching on the path of exit travel, and

(c)	an alternate means of egress not leading through the open air parking is available from the interior side of the door opening onto the path of exit travel through the open air parking area.

3.4.4.2.  Exits through Lobbies

(1)  Except as permitted by Sentence (2), no exit from a floor area above or below the first storey shall lead through a lobby.

(2)  Not more than one exit from a floor area is permitted to lead through a lobby provided

(a)	the lobby floor is not more than 4.5 m above grade,

(b)	the path of travel through the lobby to the outdoors is not more than 15 m,

(c)	the adjacent rooms or premises having direct access to the lobby do not contain a residential occupancy or an industrial occupancy, except that dwelling units may open directly onto the lobby where

(i)	from the interior of the exit stair which opens onto the lobby there is alternate means of egress not leading through the lobby and such means of egress is entirely within the same storey as the lobby, or

(ii)	the floor area is sprinklered.

(d)	except as required by Clause (g), the lobby is not located within an interconnected floor space other than as described in Sentence 3.2.8.2.(6),

(e)	the lobby conforms to the requirements for exits, except that

(i)	rooms other than service rooms and storage rooms are permitted to open onto the lobby,

(ii)	the fire separation between the lobby and a room used for the sole purpose of control and supervision of the building need not have a fire-resistance rating, and

(iii)	the fire separation between the lobby and adjacent occupancies that are permitted to open onto the lobby need not have a fire-resistance rating provided the lobby and adjacent occupancies are sprinklered,

(f)	a fire separation, constructed in accordance with Sentence 3.4.4.1.(1), is maintained between the lobby and any exit permitted by this Sentence to lead through the lobby, and

(g)	that if the exit serves a hotel, the lobby is not located within an interconnected floor space.

3.4.4.3.  Exterior Passageway Exceptions

(1)  The requirements of Sentences 3.4.4.1.(1) and 3.2.3.12.(1) and (3) do not apply to an exterior exit passageway provided

(a)	not less than 50% of the exterior side is open to the outdoors, and

(b)	an exit stair is provided at each end of the passageway.

3.4.4.4.  Integrity of Exits

(1)  A fire separation that separates an exit from the remainder of the building shall have no openings except for

(a)	standpipe and sprinkler piping,

(b)	electrical wires and cables, totally enclosed noncombustible raceways and noncombustible piping that serve only the exit,

(c)	openings required by the provisions of Subsection 3.2.6.,

(d)	exit doorways, and

(e)	wired glass and glass block permitted by Article 3.1.8.14.

(2)  Exits within scissors stairs and other contiguous exit stairways shall be separated from each other by a smoke-tight fire separation having a fire-resistance rating not less than that required for the floor assembly through which they pass.

(3)  Fire separations separating contiguous stairs described in Sentence (2) shall not be pierced by doorways, ductwork, piping or any other openings that affect the continuity of the separation.

(4)  A fuel-fired appliance shall not be installed in an exit.

(5)  An exit shall not be used as a plenum for a heating, ventilating or air-conditioning system.

(6)  An exit shall be designed for no purpose other than for exiting, except that an exit is permitted also to be designed to serve as an access to a floor area.

(7)  A service room shall not open directly into an exit.

(8)  Storage rooms, washrooms, toilet rooms, laundry rooms and similar ancillary rooms shall not open directly into an exit.

(9)  Service spaces referred to in Sentence 3.2.1.1.(7) shall not open directly into an exit.

(10)  In elementary and secondary schools, an exit shall be designed so that it does not serve as an access from one portion of a floor area to another portion of the same floor area.

3.4.5. Exit Signs

3.4.5.1.  Exit Signage

(1)  Except as required by Sentences (7) and (9), every exit door other than the main entrance to a room or building shall have an exit sign placed over or adjacent to it if the exit serves

(a)	a building more than 2 storeys in building height,

(b)	a building having an occupant load more than 150, or

(c)	a room or floor area that has a fire escape as part of a required means of egress.

(2)  Except as provided in Sentence (9), every exit sign shall

(a)	be visible from the exit approach,

(b)	have the word EXIT or the words EXIT/SORTIE displayed in plain legible letters, and

(c)	be illuminated continuously while the building is occupied.

(3)  Exit signs shall consist of red letters on a contrasting background or a red background with contrasting letters, with the letters having a 19 mm stroke and a height not less than

(a)	114 mm when internally illuminated, and

(b)	150 mm when externally illuminated.

(4)  If illumination of an exit sign is provided from an electrical circuit, that circuit shall

(a)	serve no equipment other than emergency equipment, and

(b)	be connected to an emergency power supply as described in Sentence 3.2.7.4.(1)

(5)  If necessary, the direction of egress in public corridors and passageways shall be indicated by a sign conforming to Sentences (2), (3) and (4) with a suitable arrow or pointer indicating the direction of egress.

(6)  Except for egress doorways described in Sentence 3.3.2.3.(4) and except for the main entrance door, an exit sign conforming to Sentences (2), (3) and (4) shall be placed over or adjacent to every egress doorway from rooms with an occupant load more than 60 in Group A, Division 1 occupancies, dance halls, licensed beverage establishments and other similar occupancies that, when occupied, have lighting levels below that which would provide easy identification of the egress doorway.

(7)  Except for suite doors opening directly to the exterior, every exit serving a hotel shall have an exit sign placed over or adjacent to it.

(8)  If an exit sign having the word EXIT is installed in conformance with this Article, an additional sign displaying the word SORTIE is permitted to be installed.

(9)  An exit sign is not required within a suite containing a Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than 6 occupants requiring assistance in evacuation in case of an emergency.

3.4.5.2.  Signs within Exit Facilities

(1)  In a building more than 2 storeys in building height, any part of an exit ramp or stair that continues past an exterior exit door down to a basement shall be clearly marked.

(2)  An exit stair serving a building more than 6 storeys in building height shall be clearly marked by signs indicating that it does not lead to an exit at the roof level.

3.4.6. Types of Exit Facilities

3.4.6.1.  Slip Resistance of Ramps and Stairs

(1)  The surfaces of ramps, landings and treads

(a)	shall have a finish that is slip resistant, and

(b)	if accessible to the public, shall have either a colour contrast or a distinctive pattern to demarcate the leading edge of the tread and the leading edge of the landing, as well as the beginning and end of a ramp.

(2)  Treads and landings of exterior exit stairs shall be designed to be free of ice and snow accumulations if the stairs

(a)	are more than 10 m high, or

(b)	serve a hotel.

3.4.6.2.  Minimum Number of Risers

(1)  Except as permitted by Sentence 3.3.2.13.(1), every flight of interior stairs shall have not less than 3 risers.

3.4.6.3.  Landings and Maximum Vertical Rise of Stair Flights

(1)  No flight of stairs shall have a vertical rise of more than 3.7 m between floors or landings, except that a flight of stairs serving as an exit in a Group B, Division 2 or 3 occupancy shall have a vertical rise not more than 2 400 mm between floors or landings.

(2)  Except as provided in Sentence (6), the length and width of a landing shall be at least the width of the stairway in which it occurs, except that in a straight run the length of the landing need not be more than 1 100 mm.

(3)  Where a doorway or stairway empties onto a ramp through a side wall, there shall be a level area extending across the full width of the ramp, and for a distance of 300 mm on either side of the wall opening, or on one side if the opening abuts on an end wall.

(4)  Where a doorway or stairway empties onto a ramp through an end wall, there shall be a level area extending across the full width of the ramp and along its length for not less than 900 mm.

(5)  A landing shall be provided at the top and bottom of every flight of stairs.

(6)  Where the direction of exit travel changes at a landing, the landing is permitted to be chamfered or curved in plan, provided the required width of the stair is maintained where measured perpendicular to the direction of exit travel across the landing.

3.4.6.4.  Handrails

(1)  An exit ramp or stairway shall have a handrail on at least one side, and if 1 100 mm or more in width, shall have handrails on both sides.

(2)  If the required width of a ramp or flight of stairs is more than 2 200 mm, one or more intermediate handrails continuous between landings shall be provided, and located so that there will be not more than 1 650 mm between handrails.

(3)  Handrails shall be continuously graspable along their entire length and shall have

(a)	a circular cross-section with an outside diameter not less than 30 mm and not more than 50 mm, or

(b)	any non-circular shape with a graspable portion that has a perimeter not less than 100 mm and not more than 155 mm and whose largest cross-sectional dimension is not more than 57 mm.

(4)  Handrails on stairs and ramps shall be not less than 865 mm and not more than 965 mm high, measured vertically from a line drawn through the outside edges of the stair nosing or from the surface of the ramp, except that handrails not meeting these requirements are permitted provided they are installed in addition to the required handrail.

(5)  Except as required by Sentence (10), at least one handrail shall be continuous throughout the length of the stairway, including landings, except where interrupted by doorways or newels at changes in direction.

(6)  Handrails shall be terminated in a manner which will not obstruct pedestrian travel or create a hazard.

(7)  At least one handrail at the side of a stairway or ramp shall extend horizontally not less than 300 mm beyond the top and bottom of the stairway or ramp.

(8)  A clearance of not less than 40 mm shall be provided between a handrail and any wall to which it is fastened.

(9)  Handrails and their supports shall be designed and constructed to withstand the loading values obtained from the nonconcurrent application of

(a)	a concentrated load not less than 0.9 kN applied at any point and in any direction for all handrails, and

(b)	a uniform load not less than 0.7 kN/m applied in any direction to handrails not located within dwelling units.

(10)  In a nursing home, a home for the aged and a Group B, Division 3 occupancy, a continuous handrail shall be provided on both sides of a stairway throughout the length of the stairway, including landings, except where a handrail is interrupted by doorways or newels at changes in direction.

3.4.6.5.  Guards

(1)  Every exit shall have a wall or a well-secured guard on each side.

(2)  Except as required by Sentence (4), the height of guards for exit stairs shall be not less than 920 mm measured vertically to the top of the guard from a line drawn through the outside edges of the stair nosings and 1 070 mm around landings.

(3)  Exit ramps and their landings shall be protected with guards not less than 1 070 mm measured vertically to the top of the guard from the ramp surface where the difference in elevation between the adjacent ground or floor level and the ramp is more than 600 mm.

(4)  The height of guards for exterior stairs and landings more than 10 m above adjacent ground level shall be not less than 1 500 mm measured vertically to the top of the guard from a line drawn through the outside edges of the stair nosings.

(5)  Except as provided in Sentence (6), openings through any guard which is required by Sentence (1) shall be of a size which will prevent the passage of a sphere having a diameter more than 100 mm unless it can be shown that the location and size of openings which exceed this limit do not represent a hazard.

(6)  Openings through any guard which is required by Sentence (1) and which is installed in a building of industrial occupancy shall be of a size which will prevent the passage of a sphere having a diameter more than 200 mm unless it can be shown that the location and size of openings which exceed this limit do not represent a hazard.

(7)  In a stairway, a window for which the distance measured vertically between the bottom of the window and a line drawn through the outside edges of the stair nosings is less than 900 mm, or a window that extends to less than 1 070 mm above the landing, shall

(a)	be protected by a guard that is

(i)	located approximately 900 mm above a line drawn through the outside edges of the stair nosings, or

(ii)	not less than 1 070 mm high measured to the top of the guard from the surface of the landing, or

(b)	be fixed in position and designed to resist the lateral design loads specified for guards and walls in Articles 4.1.10.1. and 4.1.10.3.

(8)  Unless it can be shown that the location and size of openings do not present a hazard, a guard shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above the level being protected by the guard will facilitate climbing.

3.4.6.6.  Ramp Slope

(1)  Except as required for aisles by Article 3.3.2.4., the maximum slope of a ramp shall be

(a)	1 in 10 in any assembly occupancy, care or detention occupancy or residential occupancy,

(b)	1 in 6 in rooms or floor areas classified as mercantile occupancy or industrial occupancy,

(c)	1 in 8 in any other floor area, and

(d)	1 in 10 for an exterior ramp.

3.4.6.7.  Treads and Risers

(1)  Except as permitted for dwelling units and by Sentence 3.4.7.5.(1) for fire escapes, steps for stairs shall have a run of not less than 255 mm and not more than 355 mm between successive steps.

(2)  Steps for stairs referred to in Sentence (1) shall have a rise between successive treads not less than 125 mm and not more than 200 mm.

(3)  Treads and risers in every exit stair, except a fire escape stair, shall have uniform run and rise in any one flight, and shall not alter significantly in run and rise in successive flights in any stair system.

(4)  The leading edge of a stair tread shall have either a radius or a bevel between 8 mm and 13 mm in horizontal dimension.

(5)  The front edge of stair treads in exits and public access to exits shall be at right angles to the direction of exit travel.

3.4.6.8.  Curved Stairs

(1)  Except as permitted by Sentence (2), tapered treads shall not be used in an exit.

(2)  A curved stair used as an exit shall have

(a)	a handrail on each side,

(b)	treads with a minimum run of 240 mm exclusive of nosings,

(c)	treads that conform to Article 3.4.6.7. where they are measured 230 mm away from the handrail at the narrow end of the tread, and

(d)	an inside radius that is not less than twice the stair width.

3.4.6.9.  Horizontal Exits

(1)  Except in an elementary or secondary school which is subdivided by a firewall, the floor area on each side of a horizontal exit shall be sufficient to accommodate the occupants of both floor areas, allowing not less than 0.5 m2 of clear floor space per person, except that 1.5 m2 shall be provided for each person in a wheelchair and 2.5 m2 for each patient in bed.

(2)  If vestibules, enclosed balconies or bridges are used as parts of a horizontal exit, their clear width shall be not less than that of the exit doorways opening into them, except that handrails are not permitted to project into this clear width more than 100 mm.

(3)  In a horizontal exit where there is a difference in level between the connected floor areas, slopes not more than those specified for ramps in Article 3.4.6.6. are permitted to be used.

(4)  No stairs or steps shall be used at a horizontal exit.

(5)  If 2 doors are provided in a horizontal exit that comprises a part of the required number of exits from the floor areas on both sides of the exit

(a)	the doors shall be mounted adjacent to each other with the door on the right side in the direction of travel through the horizontal exit swinging in the direction of travel through the horizontal exit, and

(b)	signs shall be provided on each side of the horizontal exit to indicate the door that swings in the direction of travel from that side.

(6)  If a horizontal exit utilizes bridges between buildings or outside balconies, the bridges or balconies shall conform to Article 3.2.3.18.

(7)  Any change in floor level from one side of a horizontal exit to the other side shall not exceed 2 000 mm.

3.4.6.10.  Doors

(1)  The distance between a stair riser and the leading edge of a door during its swing shall be not less than 300 mm.

(2)  No exit door shall open directly onto a step except that, if there is danger of blockage from ice or snow, an exit door is permitted to open onto not more than one step which shall be not more than 150 mm high.

(3)  Exit doors shall be clearly identifiable.

(4)  No door leaf in an exit doorway with more than one leaf shall be less than 600 mm wide.

3.4.6.11.  Direction of Door Swing

(1)  Except as permitted by Sentences (2), (3) and Article 3.4.6.13., every exit door shall

(a)	open in the direction of exit travel, and

(b)	swing on its vertical axis.

(2)  A door serving a single dwelling unit shall swing on its vertical axis.

(3)  Except in a high hazard industrial occupancy, an exit door need not swing in the direction of exit travel where it serves

(a)	a room, suite or floor area having an occupant load of not more than 60 persons, or

(b)	as part of a means of egress from more than one floor area and the floor areas so served have a total occupant load of not more than 60 persons.

3.4.6.12.  Self-Closing Devices

(1)  An exit door that is normally required to be kept closed

(a)	shall be provided with a self-closing mechanism, and

(b)	shall not be secured in an open position except as permitted by Sentence 3.1.8.12.(1).

3.4.6.13.  Sliding Doors

(1)  Except as permitted by Sentence (2) an exit door leading directly to outdoors at ground level is permitted to be a sliding door provided it is released in conformance with Sentence 3.3.1.11.(1).

(2)  An exit door serving a Group B, Division 1 occupancy, or an impeded egress zone in other occupancies, is permitted to be a sliding door that does not conform to Sentence 3.3.1.11.(1) provided it is designed to be released in conformance with Article 3.3.1.12.

3.4.6.14.  Revolving Doors

(1)  Except as permitted by Sentence (3), a revolving door, if used, shall

(a)	be collapsible,

(b)	have hinged doors providing equivalent exiting capacity located adjacent to it,

(c)	be used as an exit from the ground floor level only,

(d)	be not less than 3 m from the foot of any stairway, and

(e)	have all glass in door leaves and enclosure panels conforming to

(i)	CAN/CGSB-12.1-M, “Tempered or Laminated Safety Glass”, or

(ii)	CAN/CGSB-12.11-M, “Wired Safety Glass”.

(2)  Except as permitted by Sentence (3), a revolving door shall not be considered to have an exiting capacity for more than 45 persons.

(3)  An electrically powered revolving door is not required to conform to Sentences (1) and (2) provided

(a)	the door leaves will collapse and stop automatic rotation of the door system and not obstruct the doorway if a force not more than that specified in Sentence 3.4.6.15.(2) is applied at the centre of a door leaf,

(b)	the door leaves are capable of being opened from inside the building without requiring keys, special devices, or specialized knowledge of the door opening mechanism,

(c)	the allowable exiting capacity is based on the clear width of passage through the door enclosure when the doors are fully collapsed,

(d)	a permanent sign, whose centreline is between 1 000 mm and 1 500 mm above the floor, is placed on each face of each door leaf indicating the method for collapsing the door leaf in an emergency, and

(e)	glass used for door leaves and enclosure panels is safety glass conforming to

(i)	CAN/CGSB-12.1-M, “Tempered or Laminated Safety Glass”, or

(ii)	CAN/CGSB-12.11-M, “Wired Safety Glass”.

3.4.6.15.  Door Release Hardware

(1)  Except for dwelling units, and except for devices on doors serving a contained use area or an impeded egress zone designed to be released in conformance with Article 3.3.1.12., and except as permitted by Sentence (4), locking, latching and other fastening devices on every exit door shall permit the door to be readily opened from the inside with not more than one releasing operation and without requiring keys, special devices or specialized knowledge of the door opening mechanism.

(2)  If a door is equipped with a latching mechanism, a device that will release the latch and allow the door to swing wide open when a force of not more than 90 N is applied to the device in the direction of travel to the exit shall be installed on

(a)	every exit door from a floor area containing an assembly occupancy having an occupant load more than 100,

(b)	every door leading to an exit lobby from an exit stair shaft, and every exterior door leading from an exit stair shaft in a building having an occupant load more than 100, and

(c)	every exit door from a floor area containing a high hazard industrial occupancy.

(3)  Except as required by Sentence 3.8.3.3.(7), every exit door shall be designed and installed so that, when the latch is released, the door will open under a force of not more than 90 N, applied at the knob or other latch releasing device.

(4)  Electromagnetic locks that do not incorporate latches, pins or other similar devices to keep the door in the closed position are permitted to be installed on exit doors other than doors described in Sentence (5) provided

(a)	the building is equipped with a fire alarm system conforming to Subsection 3.2.4.,

(b)	the locking device, and all similar devices in the access to exit leading to the exit door, are installed as ancillary devices to the fire alarm system and release immediately upon activation of

(i)	the alarm signal where a single stage fire alarm system is installed,

(ii)	except as provided in Subclause (iii), the alert signal where a 2 stage fire alarm system is installed, or

(iii)	the alarm signal of a 2 stage fire alarm system installed in a care or detention occupancy,

(c)	the locking device releases immediately upon loss of power to the fire alarm control panel or loss of power controlling the electromagnetic locking mechanism and its associated auxiliary controls,

(d)	the locking device releases immediately upon actuation of a manually operated switch readily accessible only to authorized personnel and located near the main entrance of the building or in the central alarm and control facility of Sentence 3.2.6.12.(1),

(e)	the locking device releases immediately upon a fault being detected in the electrical circuit between the fire alarm control panel and the controller of the locking device,

(f)	the locking device releases immediately upon the operation of a manual pull station for the fire alarm system located on the wall not more than 600 mm from the door,

(g)	a legible sign having the words EMERGENCY EXIT UNLOCKED BY FIRE ALARM is permanently mounted on the door,

(h)	the lettering on the sign required in Clause (g) is at least 25 mm high with a 5 mm stroke,

(i)	upon release, the locking device must be reset manually by the actuation of the switch referred to in Clause (d),

(j)	the operation of any by-pass switch, where provided for testing of the fire alarm system, causes an audible signal and a visual signal to be indicated at the fire alarm annunciator panel and at the monitoring station of Clauses 3.2.4.7.(4)(a), (b) or (c), and

(k)	emergency lighting is provided at the doors.

(5)  Except as permitted in Sentences (6) and (6.1), electromagnetic locks are not permitted to be installed on exit doors

(a)	described in Clauses 3.4.6.15.(2)(a), (b) or (c),

(b)	serving an elementary or secondary school, or

(c)	leading directly from a high hazard industrial occupancy.

(6)  Electromagnetic locks are permitted to be installed on an exterior door leading from an exit stairway in a building serving only a Group B, Division 2 major occupancy or a Group B, Division 3 major occupancy.

(6.1)  Electromagnetic locks are permitted to be installed on an exit door that serves only a gaming premise if

(a)	the gaming premise is located within a sprinklered floor area,

(b)	smoke detectors are installed in each room and each corridor accessible to the public,

(c)	a force of not more than 90 N applied to the door opening hardware initiates an irreversible process that will release the locking device within 15 s and not relock until the door has been opened, and

(d)	a legible sign conforming with Clause (4) (h) is permanently mounted on the exit door to indicate that the locking device will release within 15 s of applying pressure to the door release hardware.

(7)  Door hardware for the operation of the doors referred to in this Section shall be installed at a height not more than 1 200 mm above the finished floor.

3.4.6.16.  Reserved

3.4.6.17.  Emergency Access to Floor Areas

(1)  In a building more than 6 storeys in building height

(a)	except as permitted by Sentence (3), doors providing access to floor areas from exit stairs shall not have locking devices to prevent entry into

(i)	any floor area designated as an area of refuge,

(ii)	floor areas located at intervals of 5 storeys or less, and

(iii)	at least one of the three highest storeys,

(b)	doors referred to in Clause (a) that provide access into the floor area shall be identified by a sign on the stairway side to indicate that they are openable from that side, and

(c)	a master key to fit all door locking devices that are intended to prevent entry into a floor area from an exit stair shall be provided in a designated location accessible to firefighters, or the door shall be provided with a wired glass panel not less than 0.0645 m2 in area and located not more than 300 mm from the door opening hardware.

(2)  If access to floor areas through unlocked doors is required by Clause (1)(a) or through electromagnetically locked doors as permitted by Sentence (3), it shall be possible for a person entering the floor area to have access through unlocked doors or through electromagnetically locked doors within the floor area to at least one other exit.

(3)  Electromagnetic locking devices may be installed on the doors providing access to floor areas from exit stairs as required by Clause (1)(a), provided all locking device release and signage provisions in Sentence 3.4.6.15.(4) are installed on both sides of the doors.

(4)  In a building not more than 6 storeys in building height, doors providing access from exit stairs to a floor area containing a hotel are permitted to have locking devices to prevent entry into the floor area provided the requirements in Clause (1)(c) are complied with.

3.4.6.18.  Floor Numbering

(1)  Arabic numerals indicating the assigned floor number shall

(a)	be mounted permanently on each side of doors to exit stair shafts,

(b)	be not less than 60 mm high, raised approximately 0.7 mm above the surface,

(c)	be located 1 500 mm from the finished floor, and

(d)	be contrasting in colour with the surface to which they are applied.

(2)  Upper case letters indicating the designation assigned to each exit stair shaft shall be mounted permanently on each side of doors to the exit stair shaft and shall

(a)	be not less than 60 mm high, raised approximately 0.7 mm above the surface,

(b)	be located 1 500 mm from the finished floor, and

(c)	be contrasting in colour with the surface on which they are applied.

3.4.7. Fire Escapes

3.4.7.1.  Scope

(1)  Except as permitted by Sentence (2), fire escapes shall not be erected on a building.

(2)  If it is impracticable to provide one or more of the exit facilities listed in Article 3.4.1.4., fire escapes conforming to Articles 3.4.7.2. to 3.4.7.7. are permitted to serve floor areas in an existing building provided the floor areas served are

(a)	not in an elementary or secondary school,

(b)	not more than 2 storeys above ground level in care or detention occupancies, and

(c)	not more than 5 storeys above ground level in other occupancies.

3.4.7.2.  Fire Escape Construction

(1)  Fire escapes shall be of metal or concrete, of the stair type extending to ground level, constructed throughout in a strong substantial manner and securely fixed to the building, except that wooden fire escapes are permitted to be used on buildings of combustible construction if all posts and brackets are not less than 89 mm in their least dimension and all other woodwork is not less than 38 mm in its least dimension.

3.4.7.3.  Access to Fire Escapes

(1)  Access to fire escapes shall be from corridors through doors at floor level, except that access from a dwelling unit is permitted to be through a casement window having an unobstructed opening not less than 1 100 mm high by 550 mm wide with a sill height of not more than 900 mm above the inside floor.

(2)  The clear area of a fire escape balcony onto which a door opens, shall be not less than 1 m2.

3.4.7.4.  Protection of Fire Escapes

(1)  If a fire escape serves any storey above the second, openings located in a zone described in Sentence (2), including access doorways in the exterior walls of the building to which the fire escape is attached, shall be protected by closures conforming to Subsection 3.1.8.

(2)  The zone referred to in Sentence (1) extends from any balcony, platform or stairway of a fire escape to a distance

(a)	3 m horizontally,

(b)	10 m below, and

(c)	1 800 mm above.

3.4.7.5.  Stairs

(1)  Stairs shall be inclined at an angle of not more than 45° with the horizontal, and their steps shall have risers not more than 210 mm high and treads not less than 220 mm wide exclusive of nosing.

(2)  Stairway headroom shall be not less than 1 950 mm plus the height of one riser measured vertically above the nosing of any tread or platform.

(3)  The width of a fire escape shall conform to Sentence 3.4.3.1.(1), except that the width is permitted to be reduced to 550 mm provided the fire escape serves

(a)	not more than 3 storeys, and

(b)	not more than 15 persons.

(4)  If a flight of stairs leading to the ground at the foot of a fire escape is not fixed in position, it shall

(a)	be held in the raised position without a latch or locking device,

(b)	be fitted with a counterbalancing device,

(c)	be easily and quickly brought into position for use, and

(d)	reach the ground in the lowered position.

3.4.7.6.  Guards and Railings

(1)  The open sides of every platform, balcony and stairway forming part of a fire escape shall be protected by guards not less than 920 mm high measured vertically above the nosing of any tread or platform.

(2)  The top rail of a guard is permitted to serve as a handrail if it is free from obstructions which could break a handhold.

(3)  A wall handrail shall be installed if the fire escape is more than 550 mm wide.

(4)  Openings through any guard which is required by Sentence (1) shall be of a size which will prevent the passage of a sphere having a diameter more than 100 mm unless it can be shown that the location and size of openings which exceed this limit do not represent a hazard.

(5)  Unless it can be shown that the location and size of openings do not present a hazard, a guard for a fire escape shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above a platform or the nosing of any tread will facilitate climbing.

3.4.7.7.  Landings

(1)  Platforms for a fire escape shall be provided in conformance with the requirements for stair landings in Article 3.4.6.3.

Section 3.5. Vertical Transportation

3.5.1. General

3.5.1.1.  Scope

(1)  This Section applies to vertical transportation facilities installed in a building, including elevators, escalators and dumbwaiters.

(2)  Elevators in a building within the scope of Subsection 3.2.6. shall conform to Articles 3.2.6.8. and 3.2.6.9.

3.5.2. Elevator Required

3.5.2.1.  Elevator for Group B, Division 2 and 3 Occupancies

(1)  In a Group B, Division 2 or 3 occupancy, if sleeping rooms or patient or resident services are provided on more than one floor level and the floor levels are not connected by ramps conforming to Article 3.8.3.4., such floor levels shall be served by at least one elevator that

(a)	is large enough to accommodate a stretcher in a horizontal position, and

(b)	conforms to Appendix E of CSA-B44 “Safety Code for Elevators, Escalators, Dumbwaiters, Moving Walks and Freight Platforms Lifts”.

3.5.3. Fire Separations

3.5.3.1.  Fire Separations for Elevator Hoistways

(1)  A vertical service space used as an elevator hoistway shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.5.3.1. for the fire-resistance rating required by Subsection 3.2.2. for

(a)	the floor assembly above the storey, or

(b)	the floor assembly below the storey, if there is no floor assembly above.

3.5.3.2.  Vertical Service Spaces for Dumbwaiters

(1)  A vertical service space containing a dumbwaiter shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.5.3.1. for the fire-resistance rating required by Subsection 3.2.2. for

(a)	the floor assembly above the storey or

(b)	the floor assembly below the storey, if there is no floor assembly above.

Table 3.5.3.1.

Fire Separation for Vertical Transportation Space

Forming Part of Articles 3.5.3.1. and 3.5.3.2.

| Fire-Resistance Rating of Fire Separation Required for Floor Assembly | Minimum Fire-Resistance Rating of Vertical Service Space for Elevator Hoistway | Minimum Fire-Resistance Rating of Vertical Service Space for Dumbwaiters |
| --- | --- | --- |
| less than 45 min | 45 min | — |
| 45 min | 45 min | 45 min |
| 1 h | 1 h | 45 min |
| 1.5 h | 1 h | 1 h |
| 2 h or more | 1.5 h | 1 h |
| Column 1 | 2 | 3 |

3.5.3.3.  Fire Separations for Elevator Machine Rooms

(1)  Except as permitted by Sentence (2), a room containing elevator machinery shall be separated from all other parts of the building by a fire separation having a fire-resistance rating not less than that required for the vertical service space containing the elevator hoistway.

(2)  A room containing elevator machinery need not be separated from the elevator hoistway that it serves provided the room and the hoistway are separated from all other parts of the building by a fire separation having a fire-resistance rating not less than that required for the vertical service space containing the elevator hoistway.

3.5.4. Dimensions and Signs

3.5.4.1.  Elevator Car Dimensions

(1)  If an elevator is installed to conform to the requirements of Article 3.3.1.7., or if one or more elevators are provided in a building more than three storeys in building height, each storey having elevator service shall be served by at least one elevator which has inside dimensions that will accommodate and provide adequate access for a patient stretcher 2 010 mm long and 610 mm wide in the prone position.

(2)  An elevator satisfying the requirements of Sentence (1) shall be clearly identified on the main entrance level of the building.

Section 3.6. Service Facilities

3.6.1. General

3.6.1.1.  Scope

(1)  The provisions of this Section apply to horizontal service spaces, vertical service spaces, attic or roof spaces, ducts, crawl spaces, shaft spaces, service rooms, and mechanical penthouses, and facilities contained therein.

(2)  Except for plenum requirements in 3.6.4.3., the fire safety characteristics of heating, ventilating and air-conditioning systems shall comply with Part 6.

3.6.1.2.  Reserved

3.6.1.3.  Storage Use Prohibition

(1)  Service spaces shall not be designed to facilitate subsequent use as storage space.

3.6.1.4.  Reserved

3.6.1.5.  Fixed Access Ladders

(1)  If a fixed ladder is installed to provide access to a roof of a building, the design and installation of the attachment and anchorage system for the ladder shall be as described in the Supplementary Guidelines.

3.6.2. Service Rooms

3.6.2.1.  Fire Separations around Service Rooms

(1)  Except as permitted by Article 3.6.2.2., a fuel-fired appliance in a building containing a Group B or Group F, Division 1 occupancy shall be located in a service room which shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than

(a)	2 h if the building is more than 2 storeys in building height or more than 400 m2 in building area, or

(b)	1 h if the building is neither more than 2 storeys in building height nor more than 400 m2 in building area.

(2)  Except as permitted by Article 3.6.2.2., a fuel-fired appliance in a building not containing a Group B or Group F, Division 1 occupancy shall be located in a service room which shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h if the building is more than 2 storeys in building height or more than 400 m2 in building area.

(3)  A solid fuel-fired appliance shall not be located in a repair garage, a storage garage or any other location where the appliance could be exposed to flammable vapours or gases unless

(a)	it is enclosed in a service room which is

(i)	separated from the remainder of the building in conformance with Sentence (1) or Sentence (2), and

(ii)	supplied with combustion air directly from outside the building, and

(b)	the heat generated by the appliance is supplied indirectly to the space served by means of ducts or piping.

(4)  The fire separation requirements of Sentence (1) or Sentence (2) shall apply to a service room intended to contain equipment that uses a liquid having a flash point below 93.3°C.

(5)  Except as permitted by Article 3.6.2.2., a service room used for a purpose not described in Sentences (1), (2), (3), or (4) and Articles 3.6.2.5., 3.6.2.6. and 3.6.2.8. shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(6)  Sentence (5) shall apply to a room that contains electrical equipment that is required to be located in a service room by a regulation made under the Electricity Act, 1998.

(7)  The fire separation provisions for a fuel-fired appliance in a portable classroom shall conform to Article 3.9.3.7.

3.6.2.2.  Waiver of Fire Separations

(1)  A fire separation is not required between a fireplace and the space it serves.

(2)  A fire separation is not required between a roof-top appliance and the building it serves.

(3)  Except for buildings classified as Group B or Group F, Division 1 occupancies, the fire separations required by Sentence 3.6.2.1.(2) need not be provided for fuel-fired appliances that serve not more than one room or suite, provided the appliances are not solid fuel-fired appliances referred to in Sentence 3.6.2.1.(3).

(4)  The fire separation required by Sentence 3.6.2.1.(5) need not be provided if the service room is located in a floor area that is sprinklered.

(5)  If a room contains a limited quantity of service equipment, and the service equipment does not constitute a fire hazard, the requirements of Sentence 3.6.2.1.(5) for a fire separation shall not apply.

3.6.2.3.  Service Rooms under Exits

(1)  A service room containing service equipment subject to possible explosion, such as boilers operating in excess of 100 kPa (gauge) and some types of refrigerating machinery and transformers, shall not be located directly under a required exit.

3.6.2.4.  Service Equipment

(1)  A service room containing space heating, space cooling and service water heating appliances is permitted to contain other service equipment such as electrical service equipment.

3.6.2.5.  Incinerator Rooms

(1)  A service room containing an incinerator shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 2 h.

(2)  A service room containing an incinerator shall not contain other fuel-fired appliances.

3.6.2.6.  Combustible Refuse Storage

(1)  Except as required by Sentence 3.6.3.3.(9), a room for the storage of combustible refuse shall be

(a)	separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 1 h, and

(b)	sprinklered.

3.6.2.7.  Door Swing for Service Rooms

(1)  A swing-type door from a service room containing a boiler or incinerator shall swing outward from the room, except that the door shall swing inward if the door opens onto a corridor or any room used for an assembly occupancy.

3.6.2.8.  Electrical Equipment Vaults

(1)  Where an electrical equipment vault is required by a regulation made under the Electricity Act, 1998, the electrical equipment vault shall be totally enclosed by a fire separation of solid masonry or concrete construction having a fire-resistance rating of not less than 3 h if the vault is not provided with an automatic fire extinguishing system and not less than 2 h if the vault is so protected.

(2)  Where a building is required to be sprinklered, the electrical equipment vault described in Sentence (1) need not be sprinklered provided

(a)	the vault is designed for no purpose other than to contain the electrical equipment, and

(b)	a smoke detector is provided in the vault which will actuate the building fire alarm system in the event of a fire in the vault.

(3)  A vault, which is part of a building and houses electrical equipment indoors, shall have

(a)	roofs or ceilings consisting of reinforced concrete of adequate strength for the conditions and not less than 150 mm thick, and

(b)	floors consisting of reinforced concrete of adequate strength for the conditions and not less than 150 mm thick, except that floors which are at excavation level are permitted to be of reinforced concrete not less than 100 mm thick.

(4)  Walls, roofs or ceilings, and floors shall be adequately anchored together in a manner designed to resist dislodgement by explosion.

(5)  Only pipes or ducts necessary for fire protection or the proper operation of the electrical installation shall penetrate the fire separations surrounding the electrical equipment vault.

(6)  A ventilation duct or opening, which penetrates the fire separation to the outdoors, need not be protected by a closure at the penetration.

(7)  Each door to an electrical equipment vault shall be provided with a substantial lock or padlock.

(8)  Explosion-relief devices and vents or other protective measures shall be provided for every electrical equipment vault containing dielectric liquid filled electrical equipment in conformance with Sentence 3.3.1.19.(2).

(9)  Every electrical equipment vault shall be provided with a ventilation system designed in conformance with Part 6 to prevent the ambient temperature in the vault from exceeding 40°C.

(10)  Where the vault ventilation system in Sentence (9) is directly from an outdoor area by natural ventilation without the use of ducts, and where the electrical equipment is the principal source of heat, the combined net area of inlet and outlet openings shall be not less than 0.002 m2/kVa of electrical equipment capacity with a minimum of 0.093 m2, except that

(a)	where equipment in the power class as described in CAN3-C88, “Power Transformers and Reactors” is installed, ventilation requirements are permitted to be based on the actual full-load losses, or

(b)	where the equipment is installed for emergency purposes only and is not normally energized, it need not be considered in determining the ventilation requirements.

(11)  In the vault ventilation system in Sentence (10), the inlet for fresh air shall lead from an outdoor area and shall terminate at a point not more than 1 000 mm above the floor level of the vault.

(12)  Where the vault ventilation system in Sentence (9) is a mechanical system, it shall be separate from the system for the remainder of the building and shall be designed so that

(a)	the vault temperature is thermostatically controlled,

(b)	the fan is located so that it may be serviced without danger to personnel,

(c)	a high temperature alarm is provided in the vault,

(d)	the system is automatically shut off in the event of a fire in the vault, and

(e)	a filter is provided in the air inlet if there is a possibility of dirt being drawn in.

(13)  All ventilation openings shall be protected in conformance with Sentences 6.2.3.17.(4) and (5) and the protection shall be installed in such a manner that it cannot be removed from the outside by the use of common tools and it is tamperproof.

(14)  Except as permitted in Sentence (15), the floor of the electrical equipment vault described in Sentences (1) and (2) shall be liquid tight and surrounded by liquid tight walls and sills of sufficient height to confine within the vault all of the liquid from the largest item of electrical equipment, but to a height of not less than 100 mm.

(15)  The floor of the electrical equipment vault described in Sentences (1) and (2) may be provided with a floor drain connected to a covered sump capable of holding all of the liquid from the largest item of electrical equipment, and the connection shall have a noncombustible trap to prevent the spread of fire from the vault to the sump.

3.6.2.9.  Storage of Oxygen Containers

(1)  In a Group B, Division 2 or 3 occupancy, a room for the storage of oxygen containers shall be

(a)	separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h,

(b)	designed for the storage of oxygen containers only,

(c)	vapour tight,

(d)	lined with noncombustible finish,

(e)	separately exhausted to the exterior, and

(f)	equipped with racks to store the containers.

3.6.3. Vertical Service Spaces and Service Facilities

3.6.3.1.  Fire Separations for Vertical Service Spaces

(1)  Except as required by Section 3.5., a vertical service space shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.6.3.1. for the fire-resistance rating required by Subsection 3.2.2. for

(a)	the floor assembly above the storey, or

(b)	the floor assembly below the storey, if there is no floor assembly above.

(2)  A vertical service space that does not extend through the roof of a building shall be enclosed at the top with construction having a fire-resistance rating not less than that required for the vertical service space walls.

Table 3.6.3.1.

Fire Separations for Vertical Service Space

Forming Part of Sentence 3.6.3.1.(1)

| Fire-Resistance Rating of Fire Separation Required for Floor Assembly | Minimum Fire-Resistance Rating of Vertical Service Space |
| --- | --- |
| less than 45 min | — |
| 45 min | 45 min |
| 1 h | 45 min |
| 1.5 h | 1 h |
| 2 h or more | 1 h |
| Column 1 | 2 |

(3)  A vertical service space that does not extend to the bottom of a building shall be enclosed at the lowest level with construction having a fire-resistance rating not less than that required for the vertical service space walls.

(4)  A vent from a vertical service space not extending to the roof shall be enclosed within the building with construction having a fire-resistance rating not less than that required for the vertical service space walls.

(5)  Only openings that are necessary for the use of the vertical service space shall be permitted through a vertical service space enclosure.

3.6.3.2.  Foamed Plastic Protection

(1)  Foamed plastic insulation in a vertical service space shall be protected in conformance with Article 3.1.5.11.

3.6.3.3.  Linen and Refuse Chutes

(1)  A linen chute or refuse chute shall

(a)	be impervious to moisture,

(b)	have a smooth internal surface,

(c)	be corrosion-resistant,

(d)	be constructed of noncombustible material, and

(e)	be located in a shaft in which there are no services other than noncombustible drain, waste and vent piping or noncombustible water piping.

(2)  A shaft containing a linen chute or refuse chute shall have a fire-resistance rating conforming to Sentence 3.6.3.1.(1), but not less than

(a)	1 h if the chute outlet for the discharge room is protected by an automatic, self-latching closure held open by a fusible link, or

(b)	2 h if no closure is provided at the chute outlet into the discharge room.

(3)  An interior linen chute or refuse chute shall extend not less than 1 000 mm above the roof and shall be vented above the roof with a vent which

(a)	has an unobstructed area not less than the cross-sectional area of the chute, and

(b)	is equipped with a cover that will open automatically, or that can be opened manually, in the event of a fire in the chute.

(4)  Intake openings for a linen chute or a refuse chute shall

(a)	have an area not more than 60% of the cross-sectional area of the chute, and

(b)	be fitted with closures designed to close automatically and latch after use.

(5)  Intake openings for a linen chute or a refuse chute shall be located in rooms or compartments that

(a)	have no dimension less than 750 mm,

(b)	are separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 45 min,

(c)	are designed for no other purpose, and

(d)	do not open directly into an exit.

(6)  Sprinklers shall be installed at the top of each linen chute or refuse chute, at alternate floor levels and in the room or bin into which the chute discharges.

(7)  The room into which a linen chute discharges shall be separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 1 h.

(8)  A refuse chute shall be equipped at the top with spray equipment for washing-down purposes.

(9)  A refuse chute shall discharge only into a room or bin separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 2 h.

(10)  The room or bin into which a refuse chute discharges shall be of sufficient size to contain the refuse between normal intervals of emptying, be impervious to moisture and be equipped with a water connection and floor drain for washing-down purposes.

(11)  A room into which a refuse chute discharges shall contain no service equipment that is not related to refuse handling and disposal.

3.6.3.4.  Exhaust Duct Negative Pressure

(1)  If a vertical service space contains an exhaust duct that serves more than one fire compartment, the duct shall have a fan located at or near the exhaust outlet to ensure that the duct is under negative pressure.

3.6.4. Horizontal Service Spaces and Service Facilities

3.6.4.1.  Scope

(1)  This Subsection applies to horizontal service spaces and service facilities, including ceiling spaces, duct spaces, crawl spaces and attic or roof spaces.

3.6.4.2.  Fire Separations for Horizontal Service Spaces

(1)  A horizontal service space that penetrates a required vertical fire separation shall be separated from the remainder of the building it serves in conformance with Sentence (2).

(2)  If a horizontal service space or other concealed space is located above a required vertical fire separation other than a vertical shaft, this space need not be divided at the fire separation as required by Article 3.1.8.3. provided the construction between this space and the space below is a fire separation with a fire-resistance rating equivalent to that required for the vertical fire separation, except that the fire-resistance rating is permitted to be not less than 30 min if the vertical fire separation is not required to have a fire-resistance rating more than 45 min.

3.6.4.3.  Plenum Requirements

(1)  A concealed space used as a plenum within a floor assembly or within a roof assembly need not conform to Sentence 3.1.5.14.(1) and Article 6.2.3.2. provided

(a)	all materials within the concealed space have a flame-spread rating not more than 25 and a smoke developed classification not more than 50, except for

(i)	tubing for pneumatic controls,

(ii)	optical fibre cables and electrical wires and cables that exhibit a flame spread not more than 1.5 m, a smoke density not more than 0.5 at peak optical density and a smoke density not more than 0.15 at average optical density when tested in conformance with the Flame and Smoke Test in the Appendix to CAN/CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT6 Rating),

(iii)	optical fibre cables and electrical wires and cables that are located in totally enclosed noncombustible raceways, and

(iv)	Reserved

(v)	single conductor electrical wires and cables that exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test – Cables in Cabletrough in Clause 4.11.4. of CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT4 Rating), and

(b)	the supports for the ceiling membrane are of noncombustible material having a melting point not below 760°C.

(2)  If a concealed space referred to in Sentence (1) is used as a return-air plenum and incorporates a ceiling membrane that forms part of the required fire-resistance rating of the assembly, every opening through the membrane shall be protected by a fire stop flap which shall

(a)	stop the flow of air into the concealed space in the event of a fire,

(b)	be supported in a manner that will maintain the integrity of the ceiling membrane for the duration of time required to provide the required fire-resistance rating, and

(c)	conform to CAN4-S112.2-M, “Standard Method of Fire Test of Ceiling Firestop Flap Assemblies”.

(3)  Asbestos paper shall not be exposed in supply and return-air systems.

3.6.4.4.  Attic or Roof Space Access

(1)  An attic or roof space more than 600 mm high shall be provided with access from the floor immediately below by a hatchway not less than 550 mm by 900 mm or by a stairway.

3.6.4.5.  Horizontal Service Space Access

(1)  A horizontal service space, consisting of ceiling and duct spaces, which is more than 1 200 mm high and 600 mm wide shall have inspection doors not less than 300 mm in both horizontal and vertical dimensions placed so that the entire interior of the duct or space can be viewed.

3.6.4.6.  Crawl Space Access

(1)  A crawl space shall have at least one access opening not less than 550 mm by 900 mm.

Section 3.7. Health Requirements

3.7.1. Height and Area of Rooms

3.7.1.1.  Room and Space Height

(1)  The height of every room and space shall be sufficient that

(a)	adequate light and air are provided for the intended occupancy, and

(b)	no obstruction to movement or activities below is caused by the ceiling or ceiling fixtures.

(2)  The unobstructed height in dwelling units and sleeping rooms in Group C occupancies shall conform to Part 9.

3.7.1.2.  Residential Room Dimensions

(1)  The areas of rooms in dwelling units, dormitories, boarding houses and rooming houses shall conform to Part 9.

3.7.1.3.  Sleeping Areas in Group B and Child Care Facilities

(1)  Except as provided in Sentence (2), a sleeping area in a Group B occupancy shall provide not less than 4.7 m2 per person in a room having

(a)	an area not less than 7 m2,

(b)	a horizontal dimension not less than 2 000 mm, and

(c)	a ceiling height not less than 2 300 mm.

(2)  Sleeping rooms for residents in nursing homes shall have, exclusive of space provided for washrooms and for built-in or portable clothes closets, a floor space not less than

(a)	10.22 m2 in a single-bed unit,

(b)	16.72 m2 in a two-bed unit,

(c)	25.08 m2 in a three-bed unit, and

(d)	29.73 m2 in a four-bed unit.

(3)  A child care facility shall provide sleeping accommodation having not less than 0.93 m2 of floor surface area for each child with not less than 2 300 mm ceiling height over the entire room area.

3.7.1.4.  Sleeping Areas in Camps

(1)  Recreational camps shall have an area in the sleeping quarters of not less than 3.72 m2 per camper or, if double or triple tier bunk units are used, 2.79 m2 per camper.

(2)  A camp for housing of workers shall have an area of not less than 3.72 m2 per employee in every room used for sleeping purposes.

3.7.2. Windows

3.7.2.1.  Window Areas

(1)  Except as provided in Sentences (2) and (3) or otherwise permitted, every room used for sleeping in any building, and every principal room such as living room, dining room or combination thereof in dwelling units shall be provided with windows having areas conforming to Part 9, except that Article 9.7.1.3 does not apply.

(2)  Nursing homes shall have

(a)	in an activity room, a sitting room or a lounge, one or more windows with a total unobstructed glass area, exclusive of skylights, of not less than 10% of the area of the room, and

(b)	in a residents’ sleeping room, one or more windows that

(i)	have a total unobstructed glass area, exclusive of skylights, of not less than 10% of the area of the room,

(ii)	open to the outdoors and have a total unobstructed glass area, exclusive of skylights, of not less than 5% of the area of the room, and

(iii)	are installed with the bottom edge of the glass of every window not more than 660 mm above the floor.

(3)  Play activity rooms in a child care facility and work areas in live/work units shall have one or more windows that conform to Clause (2)(a).

3.7.2.2.  Window Protection in Apartment Buildings

(1)  In Group C major occupancy apartment buildings protection shall be provided at windows to minimize the hazards to children in accordance with Sentences (2) to (4).

(2)  Fixed windows within dwelling units that extend to less than 1 000 mm from the floor shall be protected by guards to at least 1 000 mm above the floor, or shall be designed to withstand the lateral design loads for balcony guards in Part 4.

(3)  Except as provided in Sentence (4), in dwelling units any window located more than 2 000 mm above grade which opens within 1 500 mm of the floor shall be protected

(a)	by a guard conforming to Sentence 3.3.1.17.(3),

(b)	by

(i)	a controlled sash operation to restrict, when engaged, the opening of the operable sash to not more than 100 mm, and

(ii)	a heavy duty screen conforming to CAN/CSA-A440-M, “Windows”, or

(c)	by an alternative device which does not reduce the degree of safety provided by Clauses (a) or (b).

(4)  Protection of a window need not be provided in a dwelling unit where an exterior balcony is constructed for the full length of a window.

3.7.3. Ventilation

3.7.3.1.  Ventilation Requirements

(1)  All rooms and spaces shall be ventilated to conform with Part 6.

3.7.4. Plumbing Facilities

3.7.4.1.  Plumbing and Drainage Systems

(1)  Except as permitted in Sentence (3), each building situated on property that abuts on a street in which a public or municipal water main is located shall be provided with or have accessible to its occupants a plumbing system including a potable water supply, a sanitary drainage system and plumbing fixtures.

(2)  When the installation of a sanitary drainage system is not possible because of the absence of a water supply, sanitary privies, chemical closets or other means for the disposal of human waste shall be provided.

(3)  Plumbing fixtures need not be provided in a building which is not normally occupied by persons where such installations are impractical and other fixtures are available in nearby buildings when the subject building is in use.

3.7.4.2.  Plumbing Fixtures, General

(1)  For the purposes of this Subsection, the occupant load shall be determined in accordance with the provisions in Subsection 3.1.16. except that in a Group D occupancy, the area per person shall be 14 m2.

(2)  Except as provided in this Subsection, water closets shall be provided for each sex assuming that the occupant load is equally divided between males and females, unless the proportion of each sex expected in the building can be determined with reasonable accuracy.

(3)  Except as provided in Sentence (4), urinals are permitted to be substituted for water closets required by this Subsection for males and may be counted as water closets provided the number of urinals is not more than

(a)	one-fifth of the required number of water closets in hospitals and nursing homes, and

(b)	two-thirds of the required number of water closets in any other occupancy.

(4)  If only 2 water closets are required for males, one urinal is permitted to be substituted for one of the water closets.

(5)  Except as required in this Subsection, at least one lavatory shall be provided in a room containing one or 2 water closets or urinals, and at least one additional lavatory shall be provided for each additional 2 water closets or urinals.

(6)  Wash fountains in circular or straight trough form are permitted to be provided in lieu of required lavatories provided each 500 mm of circumference or trough length is considered to be the equivalent of one lavatory.

3.7.4.3.  Plumbing Fixtures for Assembly Occupancies

(1)  Except as permitted by Sentences (2) to (16), the number of water closets required for assembly occupancies shall conform to Table 3.7.4.3.A.

Table 3.7.4.3.A.

Water Closets for Assembly Occupancies

Forming Part of Sentence 3.7.4.3.(1)

| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| --- | --- |
| 1 to 25 | 1 |
| 26 to 50 | 2 |
| over 50 | 3 plus 1 for each additional increment of 50 persons of each sex in excess of 50 |
| Column 1 | 2 |

(2)  Except for motion picture theatres, the number of water closets required for Group A, Division 1 occupancies shall conform to Table 3.7.4.3.B.

Table 3.7.4.3.B.

Water Closets for Assembly Occupancies

Forming Part of Sentence 3.7.4.3.(2)

| Number of Persons of Each Sex | Minimum Number of Water Closets |  |
| --- | --- | --- |
|  | Male | Female |
| 1 to 50 | 1 | 2 |
| 51 to 75 | 2 | 3 |
| 76 to 100 | 2 | 4 |
| 101 to 125 | 3 | 5 |
| 126 to 150 | 3 | 6 |
| 151 to 175 | 4 | 7 |
| 176 to 200 | 4 | 8 |
| 201 to 250 | 5 | 9 |
| 251 to 300 | 5 | 10 |
| 301 to 350 | 6 | 11 |
| 351 to 400 | 6 | 12 |
| over 400 | 7 plus 1 for each additional increment of 200 males in excess of 400 | 13 plus 1 for each additional increment of 100 females in excess of 400 |
| Column 1 | 2 | 3 |

(3)  The number of water closets required shall conform to Table 3.7.4.3.C. for

(a)	motion picture theatres,

(b)	Group A, Division 3 occupancies,

(c)	Group A, Division 4 occupancies, and

(d)	outdoor pools.

Table 3.7.4.3.C.

Water Closets for Assembly Occupancies

Forming Part of Sentence 3.7.4.3.(3)

| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| --- | --- |
| 1 to 50 | 1 |
| 51 to 150 | 2 |
| 151 to 250 | 3 |
| 251 to 375 | 4 |
| 376 to 500 | 5 |
| over 500 | 6 plus 1 for each additional increment of 150 persons of each sex in excess of 500 |
| Column 1 | 2 |

(4)  The number of water closets required for dining rooms, restaurants and cafeteria shall conform to Table 3.7.4.3.D.

Table 3.7.4.3.D.

Water Closets for Assembly Occupancies

Forming Part of Sentence 3.7.4.3.(4)

| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| --- | --- |
| 1 to 20 | 1 |
| 21 to 70 | 2 |
| 71 to 105 | 3 |
| 106 to 135 | 4 |
| 136 to 165 | 5 |
| 166 to 195 | 6 |
| 196 to 225 | 7 |
| 226 to 275 | 8 |
| 276 to 325 | 9 |
| 326 to 375 | 10 |
| 376 to 425 | 11 |
| over 425 | 12 plus 1 for each additional increment of 50 persons of each sex in excess of 425 |
| Column 1 | 2 |

(5)  The number of water closets required for establishments used primarily for the consumption of alcoholic beverages which provide limited or no food service shall conform to Table 3.7.4.3.E.

Table 3.7.4.3.E.

Water Closets for Assembly Occupancies

Forming Part of Sentence 3.7.4.3.(5)

| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| --- | --- |
| 1 to 50 | 2 |
| 51 to 70 | 3 |
| 71 to 90 | 4 |
| 91 to 110 | 5 |
| 111 to 140 | 6 |
| 141 to 180 | 7 |
| 181 to 220 | 8 |
| 221 to 260 | 9 |
| over 260 | 10 plus 1 for each additional increment of 40 persons of each sex in excess of 260 |
| Column 1 | 2 |

(6)  Except as provided in Sentences (7) and (8) , in every dining room, restaurant, cafeteria and alcoholic beverage establishment having more than 40 seats, separate sanitary facilities shall be provided for employees, in addition to facilities provided for patrons, and the number of water closets and lavatories required shall conform to Table 3.7.4.3.F.

(7)  Except as provided in Sentence (8), in every dining room, restaurant, cafeteria and alcoholic beverage establishment having not more than 40 seats, patrons are permitted to share the sanitary facilities provided for employees, and the minimum number of water closets and lavatories shall conform to Table 3.7.4.3.F. based on

(a)	a male occupant load of 50% of the number of seats plus the number of male employees, and

(b)	a female occupant load of 50% of the number of seats plus the number of female employees.

Table 3.7.4.3.F.

Plumbing Fixtures for Assembly Occupancies

Forming Part of Sentences 3.7.4.3.(6) and (7)

| Number of Employees of Each Sex | Minimum Number of Water Closets and Lavatories |  |
| --- | --- | --- |
|  | Male | Female |
| 1 to 9 | 1 | 1 |
| 10 to 24 | 2 | 2 |
| 25 to 49 | 3 | 3 |
| 50 to 74 | 4 | 4 |
| 75 to 100 | 5 | 5 |
| over 100 | 6 plus 1 for each additional increment of 30 male employees in excess of 100 | 6 plus 1 for each additional increment of 30 female employees in excess of 100 |
| Column 1 | 2 | 3 |

(8)  Where the total number of employees is not more than 5, the same room may be used by both female and male employees provided the door to the room can be locked from the inside.

(9)  The number of employees in Sentences (6), (7) and (8) shall be the maximum number of employees who are normally present on the premises at one time and shall include only those who are present for more than 25% of the working day.

(10)  For a parking lot that is part of a restaurant where patrons are intended to eat in vehicles parked on the lot, the number of water closets required shall conform to

(a)	Table 3.7.4.3.G. where food service by employees is not provided on the parking lot, or

(b)	Table 3.7.4.3.H. where employees serve food on the parking lot.

Table 3.7.4.3.G.

Water Closets for Assembly Occupancies

Forming part of Sentence 3.7.4.3.(10)

| Number of Parking Spaces | Minimum Number of Water Closets for Each Sex |
| --- | --- |
| 1 to 20 | 1 |
| 21 to 70 | 2 |
| 71 to 105 | 3 |
| 106 to 135 | 4 |
| 136 to 165 | 5 |
| 166 to 195 | 6 |
| 196 to 225 | 7 |
| 226 to 275 | 8 |
| 276 to 325 | 9 |
| 326 to 375 | 10 |
| 376 to 425 | 11 |
| over 425 | 12 plus 1 for each additional increment of 50 parking spaces in excess of 425 |
| Column 1 | 2 |

(11)  The number of water closets required for drive-in theatres shall conform to Table 3.7.4.3.H.

Table 3.7.4.3.H.

Water Closets for Assembly Occupancies

Forming part of Sentences 3.7.4.3.(10) and (11)

| Number of Parking Spaces | Minimum Number of Water Closets for Each Sex |
| --- | --- |
| 1 to 40 | 1 |
| 41 to 140 | 2 |
| 141 to 210 | 3 |
| 211 to 270 | 4 |
| 271 to 330 | 5 |
| 331 to 390 | 6 |
| 391 to 450 | 7 |
| 451 to 550 | 8 |
| 551 to 650 | 9 |
| 651 to 750 | 10 |
| 751 to 850 | 11 |
| over 850 | 12 plus 1 for each additional increment of 100 parking spaces in excess of 850 |
| Column 1 | 2 |

(12)  The number of water closets required for dance halls and recreational establishments shall be not less than one fixture for each 100 males and one fixture for each 75 females.

(13)  In a child care facility the maximum number of children per water closet and lavatory shall conform to Table 3.7.4.3.I.

Table 3.7.4.3.I.

Plumbing Fixtures for a Child Care Facility

Forming Part of Sentence 3.7.4.3.(13)

| Age of Children | Maximum Number of Children per Water Closet and Lavatory |
| --- | --- |
| under 2 | 10 without regard to number of each sex |
| 2 to 5 | 10 without regard to number of each sex |
| 6 to 9 | 15 for males; 15 for females |
| over 9 | 30 for males; 26 for females |
| Column 1 | 2 |

(14)  The number of water closets required for elementary and secondary schools shall be not less than one fixture for each 30 males and one fixture for each 26 females.

(15)  The number of water closets required for non-residential college buildings shall be not less than one fixture for each 100 males and one fixture for each 75 females.

(16)  The number of water closets required for places of worship and undertaking premises shall be not less than one fixture for each 150 persons of each sex.

3.7.4.4.  Plumbing Fixtures for Care or Detention Occupancies

(1)  The number of water closets and lavatories required for Group B, Division 1 occupancies shall be determined on the basis of the special needs of these occupancies.

(2)  In a Group B, Division 2 or 3 occupancy, washrooms shall be provided so that each washroom

(a)	serves not more than four patients or residents,

(b)	is accessible from patients’ or residents’ sleeping rooms,

(c)	contains one water closet, and

(d)	contains one lavatory.

(3)  The number of water closets required for employees in Group B, Division 2 or 3 occupancies shall conform to Table 3.7.4.4.

Table 3.7.4.4.

Water Closets in Group B, Division 2 or 3 Occupancies

Forming Part of Sentence 3.7.4.4.(3)

| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| --- | --- |
| up to 9 | 1 |
| 10 to 24 | 2 |
| 25 to 49 | 3 |
| 50 to 74 | 4 |
| 75 to 100 | 5 |
| over 100 | 6 plus 1 for each additional increment of 30 persons of each sex in excess of 100 |
| Column 1 | 2 |

3.7.4.5.  Plumbing Facilities for Dwelling Units

(1)  A kitchen sink, lavatory, water closet and bathtub or shower stall shall be provided for every dwelling unit where a piped water supply is available.

3.7.4.6.  Plumbing Fixtures for Other Residential Occupancies

(1)  Except for dwelling units and as provided in Sentence (2), the number of water closets required for residential occupancies shall conform to Table 3.7.4.6.

Table 3.7.4.6.

Water Closets For Residential Occupancies

Forming Part of Sentence 3.7.4.6.(1)

| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| --- | --- |
| up to 9 | 1 |
| 10 to 24 | 2 |
| 25 to 49 | 3 |
| 50 to 74 | 4 |
| 75 to 100 | 5 |
| over 100 | 6 plus 1 for each additional increment of 30 persons of each sex in excess of 100 |
| Column 1 | 2 |

(2)  Not less than one water closet or privy shall be provided for every

(a)	10 campers of each sex in a recreational camp, and

(b)	10 employees of each sex in a camp for housing of workers.

(3)  In recreational camps and camps for housing of workers, not less than two lavatories or provision for a pail or other portable container of sound construction shall be provided for each of the water closets or privies required in Sentence (2).

(4)  A camp for housing of workers shall include

(a)	not less than one shower or other area of bathing, and

(b)	provisions for not less than one washing machine or laundry tub for every 15 beds.

3.7.4.7.  Plumbing Fixtures for Business and Personal Services Occupancies

(1)  Except as provided in Sentence (2), the number of water closets required for business and personal services occupancies shall conform to Table 3.7.4.7.

Table 3.7.4.7.

Water Closets for Business and Personal Services Occupancies

Forming Part of Sentence 3.7.4.7.(1)

| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| --- | --- |
| up to 9 | 1 |
| 10 to 24 | 2 |
| 25 to 49 | 3 |
| 50 to 74 | 4 |
| 75 to 100 | 5 |
| over 100 | 6 plus 1 for each additional increment of 30 persons of each sex in excess of 100 |
| Column 1 | 2 |

(2)  Not more than one water closet to serve both sexes need be provided in a Group D occupancy having an occupant load of not more than 5 persons.

3.7.4.8.  Plumbing Fixtures for Mercantile Occupancies

(1)  Except as provided in this Article, the number of water closets required for employees in mercantile occupancies shall conform to Table 3.7.4.8.

Table 3.7.4.8.

Water Closets for Mercantile Occupancies

Forming Part of Sentence 3.7.4.8.(1)

| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| --- | --- |
| up to 9 | 1 |
| 10 to 24 | 2 |
| 25 to 49 | 3 |
| 50 to 74 | 4 |
| 75 to 100 | 5 |
| over 100 | 6 plus 1 for each additional increment of 30 persons of each sex in excess of 100 |
| Column 1 | 2 |

(2)  Except as provided in Sentence (4), the number of water closets required for the public in mercantile occupancies shall be not less than one fixture for each 300 males and one fixture for each 150 females, except that

(a)	water closets provided for employees are permitted to be counted as part of those required for the public when these water closets are made accessible to the public, and

(b)	where the total area of the mercantile occupancy, excluding basements, is not more than 600 m2, not more than one water closet for each sex need be provided.

(3)  Not more than one water closet to serve both sexes need be provided in a Group E occupancy where

(a)	the occupant load is not more than 9 persons, or

(b)	where the total area of the occupancy, excluding basements, is not more than 300 m2.

(4)  For a restaurant classified as mercantile occupancy, the number of water closets and lavatories required shall conform to Article 3.7.4.3.

3.7.4.9.  Plumbing Fixtures for Industrial Occupancies

(1)  Except as provided in Sentence (2), the number of water closets and lavatories required for industrial occupancies shall conform to Table 3.7.4.9.

Table 3.7.4.9.

Plumbing Fixtures for Industrial Occupancies

Forming Part of Sentence 3.7.4.9.(1)

| Number of Persons of Each Sex | Minimum Number of Water Closets and Lavatories for Each Sex |
| --- | --- |
| up to 9 | 1 |
| 10 to 24 | 2 |
| 25 to 49 | 3 |
| 50 to 74 | 4 |
| 75 to 100 | 5 |
| over 100 | 6 plus 1 for each additional increment of 30 persons of each sex in excess of 100 |
| Column 1 | 2 |

(2)  Not more than one water closet to serve both sexes need be provided in a Group F occupancy where

(a)	the occupant load is not more than 9 persons, or

(b)	the total area of the occupancy, excluding basements, is not more than 300 m2.

3.7.4.10.  Plumbing Fixtures for Mobile Home Facilities

(1)  If mobile homes do not have individual plumbing facilities connected to a central water supply and drainage system, a service building shall be provided for public use.

(2)  The service building required by Sentence (1) shall contain

(a)	at least one water closet for each sex if the service building facilities serve not more than 10 mobile homes, and

(b)	an additional water closet for each sex for each additional 10 mobile homes.

(3)  If a service building is required by Sentence (1) it shall contain lavatories as required by Sentence 3.7.4.2.(5) and at least

(a)	one laundry tray or similar facility, and

(b)	one bathtub or shower for each sex.

3.7.4.11.  Safety Glass

(1)  Glass, other than safety glass, shall not be used for a shower or bathtub enclosure.

3.7.4.12.  Surface Protection near Urinals

(1)  Wall and floor surfaces below the uppermost surfaces of urinals shall be protected from deterioration for a distance from the urinal to a point not less than 900 mm from the projected outline of the urinal on to the wall or floor by impervious and durable material.

3.7.4.13.  Floor Drains

(1)  A floor drain shall be installed in a washroom containing urinals equipped with automatic flushing devices.

3.7.4.14.  Grab Bar Installation

(1)  Grab bars that are installed shall resist a minimum load of 1.3 kN applied vertically or horizontally.

3.7.4.15.  Reserved

3.7.4.16.  Privacy

(1)  If a room contains not more than 1 water closet, the doorway to the room shall be provided with a full height door which is capable of being locked from the inside.

(2)  If a room contains not less than 2 water closets or not less than 1 water closet and 1 urinal, the room shall be designed so that water closets, urinals and lavatories are not visible from the entrance to the room.

3.7.4.17.  Water Temperature Control

(1)  A water distribution system supplying hot water to plumbing fixtures shall conform to the requirements in Subsection 7.6.5.

3.7.4.18.  Drinking Water

(1)  On every floor where work will be performed and within 100 m of any area where work will be performed, potable water shall be provided from

(a)	a fountain with an upward jet,

(b)	a tap from a piped water supply, or

(c)	a tap from a covered vessel.

3.7.4.19.  Pharmacies

(1)  Every pharmacy shall be provided with a sink with hot and cold potable water for washing utensils used in the preparation, service or storage of drugs.

3.7.5. Health Care Facility Systems

3.7.5.1.  Electrical Systems

(1)  In anaesthetizing locations, electrical systems shall be designed, constructed, installed and tested in conformance with CSA Z32.1, “Code for Prevention of Explosions or Electrical Shock in Hospital Operating Rooms”.

3.7.5.2.  Medical Gas Piping

(1)  All medical gas piping systems shall be designed, constructed, installed and tested in conformance with CSA Z305.1, “Nonflammable Medical Gas Piping Systems”.

3.7.5.3.  Shielding of X-Ray Equipment

(1)  Every installation of an x-ray machine or of x-ray equipment in a building shall be shielded to protect any person who could be exposed to radiation inside and outside the building.

3.7.6. Food Premises

3.7.6.1.  Application

(1)  The requirements of this Subsection apply to all food premises.

3.7.6.2.  Room Finishes

(1)  Except as provided in Sentence (2), floors and floor coverings shall be tight, smooth and non-absorbent in rooms where

(a)	food or drink for human consumption, or an ingredient of food or drink for human consumption, is manufactured, processed, prepared, stored, displayed, handled, served, distributed, sold or offered for sale,

(b)	utensils are washed, or

(c)	washing fixtures or toilet fixtures are located.

(2)  Carpeting may be used in areas where food is served.

(3)  Wall and ceiling finishes of rooms and passageways shall be easy to clean.

3.7.6.3.  Location of Plumbing Fixtures

(1)  A room containing a water closet shall be located where

(a)	it does not open directly into any room or area where food or drink for human consumption, or an ingredient of food or drink for human consumption, is intended to be stored, prepared, processed, distributed, served, sold or offered for sale, and

(b)	it is not necessary for the public to go through the food preparation areas to gain access to the plumbing fixtures.

(2)  Except as permitted in Sentence (3), a room containing plumbing fixtures for the public and employees in a restaurant shall be located in the restaurant.

(3)  A room containing plumbing fixtures for the public in Sentence (2) need not be located in the restaurant if

(a)	the room is located in the building containing the restaurant, and

(b)	the distance of travel between the restaurant and the room is not more than 45 m.

3.7.6.4.  Lavatories, Appliances and Sinks

(1)  A separate lavatory for the handwashing of employees shall be constructed in a location convenient for employees in each manufacturing, processing and preparation area.

(2)  If equipment and facilities for the cleaning and sanitizing of utensils are provided, they shall consist of

(a)	mechanical equipment, or

(b)	drainage racks of corrosion-resistant materials and

(i)	a three-compartment sink or three sinks, or

(ii)	a two-compartment sink or two sinks, where the first compartment or sink can be used effectively for washing and rinsing and the second compartment or sink can be used effectively for sanitizing.

(3)  A retail food premise is exempt from compliance with this Article if its eating and drinking area does not exceed 56 m2 and any one or more of the following applies:

(a)	it is designed to sell only cold drinks in or from the original container,

(b)	it is designed to sell only frozen confections in the original package or wrapper,

(c)	it is designed to prepare and sell only hot beverages,

(d)	it is designed to prepare and sell only popped corn, roasted nuts or french-fried potatoes,

(e)	it is designed to sell only food or drink for human consumption that,

(i)	is pre-packaged at a premise other than the food premise at which it is being offered for sale, and

(ii)	is not capable of supporting the growth of pathogenic organisms or the production of the toxins of such organisms.

3.7.6.5.  Hot and Cold Water Supply

(1)  A hot and cold water supply shall be provided to

(a)	every plumbing appliance and fixture required by Article 3.7.6.4.,

(b)	every area where food or drink for human consumption, or an ingredient of food or drink for human consumption, is manufactured, processed or prepared, and

(c)	every area where utensils are washed.

(2)  This Article does not apply to a retail food premise described in Sentence 3.7.6.4. (3).

3.7.6.6.  Employee Facilities

(1)  In a food premise, where dressing rooms are provided for employees, there shall be separate dressing rooms for males and females that

(a)	are large enough for the employees to change and store their clothing, and

(b)	are equipped with lockers or other facilities suitable for storing the clothing of the employees.

(2)  Every room containing sanitary units for employees shall have a floor area not less than 2.3 m2.

3.7.6.7.  Sleeping Quarters

(1)  A room or space intended to be used as sleeping quarters shall not open directly into any room where food or drink for human consumption, or an ingredient of food or drink for human consumption, is manufactured, processed, prepared, stored, displayed, handled, served, distributed, sold or offered for sale.

Section 3.8. Barrier-Free Design

3.8.1. General

3.8.1.1.  Application

(1)  The requirements of this Section apply to all buildings except

(a)	houses, including semi-detached houses, duplexes, triplexes, town houses, row houses and boarding or rooming houses with fewer than 8 boarders or roomers,

(b)	buildings of Group F, Division 1 major occupancy, and

(c)	buildings which are not intended to be occupied on a daily or full time basis, including automatic telephone exchanges, pumphouses and substations.

3.8.1.2.  Entrances

(1)  In addition to the barrier-free entrances required by Sentence (2), the number of barrier-free entrances in a building referred to in Sentence 3.8.1.1.(1) shall be not less than those as specified in Table 3.8.1.2. and shall lead from

(a)	the outdoors at sidewalk level, or

(b)	a ramp that conforms to Article 3.8.3.4. and leads from a sidewalk.

Table 3.8.1.2.

Minimum Number of Pedestrian Entrances Required to be Barrier-Free

Forming Part of Sentence 3.8.1.2.(1)

| Number of pedestrian entrances into building | Minimum number of pedestrian entrances required to be barrier-free |
| --- | --- |
| 1 to 3 | 1 |
| more than 3 to 5 | 2 |
| more than 5 | not less than 50 percent |
| Column 1 | 2 |

(2)  A suite of assembly occupancy, business and personal services occupancy or mercantile occupancy that is located in the first storey of a building or in a storey to which a barrier-free path of travel is provided, and that is separated from the remainder of the building, so that there is no access to the remainder of the building, shall have at least one barrier-free entrance.

(3)  A barrier-free entrance required by Sentences (1) or (2) shall be designed in accordance with Article 3.8.3.3.

(4)  At a barrier-free entrance that includes more than one doorway, only one of the doorways is required to be designed in accordance with the requirements of Article 3.8.3.3.

3.8.1.3.  Barrier-Free Path of Travel

(1)  Except as required in Sentence (4) and except as permitted in Subsection 3.8.3., every barrier-free path of travel shall provide an unobstructed width of at least 1 060 mm for the passage of wheelchairs.

(2)  Interior and exterior walking surfaces that are within a barrier-free path of travel shall

(a)	have no opening that will permit the passage of a sphere more than 13 mm in diam,

(b)	have any elongated openings oriented approximately perpendicular to the direction of travel,

(c)	be stable, firm and slip-resistant,

(d)	be bevelled at a maximum slope of 1 in 2 at changes in level not more than 13 mm, and

(e)	be provided with sloped floors or ramps at changes in level more than 13 mm.

(3)  A barrier-free path of travel is permitted to include ramps, elevators or other platform elevating devices where there exists a difference in elevation.

(4)  Every barrier-free path of travel less than 1 600 mm in width shall be provided with an unobstructed space not less than 1 600 mm in width and 1 600 mm in length located not more than 30 m apart.

(5)  Where the headroom of an area in a barrier-free path of travel is reduced to less than 1 980 mm, a guardrail or other barrier with its leading edge at or below 680 mm from the floor shall be provided.

3.8.1.4.  Storeys Served by Escalators

(1)  In a building in which an escalator provides access to any storey above or below the entrance storey, an interior barrier-free path of travel shall be provided to that storey.

3.8.1.5.  Controls

(1)  Except as provided in Article 3.8.3.5. for elevators, controls for the operation of building services or safety devices, including electrical switches, thermostats and intercom switches, intended to be operated by the occupant and located in a barrier-free path of travel shall be accessible to a person in a wheelchair, operable with one hand and mounted at not more than 1 200 mm above the floor.

3.8.1.6.  Illumination

(1)  All portions of a barrier-free path of travel shall be equipped to provide a level of illumination in accordance with Sentence 3.2.7.1.(1).

3.8.2. Occupancy Requirements

3.8.2.1.  Areas Requiring Barrier-Free Path of Travel

(1)  Except where essential obstructions in the work area would make a barrier-free path of travel hazardous, and except as provided in Sentences (2), (3) and (4), a barrier-free path of travel from the entrances required by Sentences 3.8.1.2.(1) and (2) to be barrier-free shall be provided throughout the entrance storey and within all normally occupied floor areas served by a passenger type elevator or other platform equipped passenger elevating device.

(2)  The provision of a barrier-free path of travel in Sentence (1) does not apply

(a)	to service rooms,

(b)	to elevator machine rooms,

(c)	to janitors rooms,

(d)	to service spaces,

(e)	to crawl spaces,

(f)	to attic or roof spaces,

(g)	to mezzanines not served by a passenger elevator or other platform equipped passenger elevating device,

(h)	to high hazard industrial occupancies

(i)	within portions of a floor area with fixed seats in an assembly occupancy where these portions are not part of the barrier-free path of travel to spaces designated for wheelchair use,

(j)	into suites of residential occupancy that are in storeys other than the entrance storey and that have all entrance doors at floor levels that do not correspond to elevator stop levels,

(k)	within a suite of residential occupancy, or

(l)	within those parts of a floor area that are not at the same level as the entry level, provided amenities and uses provided on any raised or sunken level are accessible on the entry level by means of a barrier-free path of travel.

(3)  Where a balcony is provided in a dwelling unit, access shall be provided to the balcony

(a)	by a doorway with a clear width of not less than 800 mm when the door is in the open position, and

(b)	such that no projection above the walking surface is more than 13 mm.

(4)  The minimum number of spaces designated for wheelchair use in an assembly occupancy with fixed seats shall conform to Table 3.8.2.1.

Table 3.8.2.1.

Designated Wheelchair Spaces

Forming Part of Sentence 3.8.2.1.(4)

| Number of Fixed Seats in Seating Area | Minimum Number of Spaces Required for Wheelchairs |
| --- | --- |
| up to 100 | 2 |
| 101 to 200 | 3 |
| 201 to 300 | 4 |
| 301 to 400 | 5 |
| 401 to 600 | 6 |
| Over 600 | Not less than 1 per cent of the seating capacity |
| Column 1 | 2 |

3.8.2.2. Access to Parking Areas

(1)  A barrier-free path of travel shall be provided from the entrance described in Article 3.8.1.2. to

(a)	an exterior parking area, where exterior parking is provided, and

(b)	at least one parking level, where a passenger elevator serves an indoor parking level.

(2)  The vehicular entrance to and egress from at least one parking level described in Sentence (1) and all areas intended to be used by wheelchair accessible vehicles to gain access to a parking space on that level shall have a vertical clearance of not less than 2 100 mm.

(3)  If an exterior passenger loading zone is provided, it shall have

(a)	an access aisle not less than 1 500 mm wide and 6 m long adjacent and parallel to the vehicle pull-up space,

(b)	a curb ramp, where there are curbs between the access aisle and the vehicle pull-up space, and

(c)	a clearance height of not less than 2 750 mm at the vehicle pull-up space and along the vehicle access and egress routes.

3.8.2.3. Washrooms Required to be Barrier-Free

(1)  Except where other barrier-free washrooms are provided on the same floor level within 45 m and except within suites of residential occupancy, and buildings exempted in Clauses 3.8.1.1.(1)(a), (b) and (c), in buildings where a washroom is required in accordance with Subsection 3.7.4., a barrier-free path of travel shall be provided to a barrier-free washroom designed to accommodate disabled persons in conformance with the appropriate requirements in Articles 3.8.3.8. to 3.8.3.12.

(2)  Except as permitted in Sentence (3), where washrooms in excess of those required by Subsection 3.7.4. are provided in a storey to which a barrier-free path of travel is required in conformance with Article 3.8.2.1., these washrooms shall be designed to accommodate disabled persons in conformance with the appropriate requirements in Articles 3.8.3.8. to 3.8.3.12.

(3)  Washrooms need not conform to the requirements in Sentence (2) provided

(a)	they are located within suites of residential occupancy,

(b)	other barrier-free washrooms are provided on the same floor level within 45 m, or

(c)	they are located in an individual suite having an area of less than 300 m2 in buildings where such suite is completely cut off from the remainder of the building so that there is no access to the remainder of the building.

3.8.3. Design Standards

3.8.3.1. Accessibility Signs

(1)  Where a building is required to have a barrier-free entrance to accommodate disabled persons, signs incorporating the international symbol of accessibility for disabled persons shall be installed where necessary to indicate the location of that entrance.

(2)  Where a washroom, elevator, telephone or parking area is required to accommodate disabled persons, it shall be identified by a sign consisting of the international symbol of accessibility for disabled persons and such other graphic, tactile or written directions as are needed to indicate clearly the type of facility available.

(3)  Where a washroom is not designed to accommodate disabled persons in a storey to which a barrier-free path of travel is required, signs shall be provided to indicate the location of the barrier-free facilities.

(4)  Signs incorporating the international symbol of accessibility for disabled persons shall be installed where necessary to indicate the location of the accessible means of egress.

3.8.3.2. Exterior Walks

(1)  Except as provided in Sentence (2), exterior walks that form part of a barrier-free path of travel shall

(a)	be provided by means of a continuous plane not interrupted by steps or abrupt changes in level,

(b)	have a permanent, firm and slip-resistant surface,

(c)	except as required in Sentence 3.8.1.3.(4), have an uninterrupted width of not less than 1 100 mm and a gradient not exceeding 1 in 20,

(d)	be designed as a ramp where the gradient is greater than 1 in 20,

(e)	have not less than 1 100 mm wide surface of a different texture to that surrounding it, where the line of travel is level and even with adjacent walking surfaces,

(f)	be free from obstructions for the full width of the walk to a minimum height of 1 980 mm, except that handrails are permitted to project not more than 100 mm from either side into the clear area, and

(g)	have a level area adjacent to the entrance doorway conforming to Clause 3.8.3.4.(1)(c).

(2)  Where a difference in elevation between levels in a walkway is not more than 200 mm, a curb ramp conforming the Sentences (3) and (4) may be provided.

(3)  The curb ramp permitted by Sentence (2) shall

(a)	have a maximum gradient of 1 in 7.5,

(b)	have a width of not less than 1 200 mm exclusive of flared sides,

(c)	have a surface including flared sides which shall

(i)	be slip resistant,

(ii)	have a detectable warning surface that is colour- and texture-contrasted with the adjacent surfaces, and

(iii)	have a smooth transition from the ramp and adjacent surfaces, and

(d)	have flared sides with a slope of not more than 1:10 where pedestrians are likely to walk across them.

(4)  Curb ramps described in Sentence (3) do not require handrails or guards.

Table 3.8.3.2.

Ramp Rise and Slope

Forming Part of Sentence 3.8.3.2.(3)

| Maximum Vertical Rise Between Surfaces, mm | Maximum Slope |
| --- | --- |
| 200 | 1:10 to 1:12 |
| 75 | 1:8 to 1:10 |
| Column 1 | 2 |

3.8.3.3. Doorways and Doors

(1)  Every doorway that is located in a barrier-free path of travel shall have a clear width of not less than 810 mm when the door is in the open position,

(2)  Except where no bathroom within the suite is at the level of the suite entrance door to which a barrier-free path of travel is provided in accordance with Sentence 3.8.2.1.(1), the doorway to at least 1 bathroom and to each bedroom at the same level as such bathroom within a suite of residential occupancy shall have, when the door is in the open position, a clear width of not less than

(a)	760 mm where the door is served by a corridor or space not less than 1 060 mm wide, and

(b)	810 mm where the door is served by a corridor or space less than 1 060 mm wide

(3)  Door opening devices that are the only means of operation shall be of a design which does not require tight grasping and twisting of the wrist.

(4)  Thresholds for doorways referred to in Sentences (1) and (2) shall not exceed 13 mm in height above the finished floor surface and shall be bevelled to facilitate the passage of wheelchairs.

(5)  Except as permitted in Sentence (7), the door for the entrance described in Article 3.8.1.2. shall be equipped with a power door operator in

(a)	hotels,

(b)	buildings of Group B, Division 2 or 3 major occupancy, and

(c)	buildings of Group A, D or E major occupancy having more than 300 m2 in building area.

(6)  Except as permitted in Sentence (7), where the entrance described in Article 3.8.1.2. incorporates a vestibule, a door leading from the vestibule into the floor area shall be equipped with a power door operator in

(a)	hotels,

(b)	buildings of Group B, Division 2 and 3, major occupancy, and

(c)	buildings of Group A, D or E major occupancy having more than 300 m2 in building area.

(7)  The requirements in Sentence (5) and (6) do not apply to an individual suite having an area of less than 300 m2 in buildings having only suites of Group A, D or E occupancy where such suite is completely cut off from the remainder of the building.

(8)  Except as permitted in Sentence (9), and except for doors with power operators, closers for doors in a barrier-free path of travel shall be designed to permit doors to open when a force of not more than 38 N is applied to the handles, push plates or latch-releasing devices in the case of exterior doors and 22 N in the case of interior doors.

(9)  Sentence (8) does not apply to doors at the entrances to dwelling units, or where greater forces are required in order to close and latch the doors against prevailing differences in air pressures on opposite sides of the doors.

(10)  Except for doors at the entrances to dwelling units, closers for interior doors in a barrier-free path of travel shall have a closing period of not less than 3 seconds measured from when the door is in an open position of 70° to the doorway, to when the door reaches a point 75 mm from the closed position, measured from the leading edge of the latch side of the door.

(11)  Every door equipped with a closer in a barrier-free path of travel shall have a clear space beyond the latch side of not less than

(a)	600 mm where the door swings towards the approach side, and

(b)	300 mm where the door swings away from the approach side.

(12)  Vestibules located in a barrier-free path of travel shall be arranged to allow the movement of wheelchairs between doors and shall provide a distance between 2 doors in series of at least 1 200 mm plus the width of any door that swings into the space in the path of travel from one door to another.

(13)  Only the active leaf in a multiple leaf door in a barrier-free path of travel need conform to the requirements of this Article.

(14)  Where a vision panel is provided in a door in a barrier-free path of travel, such panel shall be at least 75 mm in width and be located so that

(a)	the bottom of the panel is not more than 900 mm above the finished floor, and

(b)	the edge of the panel closest to the latch is not more than 250 mm from the latch side of the door.

(15)  A door in a barrier-free path of travel consisting of a sheet of glass shall be marked with a continuous opaque strip which

(a)	shall be colour and brightness contrasted to the background of the door,

(b)	shall be at least 50 mm wide,

(c)	shall be located across the width of the door at a height of 1 350 mm to 1 500 mm above the finished floor, and

(d)	may incorporate a logo or symbol provided such logo or symbol does not diminish

(i)	the opacity of the strip,

(ii)	the width of the strip,

(iii)	the colour and brightness contrast of the strip to the background of the door, and

(iv)	the continuity of the strip across the width of the door.

3.8.3.4. Ramps

(1)  Ramps located in a barrier-free path of travel shall

(a)	have a minimum width of 870 mm between handrails,

(b)	have a maximum gradient of 1 in 12,

(c)	have a level area of at least 1 500 mm by 1 500 mm at the top and bottom of a ramp and where a door is located in a ramp, so that the level area extends at least 600 mm beyond the latch side of the door opening, except that where the door opens away from the ramp, the area extending beyond the latch side of the door opening may be reduced to 300 mm,

(d)	have a level area at least 1 500 mm long and at least the same width as the ramp

(i)	at intervals of not more than 9 m along its length, and

(ii)	where there is an abrupt change in the direction of the ramp,

(e)	except as provided in Sentence (2), be equipped with handrails on both sides which shall

(i)	be continuously graspable along their entire length and have circular cross-section with an outside diameter not less than 30 mm and not more than 40 mm, or any non-circular shape with a graspable portion that has a perimeter not less than 100 mm and not more than 155 mm and whose largest cross-sectional dimension is not more than 57 mm,

(ii)	be not less than 865 mm and not more than 965 mm high, measured vertically from the surface of the ramp, except that handrails not meeting these requirements are permitted provided they are installed in addition to the required handrail,

(iii)	be terminated in a manner which will not obstruct pedestrian travel or create a hazard,

(iv)	extend horizontally not less than 300 mm beyond the top and bottom of the ramp,

(v)	be provided with a clearance of not less than 40 mm between the handrail and any wall to which it is attached, and

(vi)	be designed and constructed such that handrails and their supports will withstand the loading values obtained from the nonconcurrent application of a concentrated load not less than 0.9 kN applied at any point and in any direction for all handrails and a uniform load not less than 0.7 kN/m applied in any direction to the handrail,

(f)	except as provided in Sentence (2), have a wall or a guard on both sides and where a guard is provided the guard shall

(i)	be not less than 1 070 mm measured vertically to the top of the guard from the ramp surface, and

(ii)	be designed so that no member, attachment or opening located between 140 mm and 900 mm above the ramp surface being protected by the guard will facilitate climbing, and

(g)	be provided

(i)	with a curb at least 50 mm high on any side of the ramp where no solid enclosure or solid guard is provided, and

(ii)	with railings or other barriers that extend to within 50 mm of the finished ramp surface or have a curb not less than 50 mm high.

(2)  Where a ramp serves as an aisleway for fixed seating, the requirements for handrails in Clause 3.8.3.4.(1)(e) need not apply.

(3)  Floors or walks in a barrier-free path of travel having a slope steeper than 1 in 20 shall be designed as ramps.

3.8.3.5. Elevators

(1)  The passenger-type elevator in Article 3.8.2.1. shall conform to Appendix E of CAN/CSA B44, “Safety Code for Elevators”.

(2)  The passenger-type elevating device in Article 3.8.2.1. shall conform to CAN/CSA-B355, “Lifts for Persons with Physical Disabilities”.

3.8.3.6. Spaces in Seating Area

(1)  Spaces designated for wheelchair use in Sentence 3.8.2.1.(4) shall be

(a)	clear and level or level with removable seats,

(b)	not less than 900 mm wide and 1 525 mm long to permit a wheelchair to enter from a side approach, and 1 220 mm long where the wheelchair enters from the front or rear of the space,

(c)	arranged so that at least two designated spaces are side by side,

(d)	located adjoining a barrier-free path of travel without infringing on egress from any row of seating or any aisle requirements, and

(e)	situated, as part of the designated seating plan, to provide a choice of viewing location and a clear view of the event taking place.

3.8.3.7. Assistive Listening Devices

(1)  In buildings of assembly occupancy, all classrooms, auditoria, meeting rooms and theatres with an area of more than 100 m2 and an occupant load of more than 75 shall be equipped with assistive listening systems encompassing the entire seating area.

3.8.3.8. Water Closet Stalls

(1)  Where a washroom is required by Article 3.8.2.3. to barrier-free, at least 1 water closet stall or enclosure shall

(a)	be at least 1 500 mm in width by 1 500 mm in depth,

(b)	be equipped with a door which shall

(i)	be capable of being locked from the inside with a locking mechanism that is operable by one hand,

(ii)	provide, when the door is in an open position, a clear opening of at least 810 mm,

(iii)	swing outward, unless 760 mm by 1 220 mm clear floor area is provided within the stall or enclosure to permit the door to be closed without interfering with the wheelchair,

(iv)	be provided with spring-type or gravity hinges so that the door closes automatically,

(v)	be provided with a door pull on the outside, near the latch side of the door, and

(vi)	be aligned with the clear manoeuvring space adjacent to the water closet,

(c)	have a water closet located so that its centreline is not less than 460 mm and not more than 480 mm from an adjacent side wall on one side,

(d)	be equipped with grab bars which shall

(i)	be at least 760 mm in length and mounted at a 30° to 50° angle sloping upwards, away from the water closet with the lower end of the bar mounted 230 mm above the toilet seat and 50 mm in front of the toilet bowl, or alternatively, be L-shaped with 760 mm long horizontal and vertical components mounted with the horizontal component 230 mm above the toilet seat and the vertical component 150 mm in front of the toilet bowl,

(ii)	be at least 600 mm in length mounted horizontally on the wall behind the water closet from 840 mm to 920 mm above the floor and, where the water closet has a water tank, be mounted 150 mm above the tank,

(iii)	Reserved

(iv)	be installed to resist a load of at least 1.3 kN applied vertically or horizontally,

(v)	be not less than 30 mm and not more than 40 mm in diameter,

(vi)	have a clearance of 30 mm to 40 mm from the wall, and

(vii)	have a slip resistant surface,

(e)	be equipped with a coat hook mounted not more than 1 200 mm above the floor on a side wall and projecting not more than 50 mm from the wall,

(f)	have a clearance of at least 1 700 mm between the outside of the stall face and the face of an in-swinging washroom door and 1 400 mm between the outside of the stall face and any wall-mounted fixture or other obstruction, and

(g)	when a toilet paper dispenser is provided, provide a dispenser that is

(i)	wall mounted,

(ii)	located below the grab bar,

(iii)	in line with or not more than 300 mm in front of the toilet seat, and

(iv)	not less than 600 mm above the floor.

3.8.3.9. Water Closets

(1)  Water closets for a person with physical disabilities shall

(a)	be equipped with a seat located at not less than 400 mm and not more than 460 mm above the floor,

(b)	be equipped with hand-operated flushing controls that are easily accessible to a wheelchair user or be automatically operable,

(c)	be equipped with a back support where there is no seat lid or tank, and

(d)	not have a spring-activated seat.

3.8.3.10. Reserved

3.8.3.11. Lavatories

(1)  A barrier-free washroom shall be provided with a lavatory which shall

(a)	be located so that the distance between the centreline of the lavatory and the side wall is not less than 460 mm,

(b)	be mounted so that the top of the lavatory or, where the lavatory is in a vanity, the top of the vanity is not more than 840 mm above the finished floor,

(c)	have a clearance beneath the lavatory not less than

(i)	760 mm wide,

(ii)	735 mm high at the front edge,

(iii)	685 mm high at a point 205 mm back from the front edge, and

(iv)	230 mm high over the distance from a point 280 mm to a point 430 mm back from the front edge,

(d)	have insulated pipes where they would otherwise present a burn hazard or have water supply temperature limited to a maximum of 43oC,

(e)	be equipped with faucet handles of the lever type without spring loading or be automatically operable and are located so that the distance from the centreline of the faucet to the edge of the basin or, where the basin is mounted in a vanity, to the front edge of the vanity, is not more than 485 mm, and

(f)	have soap or towel dispensers that are

(i)	located to be accessible to persons in a wheelchair,

(ii)	located so that the dispensing height is not more than 1 200 mm above the floor, and

(iii)	operable with one hand.

(2)  The lavatory required by Sentence (1) is permitted to be built into a counter provided the height and clearances required by Sentence (1) are maintained.

(3)  Shelves or other projections above lavatories shall be located so that they will not present a hazard to a person with a visual disability.

(4)  If mirrors are provided in a barrier-free washroom, at least one mirror shall be

(a)	mounted with its bottom edge not more than 1 000 mm above the floor, or

(b)	inclined to the vertical to be usable by a person in a wheelchair.

(5)  If dispensing or hand-operated washroom accessories, except those located in toilet stalls or described in Clause 3.8.3.11.(1)(f), are provided, they shall be mounted so that the dispensing height is between 900 mm and 1 200 mm above the floor.

3.8.3.12. Special Washrooms

(1)  A special washroom provided primarily for the use of persons of both sexes with physical disabilities, in lieu of facilities for persons with physical disabilities in washrooms used by the general public, shall

(a)	be provided on the same floor level within 45 m of the washrooms described in Sentence 3.8.2.3.(1),

(b)	be equipped with a door capable of being locked from the inside with one hand and released from the outside in case of emergency and which has

(i)	graspable latch operating and locking mechanisms located not less than 900 mm and not more than 1 000 mm above the floor, and

(ii)	on an outward swinging door, a door pull not less than 140 mm long located on the inside so that its midpoint is not less than 200 mm and not more than 300 mm from the hinged side of the door and not less than 900 mm and not more than 1 000 mm above the floor,

(c)	be provided with a lavatory conforming to Article 3.8.3.11.,

(d)	be equipped with a water closet conforming to the requirements of Article 3.8.3.9. and located

(i)	so that its centreline is not less than 460 mm and not more than 480 mm from an adjacent side wall on one side, and

(ii)	not less than 1 020 mm to the wall on the other side,

(e)	be equipped with grab bars conforming to Clause 3.8.3.8.(1)(d),

(f)	have no dimension less than 1 700 mm,

(g)	have fixture clearances conforming to Articles 3.8.3.8. and 3.8.3.11.,

(h)	be equipped with

(i)	a coat hook conforming to Clause 3.8.3.8.(1)(e), and

(ii)	a shelf located not more than 1 000 mm above the floor in a location accessible to a person in a wheelchair,

(i)	have a doorway conforming to Article 3.8.3.3.,

(j)	be designed to permit a wheelchair to back in alongside the water closet in the space referred to in Subclause (d)(ii), and

(k)	be designed to permit a wheelchair to turn in an open space that has a diameter not less than 1 500 mm.

3.8.3.13. Showers

(1)  Where individual shower stalls are provided in buildings of assembly occupancy, at least one shower stall shall be barrier-free and shall

(a)	be at least 1 500 mm in width and 900 mm in depth,

(b)	have a clear floor space at the entrance to the shower of at least 900 mm in depth and the same width as the shower, except that fixtures are permitted to project into that space provided they do not restrict access to the shower,

(c)	have a slip-resistant floor surface,

(d)	have a bevelled threshold not exceeding 13 mm in height above the finished floor,

(e)	be equipped with a wall mounted folding seat that is not spring-loaded or provision for a portable seat that is

(i)	38 mm to 62 mm less than the shower compartment depth in width by 430 mm to 530 mm in depth,

(ii)	mounted approximately 450 mm above the floor, and

(iii)	designed to carry a minimum load of 1.33 kN,

(f)	be equipped with a grab bar which shall

(i)	be at least 900 mm in length,

(ii)	be mounted approximately 850 mm above the floor,

(iii)	be located on the wall so that at least 300 mm of its length is reachable from one side of the seat, and

(iv)	conform to Subclauses 3.8.3.8.(1)(d)(iv),(v) and (vi),

(g)	be equipped with a pressure-equalizing or thermostatic mixing valve controlled by lever or other device operable with a closed fist from the seated position,

(h)	be equipped with a hand-held shower head with at least 1 500 mm of flexible hose located so that it can be reached from the seated position and equipped with a support so that it can operate as a fixed shower head, and

(i)	have fully recessed soap holders which can be reached from the seated position.

(2)  Individual shower stalls that are provided for use by patients or residents in buildings of Group B, Division 2 or 3 occupancy shall conform to the requirements of Sentence (1).

(3)  Individual bathtubs that are provided for the use of patients or residents in buildings of Group B, Division 2 or 3 occupancy shall have

(a)	faucet handles of the lever type that are not spring-loaded or be automatically operable,

(b)	faucet handles that are located so as to be usable by a person seated in the bathtub, and

(c)	unless the bathtub is free-standing, an “L”-shaped grab bar conforming to Subclauses 3.8.3.8.(1)(d)(iv) to (vi) mounted on the wall

(i)	with each leg of the “L” being at least 900 mm long,

(ii)	with the legs of the “L” being separated by 90°,

(iii)	with the horizontal leg of the “L” being located between 150 mm and 200 mm above and parallel to the rim of the bathtub, and

(iv)	with the vertical leg of the “L” being located between 300 mm and 450 mm from the control end of the bathtub.

3.8.3.14. Reserved

3.8.3.15. Shelves or Counters for Telephones

(1)  Where built-in shelves or counters are provided for public telephones, they shall be level and shall

(a)	be not less than 350 mm deep, and

(b)	have, for each telephone provided, a clear space not less than 250 mm wide having no obstruction within 250 mm above the surface.

(2)  The top surface of a section of the shelf or counter described in Sentence (1) serving at least one telephone shall

(a)	be not more than 865 mm from the floor, and

(b)	have a knee space not less than 685 mm high.

(3)  Where a wall-hung telephone is provided above the shelf or counter section described in Sentence (2), it shall be located so that the receiver and coin slot are not more than 1 200 mm from the floor.

3.8.3.16. Drinking Fountains

(1)  Where drinking fountains are provided, at least one shall be barrier-free and shall

(a)	have a spout located near the front of the unit not more than 915 mm above the floor, and

(b)	be equipped with controls that are easily operated from a wheelchair using one hand with a force of not more than 22 N or be automatically operable.

Section 3.9. Portable Classrooms

3.9.1. Scope

3.9.1.1. Application

(1)  Except as provided in this Section, the requirements in the Code apply to portable classrooms.

3.9.1.2. Heating Systems

(1)  Heating systems and equipment in a portable classroom shall be designed and installed in accordance with Section 6.2.

3.9.2. Interior Finish

3.9.2.1. Flame-Spread Rating

(1)  Interior finish material used on a wall or ceiling of a portable classroom shall have a flame-spread rating of 150 or less.

3.9.3. Application

3.9.3.1. Building Areas

(1)  A single portable classroom shall be not more than 100 m2 in building area, and not more than 1 storey in building height.

(2)  For the purposes of Subsection 3.2.2., where the horizontal distance between portable classrooms is less than 6 m, a group of portable classrooms may be considered as a single building with a building area equal to the aggregate area of the portable classrooms.

3.9.3.2. Spatial Separations

(1)  The requirements in Subsection 3.2.3. need not be provided between individual portable classrooms where the distance between the classrooms is 6 m or more.

(2)  The requirements in Subsection 3.2.3. need not be provided between individual portable classrooms within a group where

(a)	the portable classrooms are in groups where

(i)	the distance between the classrooms is less than 6 m,

(ii)	the number of classrooms in a group is not more than 6, and

(iii)	the distance between groups of classrooms is 12 m or more, or

(b)	the portable classrooms are in groups where

(i)	the means of egress for each classroom within a group is by a common corridor or passageway,

(ii)	the number of portable classrooms in a group is not more than 6, and

(iii)	the distance between groups of portable classrooms is 12 m or more.

3.9.3.3. Fire Alarm Systems

(1)  Except as provided in Sentences (2) and (3), the fire alarm system in the main school building shall be extended to the portable classrooms with a separate zone indicator on the annunciator.

(2)  The requirements in Sentence (1) need not be provided where there are not more than 12 portables on a site and where

(a)	Reserved

(b)	the distance between portable classrooms is less than 6 m and the requirements of Subsection 3.2.3. are applied between the classrooms, or

(c)	the portable classrooms are in groups where

(i)	the distance between the classrooms is less than 6 m,

(ii)	the number of classrooms in a group does not exceed 6,

(iii)	within a group of classrooms, the facing walls have a fire-resistance rating of 45 min, rated from inside the classroom, and

(iv)	the distance between groups of classrooms is 12 m or more.

(3)  The requirements in Sentence (1) need not be provided where the distance between portable classrooms is 6 m or more.

3.9.3.4. Provisions for Fire-fighting

(1)  The requirements in Articles 3.2.2.10. and 3.2.5.1. to 3.2.5.7. need not be provided where there are not more than 12 portable classrooms on a site and where

(a)	the distance between portable classrooms is 6 m or more,

(b)	the distance between portable classrooms is less than 6 m and the requirements of Subsection 3.2.3. are applied between the classrooms,

(c)	the portable classrooms are in groups where

(i)	the distance between the classrooms is less than 6 m,

(ii)	the number of classrooms in a group is not more than 6,

(iii)	within a group of classrooms, the facing walls have a fire-resistance rating of 45 min, rated from inside the classroom, and

(iv)	the distance between groups of classrooms is 12 m or more,

(d)	the portable classrooms are in groups where

(i)	the distance between the classrooms is less than 6 m,

(ii)	the number of classrooms in a group is not more than 6, and

(iii)	the distance between groups of classrooms is 12 m or more, or

(e)	the portable classrooms are in groups where

(i)	the means of egress for each classroom within a group is by a common corridor or passageway

(ii)	the number of classrooms in a group is not more than 6, and

(iii)	the distance between groups of classrooms is 12 m or more.

3.9.3.5. Portable Fire Extinguishers

(1)  A fire extinguisher, in accordance with Article 3.2.5.17., shall be installed in each portable classroom.

3.9.3.6. Means of Egress

(1)  Except as required in Sentence 3.9.3.7.(1), a portable classroom shall be provided with means of egress conforming to Sections 3.3. and 3.4.

3.9.3.7. Fuel-Fired Appliances

(1)  Where there is only one egress door from a portable classroom, a fuel-fired appliance shall be separated from the remainder of the classroom by a fire separation with a fire-resistance rating of not less than 45 min.

(2)  Except as provided in Sentences (3) and (4), if a portable classroom contains a fuel-fired appliance, the appliance shall be separated from the remainder of the classroom by a fire separation having a fire-resistance rating not less than

(a)	1.5 h where the horizontal distance between portable classrooms is 1 500 mm or less, and

(b)	45 min where the horizontal distance between portable classrooms is more than 1 500 mm.

(3)  If the horizontal distance between portable classrooms is 6 m or more, a fuel-fired appliance need not be separated from the remainder of the classroom by a fire separation provided

(a)	there is not more than 1 appliance per portable classroom, and

(b)	the appliance is located not less than 4.5 m from an egress doorway or an exit from the portable classroom.

(4)  Fuel-fired appliances with sealed combustion located in a portable classroom are not required to be separated from the remainder of the classroom

(a)	if there are not more than four portable classrooms in a group, and

(b)	if the appliance is located not less than 4.5 m from an egress doorway or an exit from the portable classroom.

3.9.3.8. Washroom Facilities

(1)  Washroom facilities need not be provided in a portable classroom where the facilities in the main school building comply with the requirements of Subsection 3.7.4. for the total occupant load of the main school building and the portable classrooms.

3.9.3.9. Barrier-Free Access

(1)  The requirements of Section 3.8. for barrier-free access need not be provided for a portable classroom provided that the main school building complies with the requirements of Section 3.8.

Section 3.10. Self-Service Storage Buildings

3.10.1. Scope

3.10.1.1. Application

(1)  Except as provided in this Section, the requirements in the Code apply to self-service storage buildings.

3.10.2. Requirements for All Buildings

3.10.2.1. Occupancy Classification

(1)  A self-service storage building

(a)	shall comply with the requirements for a Group F, Division 2 major occupancy, and

(b)	shall not contain a Group F, Division 1 occupancy.

3.10.2.2. Occupant Load

(1)  The requirements based on occupant load shall not apply.

3.10.2.3. Structural Fire Protection

(1)  Except as provided in Sentence (2) and Sentence 3.10.4.2.(1), the requirements in Subsections 3.2.1. and 3.2.2. shall apply.

(2)  The first storey shall be subdivided into areas not more than 500 m2 by a masonry or reinforced concrete fire separation having a fire-resistance rating not less than 1 h, or it shall be sprinklered.

3.10.2.4. Safety Requirements Within Floor Areas

(1)  Except as provided in Sentences (2) to (12), the requirements in Section 3.3. shall apply.

(2)  A corridor need not be constructed as a public corridor where the travel distance, measured from inside the rental space to the nearest exit, is not more than 15 m provided that the corridor walls

(a)	are of noncombustible construction,

(b)	have no openings other than doors and the doors are of solid construction, and

(c)	are continuous from the floor to the underside of the floor above, the ceiling or the roof.

(3)  Where the building is sprinklered, doors in a public corridor do not require to be equipped with self-closing devices and latches provided that the travel distance is measured from inside the rental space to the nearest exit.

(4)  Egress doors from a rental space are not required to swing in the direction of exit travel or swing on a vertical axis provided

(a)	the area of the rental space is not more than 50 m2, and

(b)	the distance of travel within the rental space is not more than 10 m.

(5)  Where egress doors from a rental space open onto a corridor and swing in the direction of exit travel, the corridor shall be not less than 1 500 mm wide, and the doors shall be not more than 914 mm wide.

(6)  Where egress doors from a rental space open onto a corridor and do not swing in the direction of exit travel, the corridor shall be not less than 1 100 mm in width.

(7)  Dead end corridors are not permitted.

(8)  Corridors shall be provided with

(a)	natural lighting which shall be uniformly distributed and be at least 4% of the corridor area, or

(b)	emergency lighting, conforming to Sentences 3.2.7.4.(1) and (2), which shall provide average levels of illumination not less than 10 lx at floor level.

(9)  Not more than two dwelling units shall be contained within one of the buildings on the property.

(10)  Dwelling units shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 2 h.

(11)  A fire separation is not required between a dwelling unit and an office where the office is not more than 50 m2 in area.

(12)  The fire separations required in Sentence 3.3.1.1.(1) need not be provided between individual rental spaces.

3.10.2.5. Exit Requirements

(1)  Except as provided in Sentences (2) and (3), the requirements in Section 3.4. shall apply.

(2)  The clear width of an exit stair shall be not less than 1 100 mm.

(3)  Exit doors from rental spaces are not required to swing on a vertical axis provided

(a)	the area of the rental space is not more than 50 m2, and

(b)	the travel distance within the rental space is not more than 10 m.

3.10.2.6. Service Facilities

(1)  Except as provided in Sentence (2), the requirements in Section 3.6. shall apply.

(2)  Except where located in and serving only the dwelling units, a fuel-fired appliance shall be located in a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

3.10.2.7. Sanitary Facilities

(1)  Except as provided in Sentence (2), the requirements in Subsection 3.7.4. shall apply.

(2)  Except as permitted in Sentences 3.7.4.1.(2) and (3), two washrooms, each containing a water closet and a lavatory, shall be provided within one of the buildings on the property.

3.10.3. Additional Requirements for Buildings Containing more than 1 Storey

3.10.3.1. Application

(1)  The requirements in this Subsection apply to all buildings except a 1 storey building which does not contain a basement or mezzanine.

3.10.3.2. Spatial Separations

(1)  Except as provided in Sentence (2), the requirements in Subsection 3.2.3. shall apply.

(2)  The distance between buildings shall be not less than 9 m.

3.10.3.3. Fire Alarm Systems

(1)  Except as provided in Sentences (2) and (3), the requirements in Subsection 3.2.4. shall apply.

(2)  A fire alarm system shall be installed.

(3)  Within the first storey, manual pull stations are required only in corridors.

3.10.3.4. Provisions for Fire-fighting

(1)  Except as provided in Sentences (2) to (4), the requirements in Subsection 3.2.5. shall apply.

(2)  Access routes for fire department vehicles shall be provided and shall be not less than 9 m wide.

(3)  Hydrants shall be located in the access routes required in Sentence (2) so that

(a)	for a building provided with a fire department connection for a standpipe system or a sprinkler system

(i)	a fire department pumper vehicle can be located adjacent to a hydrant, and

(ii)	the unobstructed path of travel for the firefighter from the vehicle to the fire department connection is not more than 45 m, and

(b)	for a building which is not sprinklered, a fire department pumper vehicle can be located in the access route so that the unobstructed path of travel for the firefighter is not more than

(i)	45 m from the hydrant to the vehicle, and

(ii)	45 m from the vehicle to every opening in the building.

3.10.3.5. Standpipe Systems

(1)  Except as provided in Sentence (2), the requirements in Subsection 3.2.9. shall apply.

(2)  Hose stations are not required in the first storey.

3.10.4. Additional Requirements for 1 Storey Buildings

3.10.4.1. Application

(1)  The requirements in this Subsection apply to 1 storey buildings which do not contain a basement or mezzanine.

3.10.4.2. Building Area

(1)  For the purposes of Subsection 3.2.2., building area means

(a)	the building area of each building,

(b)	the total of the building areas of all buildings as a group, or

(c)	the total of the building areas of any number or group of buildings.

3.10.4.3. Spatial Separations

(1)  Except as provided in Sentences (2) to (4), the requirements in Subsection 3.2.3. shall apply.

(2)  Where the building area conforms to Clause 3.10.4.2.(1)(b), the limiting distance requirements shall not apply between individual buildings.

(3)  Where the building area conforms to Clause 3.10.4.2.(1)(c)

(a)	the limiting distance requirements shall apply between each group of buildings, but not between individual buildings within a group, and

(b)	the distance between each group of buildings shall be not less than 9 m.

(4)  The distance between individual buildings within a group shall be not less than 6 m.

3.10.4.4. Fire Alarm Systems

(1)  Except as provided in Sentence (2), the requirements in Subsection 3.2.4. shall not apply.

(2)  The requirements for smoke alarms in Article 3.2.4.21. shall apply to a dwelling unit.

3.10.4.5. Provisions for Fire-fighting

(1)  Except as provided in Sentences (2) to (7), the requirements in Subsection 3.2.5. shall not apply.

(2)  Access routes for fire department vehicles shall be provided and shall be not less than 9 m wide.

(3)  Hydrants shall be located in the access routes required in Sentence (2) so that the locations conform to Sentence 3.10.3.4.(3).

(4)  The access routes required in Sentence (2) shall conform to the requirements in Sentence 3.2.5.6.(1).

(5)  An adequate water supply for fire-fighting shall be provided for every building.

(6)  Where a sprinkler system is installed, the system shall conform to the requirements in Articles 3.2.5.13., 3.2.5.16. and 3.2.5.18.

(7)  Where combustible sprinkler piping is installed, it shall conform to the requirements in Article 3.2.5.14.

Section 3.11. Public Pools

3.11.1. General

3.11.1.1. Application

(1)  This Regulation applies to every public pool.

(2)  This Section applies to the design and construction of site assembled and manufactured pools that are intended for use as public pools.

(3)  Where material alterations to a public pool or the equipment installed in a public pool affect the bottom slope, the water volume or the capacity of the recirculation system, the adversely affected portions shall comply with the requirements of this Code.

(4)  Where material alterations or repairs concern any pool fitting passing water and/or air in or out of the pool tank, the affected fitting shall comply with Sentences 3.11.8.1.(14) to (20).

Section 3.11A.  Public Spas

3.11A.1.  General

3.11A.1.1.  Application

(1)  This Section applies to the design and construction of site-assembled public spas and factory-built public spas.

(2)  If material alterations to a public spa or the equipment installed in a public spa affect the bottom slope, the water volume or the capacity of the water circulation system, the adversely affected portions shall comply with the requirements of this Code.

(3)  Except as provided in Sentence (4), if material alterations or repairs concern any pool fitting that passes water or air, or both, in or out of the pool tank, the affected fitting shall comply with Sentences 3.11.8.1.(20) and 3.11A.4.1.(4) to (10).

(4)  If the material alterations or repairs concern a fitting cover or grille, the affected fitting cover or grille shall comply with Sentences 3.11A.4.1.(7) to (10).

(5)  For the purposes of this Section, every reference to a public pool or a recirculation system in a definition in Article 1.1.3.2., or a Sentence or Clause in Section 3.11. that is made applicable to public spas by this Section, shall be deemed to be a reference to a public spa or water circulation system, respectively.

3.11A.2.  Public Spa and Deck Design and Construction Requirements

3.11A.2.1.  Construction Requirements

(1)  In addition to the requirements of this Subsection, public spas shall comply with the requirements of Sentences 3.11.3.1.(13) to (17), (19), (20) and (22) and Clause 3.11.3.1.(24)(a).

(2)  A public spa shall be constructed to have a water depth of not more than 1 200 mm.

(3)  The slope of the bottom of any portion of a public spa shall not exceed 8%.

(4)  A public spa shall be surrounded by a hard-surfaced pool deck that

(a)	shall have a minimum clear deck space of not less than 1.8 m at the main entrance point,

(b)	shall have a clear deck space of 900 mm on all sides, except as required by Clause (a) and permitted by Sentence (5),

(c)	shall be sloped away from the pool to waste drains or to adjacent lower ground at a slope of between 2% and 4%, in the case of an outdoor public spa, and

(d)	shall be impervious and sloped away from the pool to waste drains at a slope of between 1% and 4%, in the case of an indoor public spa.

(5)  One section of the hard-surfaced pool deck that does not exceed 25% of the perimeter of the public spa may have a minimum clear deck space of not more than 300 mm if

(a)	the public spa has an area less than 6 m2, and

(b)	the public spa has no interior dimension more than 2.5 m.

(6)  The maximum depth of water to a seat or bench in a public spa shall be 600 mm.

(7)  If a set of steps is provided for entry into and egress from the public spa water, the steps

(a)	shall be equipped with a handrail,

(b)	shall have a non-slip surface, and

(c)	shall have a band of contrasting colour along the entire juncture of the side and top of the edges.

(8)  Every public spa shall be provided with dressing rooms, water closets and shower facilities that are conveniently available on the premises.

3.11A.3.  Ramps Into Public Spas

3.11A.3.1.  Ramps into Spas

(1)  Not more than 50% of the total perimeter of a public spa may be replaced by one or more ramps that permit a bather seated in a wheelchair to enter the water with or without the wheelchair.

(2)  If a public spa has one or more ramps described in Sentence (1), the public spa shall comply with Sentences 3.11.5.1.(1) to (3) and (5) to (8).

3.11A.4.  Water Circulation for Public Spas

3.11A.4.1.  Water Circulation Systems

(1)  In addition to the requirements of this Subsection, the water circulation system of a public spa shall comply with the requirements of Sentences 3.11.8.1.(2), (3), (6), (7), (9), (10), (11), (13) and (20).

(2)  A public spa shall be equipped with a water circulation system that is capable of filtering, disinfecting and passing the public spa water through the public spa with a turnover period of not more than

(a)	30 minutes for a public spa with a volume of water that exceeds 6 m3,

(b)	20 minutes for a public spa with a volume of water that exceeds 4 m3 but does not exceed 6 m3, or

(c)	15 minutes for a public spa with a volume of water that does not exceed 4 m3.

(3)  If cartridge-type filters are used for a public spa, the filters shall be a surface-type that is designed for a maximum flow rate of 0.27 L/s/m2 of effective filter area.

(4)  Except as provided in Sentence (6), every circulation system in a public spa shall be served by a minimum of two suction or gravity outlets

(a)	that are interconnected to a full size manifold, and

(b)	except as provided in Sentence (5), that are separated by a clear distance of not less than 900 mm.

(5)  If compliance with Clause (4) (b) is impracticable because of dimensional restrictions at the bottom of the public spa, the outlets may be located on two different planes of the public spa if

(a)	at least one of the outlets through which the public spa can be emptied to a full-size manifold is located on the bottom of the public spa, and

(b)	the bottom of all outlets, other than skimmers, are not more than 75 mm from the floor of the public spa.

(6)  A circulation system in a factory-built public spa may be served by a built-in suction or gravity outlet with multiple openings that are connected to a full-size manifold.

(7)  All fittings at or below the water surface that allow water or air or both to be passed to or from the public spa shall be securely held in place by corrosion resistant fastening that requires a tool for removal and is galvanically compatible with the fittings and grilles or covers.

(8)  Except as provided in Sentence (9), all suction or gravity fittings installed at or below the water line of a public spa shall

(a)	have a maximum opening of 7 mm in one direction, and

(b)	be designed so that the flow of water through the openings does not exceed 0.45 m/s.

(9)  Sentence (8) does not apply to suction and gravity outlets which are equipped with anti-entrapment covers that comply with the requirements of ANSI/ASME A112.19.8M, “Suction Fittings for Use in Swimming Pools, Wading Pools, Spas, Hot Tubs, and Whirlpool Bathtub Appliances”.

(10)  The calculation of water velocities for the purposes of Clause (8) (b) and Sentences (11) and (12) and the calculation of water flow rates for the purposes of Sentence (9) shall be based on the assumption that all possible sources of suction flow are present at the same time.

(11)  The water velocity in a suction pipe shall not exceed 1.8 m/s.

(12)  The water velocity in a pressure pipe shall not exceed

(a)	3.0 m/s for plastic piping, and

(b)	1.8 m/s for copper piping.

(13)  Every suction system that serves a public spa shall be equipped with a vacuum relief mechanism which shall include

(a)	a vacuum release system,

(b)	a vacuum limit system, or

(c)	other engineered systems which are designed, constructed and installed to conform to good engineering practice appropriate to the circumstances.

(14)  Equipment shall be installed to continuously disinfect the water in a public spa by means of a chlorination, hypochlorination or bromination system that is capable of regulating the dosage of chlorine or bromine.

(15)  If a two-speed pump is utilized for a public spa, the filter and heater shall be sized to accommodate the maximum pump output, without exceeding the manufacturer’s design flow rate of the filter element or heater and without by-passing the filter element.

(16)  A public spa equipped with hydro-massage jet fittings shall be provided with a timing device

(a)	that controls the period of operation of the jet pump, and

(b)	that is placed in a location where the user must exit the public spa to reset the timer.

(17)  A public spa water heater shall be equipped with an upper limit cut-off device

(a)	that is independent of the normal public spa water temperature thermostat, and

(b)	that limits the maximum water temperature of the public spa to 40ºC.

(18)  A public spa shall be equipped with a water circulation system that is capable of both completely and partially draining and refilling the public spa water.

3.11A.5.  Emergency Provisions for All Public Spas

3.11A.5.1.  Lighting and Emergency Provisions

(1)  In addition to the requirements of this Subsection, public spas shall comply with the requirements of Sentences 3.11.10.1.(1) to (6).

(2)  An emergency telephone directly connected to an emergency service or to the local telephone utility shall be installed within 30 m of the public spa.

(3)  All pumps used in a public spa shall be capable of being deactivated by an emergency stop button that is clearly labelled and located within the immediate vicinity of the public spa.

(4)  The emergency stop button required in Sentence (3)

(a)	shall be a switch separate from the public spa’s timing device,

(b)	shall activate an audible and a visual signal when used, and

(c)	shall have an emergency sign conforming to Sentence 3.11.10.1.(14).

(5)  If a public spa and public pool are located in the same room or space, the emergency stop buttons required in Sentences (3) and 3.11.10.1.(12) shall deactivate all pumps serving the public spa and public pool.

3.11A.6.  Service Rooms and Storage for All Public Spas

3.11A.6.1.  Service Rooms and Storage Facilities

(1)  Service rooms and storage facilities for all public spas shall comply with the requirements of Article 3.11.11.1.

3.11.2. Designations of Public Pools

3.11.2.1. Pool Designations

(1)  Every public pool shall be designated as being either a Class A pool or a Class B pool in accordance with Sentence (2) or (3).

(2)  A Class A pool is a public pool to which the general public is admitted or that is

(a)	operated in conjunction with or as a part of a program of an educational, instructional, physical fitness or athletic institution or association, supported in whole or in part by public funds or public subscription, or

(b)	operated on the premises of a recreational camp, for use by campers and their visitors and camp personnel.

(3)  A Class B pool is a public pool that is

(a)	operated in conjunction with six or more dwelling units, suites, single family residences, or any combination thereof for the use of occupants or residents and their visitors,

(b)	operated in conjunction with a mobile home park for the use of residents or occupants and their visitors,

(c)	operated on the premises of a hotel for the use of its guests and their visitors,

(d)	operated on the premises of a campground for the use of its tenants and their visitors,

(e)	operated in conjunction with a club for the use of its members and their visitors, or

(f)	operated in conjunction with an establishment or institution classified in Table 3.1.2.1. as,

(i)	Group B, Division 1, major occupancy, or

(ii)	Group B, Division 2 or 3, major occupancy, for the use of residents or occupants and their visitors.

3.11.3. Pool and Pool Deck Design and Construction Requirements for all Class A and Class B Pools

3.11.3.1. Construction Requirements

(1)  Except as otherwise required in Subsections 3.11.4., 3.11.5., 3.11.6., and 3.11.7. or otherwise exempted in Sentences (2) and (3), Class A pools and Class B pools shall be designed and constructed to comply with Sentences (2) to (25).

(2)  Where a Class B pool is constructed for use solely in conjunction with a club, child care facility, day camp or establishment or institution for the care of persons who are infirm, aged or in custodial care, the pool shall be exempt from the requirements of Clause (9)(a) and Sentences (13) and (14).

(3)  Where a Class B pool is constructed for use solely in conjunction with an establishment or institution for the treatment of persons who are disabled or ill, the pool shall be exempt from the requirements of Sentences (6) and (7), Clause (9)(a) and Sentences (13) and (14).

(4)  A public pool shall be constructed to have a water depth of not less than 750 mm except for

(a)	a modified pool,

(b)	a wave action pool,

(c)	a pool for therapeutic use,

(d)	a beach entry ramp, and

(e)	a pool described in Sentence 3.11.5.1.(1).

(5)  The beach entry ramp permitted in Clause 4(d) shall be protected with permanent barriers between 900 mm to 1 200 mm along the pool deck to prevent entry into the pool until the minimum water pool depth is 750 mm.

(6)  Except for a modified pool, a wave action pool and a pool used exclusively for scuba diving, the slope of the bottom of any portion of a public pool shall not exceed

(a)	8% where the water depth is 1 350 mm or less,

(b)	33% where the water depth is more than 1 350 mm and less than 2 000 mm, and

(c)	50% where the water depth is 2 000 mm or more.

(7)  Except for a modified pool and wave action pool, where the slope of any portion of the bottom of a public pool is more than 8%, the walls of the pool shall be equipped with recessed fittings to which a safety line supported by buoys can be attached across the surface of the water and the recessed fittings shall be installed at a horizontal distance of at least 300 mm measured from the vertical projection of the top of the slope in the direction of the shallow end of the pool.

(8)  Except for a modified pool, wave action pool and a pool described in Sentence 3.11.5.1.(1), the side and end walls of a public pool shall be vertical from the top of the walls to within 150 mm of the bottom except at steps or recessed ladders or in water depths of 1 350 mm or more.

(9)  Except for a modified pool and wave action pool and except as provided in Sentence (11), a public pool shall be surrounded by a hard-surfaced pool deck that shall

(a)	except for a pool described in Sentence 3.11.5.1.(1), be not less than 1 800 mm wide and provide at least 900 mm width of clear passage,

(i)	behind any diving board and its supporting structure, and

(ii)	between any column piercing the deck and the edge of the pool or between the column and outer perimeter of the pool deck,

(b)	in the case of an outdoor pool, be sloped away from the pool to waste drains or to adjacent lower ground at a slope of between 2% and 4%, and

(c)	in the case of an indoor pool, be impervious and sloped away from the pool to waste drains at a slope of between 1% and 4%.

(10)  Where a public pool is constructed with a ledge, the ledge shall

(a)	be placed only in parts of the pool where the water depth is 1 350 mm or more,

(b)	be not more than 200 mm wide,

(c)	be at least 1 000 mm below the water surface,

(d)	where located on the side of the pool, be gradually tapered towards the shallow end of the pool in such a manner as to prevent a harmful obstruction, and

(e)	have a band of contrasting colour along the entire juncture of the side and top of the ledge.

(11)  Notwithstanding Sentences (12) to (16), where a public pool is constructed on any level surface with walls rising above that surface and has a constant water depth not exceeding 1 100 mm and a water surface area not exceeding 100 m2, the pool deck may be an elevated platform surrounding the pool if it has

(a)	an unobstructed width of not less than 900 mm,

(b)	a height of at least 75 mm above grade or pavement elevation,

(c)	6 mm wide openings for drainage, and

(d)	a non-slip surface that is capable of being kept clean and disinfected.

(12)  Except for a modified pool and wave action pool, where a pool deck projects over the water surface, the projection shall not exceed 50 mm.

(13)  Except for a modified pool and wave action pool, the pool deck shall be separated from any adjacent spectator area or gallery and from any spectator access to such area or gallery by a gate or other barrier.

(14)  Except for a modified pool and wave action pool, the perimeter of the pool deck shall be clearly delineated by painted lines or other means where any area contiguous to the pool deck may be confused with the deck.

(15)  Perimeter drainage shall be provided where necessary to prevent surface run-off from draining onto the pool deck.

(16)  Except for a modified pool, one or more hose bibs shall be installed near the perimeter of the pool deck in locations convenient for flushing the pool deck.

(17)  Except for a modified pool and wave action pool, where access to the pool enclosure is over any surface that is not subject to regular cleaning and sanitizing, a foot spray to wash feet by means of a spray running freely to waste shall be provided at each such access.

(18)  Except for a modified pool and wave action pool, at least one ladder or set of steps shall be provided in both the deep and shallow areas of a public pool for entry into and egress from the pool water.

(19)  The pool deck, the submerged parts of a public pool, the walls or partitions adjacent to a pool deck and the pavement or floor adjacent to a pool deck shall have surfaces that permit thorough cleaning.

(20)  Except for markings for safety or competition purposes, submerged surfaces in public pools shall be finished white or light in colour.

(21)  Except in a modified pool, a black disc 150 mm in diameter on a white background shall be affixed to the bottom of a public pool within the area of its greatest depth.

(22)  A public pool shall be equipped with lockable doors or other barriers capable of preventing public access to the pool deck.

(23)  Except for a modified pool, wave action pool or a pool installed at a recreational camp, a Class A pool shall be provided with

(a)	where the water surface area is greater than 150 m2 but not greater than 230 m2, at least one lifeguard control station, and

(b)	where the water surface area is greater than 230 m2, at least two lifeguard control stations.

(24)  Except for a modified pool, every public pool shall display on the deck clearly marked figures, not less than 100 mm high, that set out

(a)	the water depths indicating the deep points, the breaks between gentle and steep bottom slopes and the shallow points,

(b)	the words SHALLOW AREA at one or more appropriate locations, and

(c)	where the water depth exceeds 2 500 mm, the words DEEP AREA at one or more appropriate locations.

(25)  Except for a modified pool and a pool to which Sentence 3.11.5.1.(4) applies, every public pool having a maximum water depth of 2 500 mm or less shall display a warning notice posted in a location clearly visible to divers on which is printed in letters at least 150 mm high, the words CAUTION — AVOID DEEP DIVES or SHALLOW WATER — NO DIVING.

3.11.4. Public Pools Equipped with Diving Boards or Diving Platforms

3.11.4.1. Diving Boards or Platforms

(1)  No diving board or diving platform shall be installed in a public pool unless the requirements of Sentences (5) to (17) are met but the requirements for a diving platform do not apply to a starting platform.

(2)  No diving board or diving platform shall be installed in a modified pool or a wave action pool.

(3)  Where a public pool is equipped with a diving board or a diving platform, the board or platform shall have a non-slip surface.

(4)  Where a diving board or a diving platform in a public pool is more than 600 mm above the water surface, the board or platform shall be equipped with one or more adjacent handrails.

(5)  Where a public pool is equipped with a diving board or a diving platform not more than 3 m in height above the water surface, the pool shall be designed and constructed in conformance with Sentences (6) to (15).

(6)  The depth of water in the area directly below a horizontal semi-circle in front of a diving board or diving platform having a radius of 3 m measured from any point on the front end of the board or platform shall not be less than

(a)	2 750 mm, where a board is 600 mm or less in height above the water surface,

(b)	3 m, where a board or platform is greater than 600 mm but not more than 1 000 mm in height above the water surface, and

(c)	3.65 m, where a board or platform is greater than 1 000 mm but not more than 3 m in height above the water surface.

(7)  Except as permitted in Sentence (8), the water depth in a public pool shall be at least 1 350 mm at the horizontal arc having a radius of 9 m measured from any point on the front end of the diving board or diving platform and intersecting the vertical projections of the walls of the pool.

(8)  Where a Class B pool is equipped with a diving board 600 mm or less in height above the water

(a)	the water depth shall be at least 1 350 mm at the horizontal arc having a radius of 7.5 m measured from any point on the front end of the diving board, and

(b)	a warning notice, on which is printed in letters at least 150 mm high, the words DANGER – AVOID DEEP OR LONG DIVES, shall be posted in a location clearly visible to divers.

(9)  The slope of the bottom of a public pool having a diving board or diving platform shall not change by more than 17% where the water depth is less than the applicable depth set out in Sentence (6) and greater than the depth set out in Sentence (7) or (8), as applicable.

(10)  The horizontal distance between the vertical projection of the centre line of a diving board or diving platform and the vertical projection of the centre line of another board or platform shall be at least 2 750 mm.

(11)  The horizontal distance between the centre line of a diving board or diving platform and the vertical projection of the closest side or any ledge on the closest side of a public pool shall be at least

(a)	3 m, where a diving board or diving platform is 1 000 mm or less in height above the water surface, and

(b)	3.6 m, where a diving board or diving platform is greater than 1 000 mm in height above the water surface.

(12)  A diving board or a diving platform 600 mm or less in height above the water surface shall project over the water a horizontal distance of at least 900 mm from the vertical projection of a pool wall under it.

(13)  A diving board greater than 600 mm in height above the water surface shall project over the water a horizontal distance of at least 1 500 mm from the vertical projection of the pool wall under it.

(14)  A diving platform greater than 600 mm in height above the water surface shall project a horizontal distance of at least 1 200 mm from the vertical projection of the pool wall under it.

(15)  The space above a diving board or diving platform shall be unobstructed and shall consist of at least

(a)	a space having a width of 2 500 mm on each side of the centre line of the board or platform, a length equal to the sum of the horizontal distance the board or platform projects over the water plus 3 m, and a height of

(i)	3.65 m above a diving board 3.65 m or less in length,

(ii)	5 m above a diving board greater than 3.65 m in length, or

(iii)	3 m above a diving platform, and

(b)	the space below the planes originating from the front and sides of the uppermost horizontal plane of the space determined under Clause (a) and sloping downwards at 30° from the horizontal.

(16)  A diving board or diving platform greater in height than 3 m above the water surface shall be equipped with a gate, barrier or other device capable of preventing access thereto.

(17)  Where a public pool is to be equipped with diving boards or diving platforms greater than 3 m in height above the water surface, the design of the diving boards or diving platforms and the corresponding water depths and clearances shall be in accordance with the “Rules and Laws Governing Swimming, Diving, Water Polo and Synchronized Swimming” published in 1984 by FINA.

3.11.5. Ramps into Public Pools in Group B, Division 2 or 3, Major Occupancies

3.11.5.1.  Ramps into Pools

(1)  Notwithstanding Sentences 3.11.3.1.(4) and (7) and Clause 3.11.3.1.(9)(a), where a public pool is constructed in a building containing a Group B, Division 2 or 3, major occupancy, and has a water depth not exceeding 1 500 mm and a water surface area not exceeding 100 m2, the pool deck contiguous to not more than 50% of the total perimeter of the pool may be replaced by one or more ramps that will permit a bather seated in a wheelchair to enter the water with or without the wheelchair.

(2)  Where a public pool has one or more ramps as described in Sentence (1), the pool shall be designed and constructed to comply with Sentences (3) to (8).

(3)  A ramp referred to in Sentence (1) shall have

(a)	a handrail having a height between 800 mm and 900 mm along each side of the ramp and running parallel to the slope of the ramp,

(b)	a width of at least 1 100 mm,

(c)	a curb or other means to prevent a wheelchair from falling off the side of the ramp,

(d)	surface finishes capable of being kept clean, sanitary and free from slipperiness, and

(e)	a landing at the bottom at least 1 500 mm in length and the same width as the ramp.

(4)  Notwithstanding Sentence 3.11.3.1.(25), a warning notice, on which is printed in letters at least 150 mm high, the words CAUTION – NO DIVING, shall be posted conspicuously on each wall or fence line enclosing the pool.

(5)  There shall be a curb along the perimeter of the pool except at steps, ladders and ramp entrances.

(6)  The curb shall have

(a)	a height of 50 mm,

(b)	rounded edges,

(c)	a coved base, and

(d)	a raised nosing at the top to serve as a fingerhold for a bather in the water.

(7)  Where a ramp that is not submerged is adjacent to the pool wall and is used for access to the water, the pool shall be constructed so that

(a)	the landing at the bottom of the ramp is at least 450 mm but not more than 550 mm below the top of the wall separating the ramp from the pool,

(b)	the landing is equipped with a floor drain at its lowest point,

(c)	the top of the wall between the pool and the ramp is at least 250 mm and not more than 300 mm in width,

(d)	the pool deck is capable of accommodating a movable barrier separating the deck from the ramp,

(e)	the water depth at the landing shall be accurately and clearly marked at the landing in figures at least 100 mm high on the top of the wall separating the pool from the ramp, and

(f)	the ramp shall have a slope not exceeding 8%.

(8)  Where a submerged ramp is adjacent to the pool wall and is used for access to the water, the pool shall be constructed so that

(a)	the water depth at the bottom of the ramp is at least 600 mm and not greater than 900 mm,

(b)	a hard-surfaced area that is at least 750 mm wide is contiguous to the entire length of the part of the submerged ramp that pierces any part of the deck,

(c)	the area described in Clause (b) is capable of accommodating a movable barrier that separates the area from the deck,

(d)	the finishes in submerged portions of the ramps and curbs are different in colour or shade from each other and from that of the pool walls and bottom, and

(e)	the submerged ramp has a slope not exceeding 11%.

3.11.6. Modified Pools

3.11.6.1.  Construction Requirements

(1)  A modified pool is exempt from Sentences (4) to (9), (12), (13), (14), (16), (17), (18), (21), (23), (24) and (25) of Article 3.11.3.1. and Sentence 3.11.8.1.(12).

(2)  A modified pool shall be designed and constructed to comply with Sentences (3) to (9).

(3)  A modified pool and its pool deck shall be constructed of hard-surfaced material that permits thorough cleaning.

(4)  The slope of the bottom of any portion of a modified pool shall not exceed 8%.

(5)  The depth of the water in any portion of a modified pool shall not be more than 1 800 mm.

(6)  A modified pool shall be surrounded on all sides by a hard-surfaced pool deck that shall

(a)	be at least 3 m wide,

(b)	have a continuous crest surrounding the pool at least 100 mm above the pool water surface, and

(c)	be sloped to shed water from the crest to the outer perimeter of the pool deck.

(7)  A modified pool shall be provided with two or more drain fittings covered with protective grilles with openings having an aggregate area of at least 10 times the internal cross-sectional area of the outlet pipe or pipes connected to the recirculation system that is capable of completely draining the pool.

(8)  Provision shall be made for lifeguard control stations adjacent to the edge of the water at intervals of not more than 60 m.

(9)  The bottom of a modified pool shall be marked with continuous black contour lines

(a)	150 mm wide located where the water depth is 600 mm, and

(b)	300 mm wide located where the water depth is 1 200 mm.

3.11.7. Wave Action Pools

3.11.7.1.  Construction Requirements

(1)  A wave action pool is exempt from Sentences (4) to (9), (12) to (14), (17), (18) and (23) of Article 3.11.3.1. and Sentence 3.11.8.1.(12).

(2)  A wave action pool shall be designed and constructed to comply with Sentences (3) to (11).

(3)  The slope of the bottom of any portion of a wave action pool

(a)	shall not exceed 8% where the still water depth is less than 1 000 mm, and

(b)	shall not exceed 11% where the still water depth is 1 000 mm or more.

(4)  The walls of a wave action pool shall be vertical from the water surface to within 150 mm of the bottom.

(5)  There shall be a hard-surfaced pool deck at least 3 m wide immediately adjacent to the pool wall at the shallow end of the pool and at least 1 500 mm wide immediately adjacent to all walls of the pool.

(6)  Provision shall be made for two or more lifeguard control stations on each side of the pool deck adjacent to which the still water depth exceeds 1 000 mm.

(7)  Sets of steps or ladders recessed into pool side walls and having continuous vertical grab bars on each side thereof shall be located at intervals of not more than 7.5 m along portions of the pool where the still water depth exceeds 1 000 mm, except that no steps or ladders shall be located within 3 m of the corners at the deep end of the pool.

(8)  Except at recessed steps or ladders, the pool deck along each side of a wave action pool adjacent to which the water depth is 2 300 mm or less shall be equipped with a barrier supported by posts or a wall that

(a)	is 1 000 mm in height,

(b)	is located 1 000 mm or less from the side of the pool, and

(c)	has warning notices affixed thereto at intervals not exceeding 7.5 m signifying clearly that jumping and diving are prohibited along the sides of the pool.

(9)  Skimming devices shall be designed and suitably located to remove surface film when no waves are induced in a wave action pool.

(10)  A system capable of deactivating the wave-making equipment shall be installed with readily accessible push buttons located on the pool deck not more than 30 m apart, adjacent to each side and the deep end of the pool.

(11)  A wave action pool shall be equipped with a first-aid room located within 50 m of the pool.

3.11.8. Recirculation for Public Pools

3.11.8.1.  Recirculation Systems

(1)  Every public pool shall be equipped with a recirculation system.

(2)  For the purposes of this Subsection, the water in a public pool and its recirculation system shall be deemed not to be potable water.

(3)  The water in a public pool and its recirculation system shall be separated from the potable water supply and from the sewer or drainage system into which it drains by air gaps or other devices that prevent

(a)	the water in the pool or its recirculation system from flowing back into the potable water supply, and

(b)	the water in the sewer or drainage system from flowing back into the pool or its recirculation system.

(4)  The recirculation system of a public pool shall be designed, constructed and equipped to comply with Sentences (5) to (20).

(5)  The recirculation system of a public pool shall be capable of filtering, disinfecting and passing through the pool each day a volume of water of at least

(a)	in the case of a Class A pool, other than a modified pool or a wave action pool, six times the total water volume of the pool,

(b)	in the case of a Class B pool, other than a wave action pool, four times the total water volume of the pool,

(c)	in the case of a modified pool, three times the total water volume of the pool, and

(d)	in the case of a wave action pool, six times the total water volume of the pool.

(6)  A recirculation system shall be equipped with a flow meter registering the rate of water flow.

(7)  All pools shall be provided with automatic make-up water devices and provided with water meters to register the volume of all make-up water added to a public pool or its recirculation system.

(8)  Equipment shall be installed to continuously disinfect the water in a public pool by means of

(a)	a chlorination or hypochlorination system provided with a chemical controller for regulating the dosage of chlorine and capable of providing not less than

(i)	in the case of an outdoor pool, other than a wave action pool, 300 g of chlorine per day per 10 000 L of total pool capacity,

(ii)	in the case of an indoor pool, other than a wave action pool, 200 g of chlorine per day per 10 000 L of total pool capacity,

(iii)	in the case of an outdoor wave action pool, 1 200 g of chlorine per day per 10 000 L of total pool capacity, and

(iv)	in the case of an indoor wave action pool, 800 g of chlorine per day per 10 000 L of total pool capacity, or

(b)	a bromination system capable of maintaining in the pool water a total bromine residual of 3 mg/L.

(9)  Gas chlorination equipment for a public pool shall contain a mechanism whereby the chlorine feed shall automatically terminate whenever the recirculation system ceases to supply clean water to the pool.

(10)  All exposed potable water piping and chlorine piping within a public pool water treatment service room shall be colour coded by means of

(a)	painting the entire outer surface of the piping, or

(b)	coloured bands at least 25 mm in width that are spaced along the piping at intervals of not more than 1 200 mm.

(11)  The colour coding referred to in Sentence (10) shall be yellow for chlorine and green for potable water.

(12)  Except for a modified pool and wave action pool, a public pool shall be equipped with overflow gutters or surface skimmers connected to the recirculation system that are capable of removing surface film from the surface of the water and withdrawing each day and discharging to the waste drains up to 15% of the total volume of pool water.

(13)  A public pool shall be equipped with clean water inlets arranged in conjunction with surface skimmers or overflow gutters to provide uniform distribution and circulation of clean water.

(14)  Except as permitted in Sentence (19), all fittings at or below the water surface that allow water and/or air to be passed to or from the public pool shall

(a)	have a maximum opening of 7 mm in one direction, and

(b)	be securely held in place by corrosion resistance fastening that require a tool for removal and are galvanically compatible with the fittings and grilles or covers.

(15)  Except as provided in Sentence 3.11.6.1.(7) for a modified pool, all fittings below the water surface that provide suction or gravity flow in a public pool shall

(a)	be provided with a minimum of two suction or gravity outlets interconnected to a full size manifold, and

(b)	be separated by a clear distance of not less than 1 200 mm.

(16)  Except as provided in Sentence 3.11.6.1.(7) for a modified pool, water in all public pools shall be capable of being emptied through the pool drains in twelve hours or less.

(17)  Except as provided in Sentence 3.11.6.1.(7) for a modified pool, openings in suction or gravity fittings shall

(a)	be such that the flow of water does not exceed 0.45 m/s and the velocity is calculated assuming all possible sources of suction flow are present at one time, and

(b)	be such that every suction fitting located within 1 000 mm of the water surface, except for skimmers and gutter fittings, contain openings with a minimum aggregate area of 0.2 m2.

(18)  Except for skimmers and gutters, all submerged suction and gravity fittings shall be clearly and permanently marked with a 50 mm wide band in a contrasting colour.

(19)  Fittings returning water and/or air to the pool tank that are located within 300 mm of the water surface are permitted to have openings with one dimension more than 7 mm but shall contain no openings more than 25 mm in diameter.

(20)  Submerged skimmer equalizer fittings and vacuum fittings are not permitted in public pools.

3.11.9. Dressing Rooms, Locker Facilities, and Plumbing Facilities for all Public Pools

3.11.9.1.  Dressing Rooms and Sanitary Facilities

(1)  Except as otherwise permitted in Sentences (2) and (3), every public pool shall be equipped with dressing rooms, locker rooms, shower heads, water closets, urinals, lavatories and drinking fountains which shall be designed, constructed and equipped to comply with Sentences (4) to (14).

(2)  Where a Class A pool is installed on the premises of a recreational camp, dressing rooms, locker rooms, shower heads, water closets, urinals, lavatories and drinking fountains are not required if

(a)	dressing, water closet and shower facilities are conveniently available for bathers elsewhere on the premises, and

(b)	foot sprays are provided in accordance with Sentence 3.11.3.1.(17).

(3)  Where a Class B pool is installed, dressing rooms, locker rooms, shower heads, lavatories, water closets, drinking fountains and urinals are not required if

(a)	dressing, water closet and shower facilities are conveniently available elsewhere on the premises for bathers when the pool is open for use, and

(b)	foot sprays are provided in accordance with Sentence 3.11.3.1.(17).

(4)  The minimum number of water closets, urinals and lavatories shall be determined from Article 3.7.4.3. and Table 3.7.4.3.C. for an occupant load based on

(a)	the formula in Sentence 3.1.16.3.(1) for all public pools, except a wave action pool, or

(b)	the formula in Sentence 3.1.16.3.(2) for a wave action pool.

(5)  A minimum of one shower head shall be provided for every 40 bathers.

(6)  Where dressing and locker rooms, water closets and urinals are provided in conjunction with a public pool, they shall be located in such a manner that bathers, after using them, shall pass through or by a shower area to reach the pool deck.

(7)  All shower heads shall be supplied with potable water at a pressure of at least 140 kPa.

(8)  The shower water system shall have one or more tempering devices capable of being adjusted to ensure that water supplied to shower heads does not exceed 40°C.

(9)  Floors in washrooms, shower areas and passageways used by bathers shall slope to waste drains at not less than 1% and shall be of hard surfaced materials that do not become slippery when wet.

(10)  Joints between floors and walls shall be coved in areas described in Sentence (9) and in dressing and locker rooms.

(11)  Hose bibs shall be provided in safe locations convenient for flushing down the walls and floors in washrooms, shower areas and passageways used by bathers.

(12)  Partitions or walls shall be provided to ensure privacy of dressing rooms, washrooms and shower areas.

(13)  The bottom of interior partitions in dressing rooms and washrooms shall be between 250 mm and 350 mm above the floor.

(14)  Dressing and locker room floors shall have non-slip surfaces that permit convenient and thorough cleaning and disinfecting.

3.11.10. Emergency Provisions for All Public Pools

3.11.10.1.  Lighting and Emergency Provisions

(1)  Except as provided in Sentences (2) and (3), rooms and spaces used by the public in conjunction with a public pool shall be capable of illumination to levels in compliance with Subsection 3.2.7.

(2)  Dressing rooms, locker rooms, shower rooms, washrooms and passageways shall have an illumination level of at least 200 lx at floor level.

(3)  An indoor pool or an outdoor pool that is intended to be open for use after sundown shall be equipped with a lighting system

(a)	that will maintain at any point on the pool deck and on the pool water surface an illumination level of at least,

(i)	200 lx in the case of an indoor pool, and

(ii)	100 lx in the case of an outdoor pool, and

(b)	that makes the underwater areas of the pool clearly visible from any point on the pool deck.

(4)  An outdoor pool that is intended to be open for use after sundown and an indoor pool shall be equipped with an independent emergency lighting system that automatically operates whenever the normal electrical power supply to a public pool lighting system fails.

(5)  The independent emergency lighting system required in Sentence (4) shall be capable of illuminating the pool deck, washroom, shower, locker areas, pool water surface and all means of egress to a level of at least 10 lx.

(6)  An emergency power supply for the emergency lighting system required in Sentence (4) shall comply with Sentences 3.2.7.4.(1) and 3.2.7.7.(1) and Article 3.2.7.5.

(7)  An emergency telephone directly connected to an emergency service or to the local telephone utility shall be installed adjacent to the pool deck of every Class A pool.

(8)  A telephone accessible for emergency use shall be installed for every Class B pool within 30 m of the pool.

(9)  Every wave action pool shall have a public address system which shall be clearly audible in all portions of the pool.

(10)  Every wave action pool shall have a communication system for the use of persons engaged in supervision or operation of the pool which shall be interconnected with each lifeguard control station, the first-aid room and the bather admission control centre.

(11)  The public address system and the communication system described in Sentences (9) and (10) shall be interconnected.

(12)  All recirculating pumps used in a public pool shall be capable of being deactivated by an emergency stop button clearly labelled and located at

(a)	a Class A pool beside the telephone that is required in Sentence (7), and

(b)	a Class B pool on the deck area.

(13)  The emergency stop button in Sentence (12) shall when used activate an audible and a visual signal located by the emergency stop.

(14)  An emergency sign containing the words IN THE EVENT OF AN EMERGENCY PUSH EMERGENCY STOP BUTTON AND USE EMERGENCY PHONE, AUDIBLE AND VISUAL SIGNAL WILL ACTIVATE shall be in letters at least 25 mm high with a 5 mm stroke and posted above the emergency stop button.

3.11.11. Service Rooms and Storage for all Public Pools

3.11.11.1.  Service Rooms and Storage Facilities

(1)  In addition to the requirements of this Subsection, service rooms shall comply with the requirements of Sentences 3.6.2.1.(4), 3.6.2.1.(5) and 3.6.2.2.(5) and Articles 3.5.3.3. and 3.6.2.3.

(2)  Where compressed chlorine gas is used as a pool water disinfectant, the cylinders or containers of gas shall be located in a service room that

(a)	except as provided in Sentences 3.1.9.4.(3) to (8), is separated from the remainder of the building by a 1 h fire separation that is substantially gas tight,

(b)	is designed for the sole purpose of containing all installed pressurized chlorine gas apparatus and piping and storing all chlorine gas containers or chlorine gas cylinders that are individually secured against toppling,

(c)	is located at or above ground level,

(d)	is provided with an exit door opening to the outdoors,

(e)	has screened openings to the outdoors with at least one opening located within 150 mm from the floor and at least one opening located within 150 mm from the ceiling, each opening being 2% of the area of the floor,

(f)	is equipped with emergency mechanical ventilation capable of producing at least 30 air changes per hour, taking suction at a maximum of 900 mm above the floor level and discharging at least 2 500 mm above ground level directly to the outdoors, and

(g)	contains a platform weigh scale of at least 135 kg capacity for each chlorine cylinder in use.

(3)  Storage facilities shall be provided for the safe storage of all chemicals required in pool operations.

(4)  The storage facilities shall be ventilated and shall be equipped with a water hose connection and a floor drain.

(5)  Service rooms and storage facilities, including rooms and facilities that contain electrical or mechanical equipment or chemicals or chemical feeders, shall be equipped with a secure locking device.

Section 3.12. Rapid Transit Stations

3.12.1. Scope and Definitions

3.12.1.1.  Scope

(1)  Except as provided in this Section the requirements in the Code apply to rapid transit stations.

3.12.1.2.  Definitions

(1)  In this Section

Ancillary space means the rooms or spaces in the station used only by the transit agency to house or contain operating, maintenance or support equipment and functions, but does not include booths and kiosks used by the transit agency or service rooms.

Central supervising station means the operations centre where the transit agency controls and co-ordinates the system-wide movement of passengers and vehicles and from which communication is maintained with supervisory and operating personnel of the transit agency and with participating agencies when required.

Crush load means the total of the seating capacity and the standing capacity of a car where

(a)	the seating capacity is the number of seats in a car, and

(b)	the standing capacity is 0.2 m2 per person for the standing area which is measured 300 mm in front of the seats.

Egress capacity means the number of people able to travel from or through a type of egress facility in a specified period of time.

Entraining load means the number of passengers boarding the train at a station.

Fare-paid area means that portion of a rapid transit station to which access is gained by a pass or by paying a fare.

Fare-paid area control means the point where passengers enter or leave the fare-paid area.

Link load means the number of passengers on board the train(s) travelling between two stations.

Maximum calculated train load means the crush load per car multiplied by the maximum number of cars per train in the peak period.

Peak direction means, for each route, the direction of train travel having the largest passenger flow volume based on the sum of the incoming link load plus the entraining load per peak hour.

Protected route means that portion of a means of egress which starts at the point where passengers would not be vulnerable to exposure from a train fire and which leads to the exterior of the station or through an exit to an adjacent building.

Public area means the public circulation areas in a rapid transit station providing pedestrian access to and from trains.

Rapid transit station means a building or part of a building used for the purpose of loading and unloading passengers of a rapid transit system but does not include open air shelters at street level.

Rapid transit system means an electrified transportation system, utilizing guidance methods involving positive mechanical contact with the fixed way operating on a right-of-way for the mass movement of passengers.

3.12.2. Construction Requirements

3.12.2.1.  Requirements for Stations

(1)  Except as provided in this Subsection, the requirements in Subsections 3.2.1. and 3.2.2. do not apply to a rapid transit station.

(2)  The requirements in Sentence (3) shall apply to

(a)	a rapid transit station erected entirely below the adjoining finished ground level, and

(b)	the underground portion of a rapid transit station.

(3)  Except as permitted in Sentence (4), an underground station or an underground portion of a station in Sentence (2) shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations having a fire-resistance rating not less than 2 h,

(b)	roof assemblies below ground level

(i)	shall have a fire-resistance rating not less than 2 h, or

(ii)	a fire-resistance rating is not required where steel tunnel liners are left in place to form part of the assembly and the tunnel liners are in direct contact with soil, and

(c)	all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(4)  An interior stair extending to street level is permitted to be protected by a combustible roof.

(5)  Where a rapid transit station is erected above and below the adjoining finished ground level, the above ground portion of the station shall be of noncombustible construction and shall conform to the requirements in Sentence (10).

(6)  Where a rapid transit station is erected entirely above the adjoining finished ground level and is a stand-alone building, the station shall be of noncombustible construction and shall conform to the requirements in Sentence (11).

(7)  Openings for stairways and escalators used by passengers are permitted to penetrate the fire separations required in Sentences (2) to (6).

(8)  Elevator shafts are permitted to penetrate the fire separations required in Sentences (2) to (6) provided they are enclosed by

(a)	a fire separation having a fire-resistance rating not less than 1 h, or

(b)	wired glass assemblies conforming to the Supplementary Guidelines.

(9)  Openings for other than stairways, escalators or elevators are permitted to penetrate the fire separations required in Sentences (2) to (6) provided the openings are protected by a closure having a fire-protection rating not less than 45 min.

(10)  The building shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(b)	mezzanines shall have a fire-resistance rating not less 1 h,

(c)	roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(11)  Except as provided in Sentence (12), the building shall be of noncombustible construction, and

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(12)  A building classified as Group A, Division 2 occupancy that is not more than 1 storey in building height, and in which the building area is not more than 3 200 m2 if not sprinklered, or 6 400 m2 if sprinklered, is permitted to be constructed with a roof of heavy timber construction and have columns of heavy timber construction.

3.12.3. Safety Requirements Within Stations

3.12.3.1.  Application

(1)  Except as provided in this Subsection and Subsection 3.12.4., the requirements in Subsections 3.3.1. and 3.6.2. apply to a rapid transit station.

(2)  A door in a fire separation is permitted to be equipped with pivot hinges in conformance with Table 2-8A of NFPA 80, “Fire Doors and Windows”.

(3)  The requirements in Subsection 3.4.4. for fire separation of exits do not apply in a rapid transit station.

(4)  Except as provided in Sentence (5), the requirements in Sentence 3.4.6.15.(1) for doors to be readily opened from the inside apply to required exit doors in a rapid transit station.

(5)  Where a group of two or more doors serves as a single exit facility, only one door in the group is required to comply with Sentence 3.4.6.15.(1).

(6)  A door which is required to be readily opened in Sentence (4) or (5) shall have a sign attached to it

(a)	displaying the words EMERGENCY EXIT with the letters not less than 25 mm high, and

(b)	visible from the exit approach.

3.12.3.2.  Booths and Kiosks

(1)  Booths and kiosks that are not more than 20 m2 in area and are used only by the transit agency for fare collection, dissemination of information or similar non-mercantile occupancies shall be of noncombustible construction and are not required to be separated from the remainder of the floor area by a fire separation.

(2)  Booths and kiosks that are more than 20 m2 in area and are used only by the transit agency for fare collection, dissemination of information or similar non-mercantile occupancies shall be

(a)	sprinklered, and

(b)	separated from the remainder of the floor area by a fire separation of noncombustible construction which is not required to have a fire-resistance rating.

(3)  A door acting as a closure in the fire separation in Sentence (2) is not required to be equipped with a self-closing device.

3.12.3.3.  Service Rooms and Ancillary Spaces

(1)  An ancillary space in a rapid transit station shall be separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 1 h.

(2)  Except as provided in Sentence (3), a door opening from a service room onto a means of egress in a rapid transit station shall be located not less than 5 m from an escalator balustrade and from the top and bottom riser of a flight of stairs used as a means of egress from the rapid transit station.

(3)  The requirements in Sentence (2) do not apply where

(a)	the service room is sprinklered, or

(b)	there is a vestibule between the service room and the means of egress.

(4)  Where a door from a service room opens onto a means of egress less than 5 m wide

(a)	the service room shall be sprinklered, or

(b)	there shall be a vestibule between the service room and the means of egress.

3.12.3.4.  Leased Areas

(1)  All leased areas within a rapid transit station shall be

(a)	sprinklered, and

(b)	separated from the remainder of the floor area by a fire separation of noncombustible construction which is not required to have a fire-resistance rating.

(2)  A door acting as a closure in the fire separation in Clause (1)(b) is not required to be equipped with a self-closing device.

(3)  Where leased areas are located on opposite sides of a means of egress, the width of the means of egress shall not be reduced to less than 5 m.

(4)  Except as provided in Sentence (5), where the leased area on any floor level exceeds 15% of the public area on that level, the public area shall be sprinklered.

(5)  In a rapid transit station which is erected entirely above the adjoining finished ground level and is a stand-alone building, where the leased area on any floor level exceeds 20% of the public area on that level, the public area shall be sprinklered.

(6)  In determining the leased area in Sentences (4) and (5), it is not necessary to include a leased area which is separated from the public area by a fire separation having a fire-resistance rating not less than

(a)	2 h where the leased area contains a mercantile or medium hazard industrial occupancy, or

(b)	1 h where the leased area contains any other occupancy.

(7)  A leased area is permitted on a platform level provided it is

(a)	located not less than 5 m from the platform edge,

(b)	located not less than 5 m from an egress facility, and

(c)	not located in a dead end portion of the platform.

3.12.3.5.  Vehicle Terminal

(1)  Where an enclosed terminal serves vehicles powered by combustible fuels, and the terminal has direct access to a rapid transit station

(a)	the terminal shall be sprinklered, and

(b)	the terminal shall be separated from the rapid transit station

(i)	by a fire separation having a fire-resistance rating not less than 1 h, or

(ii)	by wired glass assemblies conforming to the Supplementary Guidelines with wired glass doors equipped with self-closing devices.

(2)  Doors in the fire separation or in the wired glass assembly in Clause (1)(b) are not required to have latches where close spaced sprinkler protection is provided on the station side.

3.12.3.6.  Access to Adjacent Building

(1)  Where an access is provided between a rapid transit station and an adjacent building, the station and the building shall be separated by a fire separation having a fire-resistance rating not less than 2 h.

(2)  The access in Sentence (1) shall be through a vestibule which is separated from the station and from the building

(a)	by a fire separation having a fire-resistance rating not less than 1 h, or

(b)	by wired glass assemblies conforming to the Supplementary Guidelines with wired glass doors equipped with self-closing devices.

(3)  The vestibule doors in Sentence (2) are not required to be equipped with latches.

(4)  Close spaced sprinkler protection shall be provided on each side of all vestibule doors.

(5)  The vestibule shall not contain an occupancy.

(6)  Where an access is provided between a rapid transit station and an adjacent building, and the building is regulated by the provisions of Subsection 3.2.6. or 3.2.8., these provisions are not required in the rapid transit station.

3.12.3.7.  Emergency Lighting

(1)  Emergency lighting shall be provided to average levels not less than 10 lx at floor or tread level in public areas in a rapid transit station.

(2)  An emergency power supply conforming to Subsection 3.2.7. shall be provided to maintain the emergency lighting required in Sentence (1) for a period of 30 min after a power failure.

3.12.4. Means of Egress

3.12.4.1.  Occupant Load

(1)  The occupant load for public areas within a rapid transit station shall be

(a)	determined in conformance with this Subsection, and

(b)	based on peak hour patronage as projected for design of the transit system.

(2)  The platform occupant load for each platform in a rapid transit station shall be the greater of the a.m. or p.m. peak period loads calculated in accordance with Sentences (3) to (5).

(3)  The a.m. and the p.m. peak period occupant loads for each platform shall be based on the simultaneous evacuation of the entraining load and the link load for that platform.

(4)  The entraining load for each platform shall be the sum of the entraining loads for each track serving that platform and the entraining load for each track shall be based on the entraining load per train headway multiplied by

(a)	a factor of 1.3 to account for surges, and

(b)	in the peak direction for each route, an additional factor of 2 to account for a missed headway.

(5)  The link load for each platform shall be the sum of the link loads for each track serving that platform and, except as provided in Sentence (6), the link load for each track shall be based on the link load per train headway multiplied by

(a)	a factor of 1.3 to account for surges, and

(b)	in the peak direction for each route, an additional factor of 2 to account for a missed headway.

(6)  The maximum link load at each track shall be the maximum calculated train load.

3.12.4.2.  General Requirements

(1)  Except as provided in Sentence (2), escalators conforming to the requirements of Sentences 3.12.4.5.(3) and 3.12.4.6.(1) shall be acceptable as part of a required means of egress in a rapid transit station.

(2)  Escalators forming part of a required means of egress shall not comprise more than one-half of the required egress capacity from any one level.

(3)  Horizontal exits conforming to Sentence (4) may provide all of the required egress capacity from a rapid transit station.

(4)  Horizontal exits to any one building shall not comprise more than one half of the required egress capacity from any area within a rapid transit station.

(5)  A protected route shall be provided with emergency ventilation conforming to Subsection 3.12.7.

(6)  In an aboveground unenclosed station, the protected route is permitted to begin at the point of leaving the platform.

(7)  In an enclosed or underground station, the protection for the protected route shall consist of

(a)	a fire separation having a fire-resistance rating not less than 1 h,

(b)	construction having a fire-resistance rating not less than 1 h, or

(c)	wired glass assemblies conforming to the Supplementary Guidelines.

3.12.4.3.  Number and Location of Means of Egress

(1)  Each platform in a rapid transit station shall be served by not less than 2 means of egress which are independent of and remote from each other from the platform to the exterior of the station.

(2)  Where a continuous level walking surface is provided between two adjacent platforms, they may be considered as one platform for the purpose of conforming to this Subsection.

(3)  At the platform level, the distance separating the egress facilities in Sentences (1) and (2) shall be the greater of one car length or 25 m.

(4)  Except as required in Sentence (1), two or more means of egress are permitted to converge in conformance with Sentence 3.12.4.4.(6).

(5)  Means of egress from platforms shall be located so that the travel time from the most remote point on a platform to a protected route does not exceed 4 min based on travel speeds of

(a)	38 m/min for horizontal travel, and

(b)	21 m/min for vertical rise.

3.12.4.4.  Egress Capacity

(1)  For a rapid transit station, the required aggregate egress capacity from each platform shall be determined by dividing the platform occupant load determined in accordance with Sentences 3.12.4.1.(2) to (6) by the required platform clearance time determined in accordance with Sentence (3).

(2)  Where 2 platforms are considered as 1 platform as provided in Sentence 3.12.4.3.(2), the required egress capacity for each platform shall be determined separately.

(3)  The required platform clearance time shall be 4 min less the travel time between the platform and the entry into the protected route based on travel speeds of

(a)	38 m/min for horizontal travel, and

(b)	21 m/min for vertical rise.

(4)  For each means of egress, the required egress capacity at the platform shall be maintained for the entire length of the means of egress.

(5)  Except as provided in Sentence (6), where 2 or more means of egress converge, the required egress capacity beyond that point shall be cumulative.

(6)  The egress capacity in Sentence (5) need not be cumulative after converging where it can be shown that the platform clearance time in Sentence (3) is not exceeded.

3.12.4.5.  Width of Means of Egress

(1)  Except as otherwise required in this Subsection, the required width of means of egress serving platforms in a rapid transit station shall be determined based on

(a)	the required egress capacity determined in conformance with Article 3.12.4.4., and

(b)	the pedestrian flow rate for the type of means of egress facility listed in Table 3.12.4.5.

Table 3.12.4.5.

Pedestrian Flow Rates

Forming Part of Sentence 3.12.4.5.(1)

| Type of Egress Facility | Flow Rate, pedestrians per minute | Flow Rate, pedestrians per minute per metre width |
| --- | --- | --- |
| Platforms | N/A | 80 |
| Corridors | N/A | 80 |
| Doorways | N/A | 80 |
| Gates | N/A | 80 |
| Ramps not more than 4% | N/A | 80 |
| Ramps more than 4% | N/A | 55(1) |
| Stairs | N/A | 55(1) |
| Escalators moving in direction of egress travel, nominal width |  |  |
| : 1 200 mm | 100 | N/A |
| : 800 mm | 80 | N/A |
| : 600 mm | 60 | N/A |
| Turnstiles, height of bar |  |  |
| : not more than 900 mm | 45 | N/A |
| : more than 900 mm | 25 | N/A |
| Column 1 | 2 | 3 |

Note to Table 3.12.4.5.:

(1) Flow rate is applied vertically.

(2)  In calculating the required width of corridors and ramps with a grade of less than 4%, 300 mm at each sidewall shall be added to the width determined based on required egress capacity.

(3)  In calculating the required width of egress routes, one escalator at each level in a rapid transit station shall be deemed to be out of service and not available for egress purposes.

(4)  Except as provided in Sentence (5), the minimum width of means of egress facilities serving platforms shall be

(a)	1 750 mm for corridors and ramps,

(b)	1 750 mm for stairs,

(c)	430 mm for turnstiles,

(d)	500 mm for fare collection gates,

(e)	600 mm nominal width for escalators, and

(f)	900 mm for a door leaf.

(5)  A second means of egress as required by Sentence 3.12.4.3.(1) is permitted to be not less than 1 100 mm wide.

(6)  The minimum width of platforms shall be

(a)	3.2 m for side platforms, and

(b)	6.4 m for island platforms.

(7)  The minimum unobstructed width of platforms measured from the platform edge shall be 2.5 m.

3.12.4.6.  Egress Facilities

(1)  Escalators forming part of a required means of egress shall

(a)	where equipped to run reverse to the direction of egress travel, be capable of being stopped remotely and locally, and

(b)	have a vertical rise not more than 12 m between floors or landings.

(2)  Where electrically operated gates or turnstiles used for fare collection are intended to be used as part of a required means of egress from a rapid transit station, provision shall be made to release the gates or turnstiles in accordance with Sentence (4) to allow them to operate freely in the direction of egress travel.

(3)  Where locked doors which prevent entry into a fare-paid area are to be used as part of a required means of egress from a rapid transit station, provision shall be made to release the doors in accordance with Sentence (4) to allow them to operate freely in the direction of egress travel.

(4)  The release device required in Sentences (2) and (3) shall be installed as an ancillary device to the fire alarm system and shall release immediately

(a)	upon activation of the fire alarm signal,

(b)	in the event of a power failure or ground fault, or

(c)	upon actuation of a manually operated switch accessible to authorized personnel and located in

(i)	a fare collector’s booth or kiosk at the station, or

(ii)	the central supervising station.

(5)  After release, the gates or turnstiles in Sentence (2) or the doors in Sentence (3) shall be capable of reactivation only by manual actuation of the switch in Clause (4)(c).

3.12.5. Fire Safety Provisions

3.12.5.1.  Fire Alarm System

(1)  Except as provided in this Subsection, a fire alarm system conforming to Subsection 3.2.4. shall be installed in a rapid transit station.

3.12.5.2.  Exceptions

(1)  Manual pull stations need not be installed in a rapid transit station.

(2)  Audible signal appliances need not be installed in a rapid transit station.

3.12.5.3.  Fire Detectors

(1)  Except where the area is sprinklered, fire detectors shall be installed in every service room, ancillary space, leased space, booth and kiosk.

3.12.5.4.  Central Supervising Station

(1)  Each rapid transit station shall be monitored by a central supervising station equipped in accordance with the provisions of Chapter 9 of NFPA-72, “Standard for the Installation, Maintenance and Use of Protective Signaling Systems”.

3.12.5.5.  Annunciators

(1)  An annunciator shall be installed

(a)	in a location that is readily accessible to firefighters entering the building, and

(b)	in the rapid transit station

(i)	in a designated collector’s booth, or

(ii)	within viewing distance of a designated collector’s booth.

3.12.5.6.  Annunciator Indication

(1)  All fire alarm, fire detectors, valve switches and water flow indicator signals when activated in a rapid transit station shall be indicated on the annunciator at the station.

(2)  The annunciator at a rapid transit station shall be monitored simultaneously at the central supervising station.

(3)  Where a means of egress from a rapid transit station leads through an adjoining building, any alarm signal originating in the building within two storeys above a connection to the station shall

(a)	be indicated on the rapid transit station annunciator, and

(b)	cause a message to flash a warning on a sign located in conformance with Sentence (4), that the means of egress shall not be used as an exit from the station.

(4)  A sign required in Clause (3)(b) shall be located

(a)	at the doors from the rapid transit station to the adjoining building, and

(b)	in the means of egress to the adjoining building, at the last point where there is a choice of direction to travel to not less than one other exit.

3.12.5.7.  Emergency Power

(1)  An emergency power supply conforming to Article 3.2.7.8. shall be provided for the fire alarm system.

3.12.5.8.  Communication Systems

(1)  In a rapid transit station, a public address system shall be installed and shall include loudspeakers which

(a)	can be operated from the central supervising station,

(b)	can be operated from the rapid transit station in which they are located, and

(c)	designed and located so that voice messages can be heard intelligibly throughout the public area in a rapid transit station.

(2)  A 2-way communication system shall be installed in each rapid transit station with telephones located at

(a)	the collector’s booth, and

(b)	at each end of each platform.

(3)  The telephones in Sentence (2) shall be provided with connections to the central supervising station.

3.12.5.9.  Emergency Reporting Devices

(1)  Emergency reporting devices shall be located on passenger platforms and throughout a rapid transit station such that the distance of travel from any point in the public area to such a device is not more than 90 m.

(2)  The emergency reporting devices required in Sentence (1) are permitted to be public telephones with an emergency no charge capability and their location shall be plainly indicated by appropriate signs.

3.12.5.10.  Sprinkler Systems

(1)  Sprinkler systems shall conform with the requirements of Articles 3.2.5.13 to 3.2.5.16.

(2)  In addition to the requirements of Subsection 3.12.3. the steel truss enclosure of an escalator shall be sprinklered.

(3)  There shall be identification on a fire department connection for a sprinkler system in a rapid transit station to indicate that the connection is part of the station system.

3.12.5.11.  Standpipe and Hose Systems

(1)  A standpipe and hose system conforming to the requirements of Subsection 3.2.9. shall be installed in a rapid transit station, except as otherwise required or permitted in this Article.

(2)  Where a rapid transit station includes more than one standpipe riser there shall be a cross-connection pipe having a diameter not less than 100 mm between each standpipe riser so that supplying of water through any fire department connection will furnish water throughout each riser.

(3)  There shall be identification on a fire department connection for a standpipe system in a rapid transit station to indicate that the connection is part of the station system.

(4)  Hose stations shall be located so that every portion of the rapid transit station can be reached by a hose stream and is within 3 m of a hose nozzle when the hose is extended.

(5)  In addition to the requirements in Sentence (4), hose stations shall be located in each tunnel not more than 20 m from the end of the platform.

(6)  The requirement for hose rack and fire hose in Sentence 3.2.9.3.(2) does not apply in a rapid transit station.

(7)  Each hose station shall have a 38 mm hose connection and a 65 mm hose connection.

(8)  All supply piping shall have a diameter not less than 100 mm.

3.12.6. Required Sanitary Facilities

3.12.6.1.  Application

(1)  Except as provided in this Subsection, Subsection 3.7.4. applies to a rapid transit station.

3.12.6.2.  Washrooms Required

(1)  Except as provided in Sentences (2) and (3), a washroom for each sex, containing not less than 1 water closet and 1 lavatory, shall be provided in each rapid transit station for use by employees.

(2)  Where the number of employees in a rapid transit station is not more than 5, a washroom containing 1 water closet and 1 lavatory is permitted to be used by both sexes provided the door to the room can be locked from the inside.

(3)  Where a rapid transit station is not staffed during operating hours, a washroom is not required in the station.

(4)  In each rapid transit station located at the end of a line, a washroom for each sex, containing not less than 3 water closets and 2 lavatories, shall be provided for use by the public.

3.12.7. Emergency Ventilation

3.12.7.1.  Application

(1)  Every rapid transit station shall be provided with an emergency ventilation system conforming to NFPA 130, “Fixed Guideway Transit Systems”.

3.12.8. Barrier-Free Design

3.12.8.1.  Application

(1)  Except as provided in this Subsection, the requirements in Section 3.8. apply to rapid transit stations.

(2)  Not less than one barrier-free path of travel shall be provided from an entrance described in Article 3.8.1.2.

(a)	into the fare-paid area, and

(b)	to each platform.

3.12.8.2.  Exception

(1)  Where an elevator is used to comply with the requirements of Article 3.3.1.7., the provisions of Clause 3.3.1.7.(1)(a) do not apply where the elevator system complies with Article 3.12.8.3.

3.12.8.3.  Elevator Requirements

(1)  Except as provided in Sentence (2), the elevator in Article 3.12.8.2. shall be capable of providing transportation from each platform to an entrance described in Article 3.8.1.2.

(2)  Where it is necessary to change elevators to reach the entrance described in Sentence (1), the elevator system shall be designed so that not more than one change of elevator is required between

(a)	a platform and a fare-paid area control, and

(b)	the fare-paid area control and the entrance.

3.12.8.4.  Emergency Operation of Elevators

(1)  Manual emergency recall operation shall be provided for all elevators.

(2)  Key-operated switches for emergency recall described in Sentence (1) shall be provided and shall be located on the outside of each elevator shaft at the level of the fare-paid area control.

(3)  In-car emergency service switches shall be provided in all elevator cars.

(4)  Keys to operate the switches required in Sentences (2) and (3) shall be located at

(a)	the annunciator required in Clause 3.12.5.5.(1)(a), and

(b)	the collector’s booth designated in Clause 3.12.5.5.(1)(b).

3.12.8.5.  Washrooms Required to be Barrier-Free

(1)  A barrier-free path of travel shall be provided to the washrooms required in Article 3.12.6.2.

(2)  Where a washroom required in Sentence 3.12.6.2.(1) contains only 1 water closet and 1 lavatory, the washroom shall be designed in conformance with the requirements in Article 3.8.3.12.

(3)  Where a washroom required in Sentence 3.12.6.2.(1) contains more than 1 water closet, the washroom shall be designed in conformance with the requirements in Articles 3.8.3.8. to 3.8.3.11.

(4)  The washroom required in Sentence 3.12.6.2.(2) shall be designed in conformance with the requirements in Article 3.8.3.12.

(5)  The washrooms required in Sentence 3.12.6.2.(4) shall be designed in conformance with the requirements in Articles 3.8.3.8. to 3.8.3.11.

Section 3.13. Tents and Air-Supported Structures

3.13.1. Tents

3.13.1.1.  Application

(1)  Except as provided in this Subsection, tents are exempted from complying with the requirements of this Code.

3.13.1.2.  General

(1)  Except as provided in Sentence (2), the requirements of this Subsection shall apply to all tents.

(2)  Articles 3.13.1.4., 3.13.1.5., 3.13.1.6. and 3.13.1.10. apply to tents that

(a)	do not exceed 225 m2 in ground area,

(b)	do not exceed 225 m2 in aggregate ground area and are closer than 3 m apart,

(c)	do not contain bleachers, and

(d)	are not enclosed with sidewalls.

3.13.1.3.  Means of Egress

(1)  Except as provided in Sentences (2) and (3), tents shall conform to Sections 3.3. and 3.4.

(2)  A tent need not conform to Article 3.4.6.11. except where swing type doors are provided.

(3)  Where the area between adjacent tents or a tent and the property line is used as a means of egress, the minimum width between stake lines shall be the width necessary for means of egress, but not less than 3 m.

3.13.1.4.  Clearance to Other Structures

(1)  Tents shall not be erected closer than 3 m to the property line.

(2)  Except as provided in Sentences (3), (4) and (5), tents shall not be erected closer than 3 m to other tents or structures on the same property.

(3)  A walkway between a building and a tent occupied by the public is permitted provided

(a)	the tent is not closer than 3 m from the building, and

(b)	the walkway conforms to Article 3.1.3.18.

(4)  Tents not occupied by the public need not be separated from one another, and are permitted to be erected less than 3 m from other structures on the same property, where such closer spacing does not create a hazard to the public.

(5)  Tents located on fair grounds or similar open spaces, need not be separated from one another provided such closer spacing does not create a hazard to the public.

3.13.1.5.  Clearances to Flammable Material

(1)  The ground enclosed by a tent and for not less than 3 m outside of such structure shall be cleared of all flammable or combustible material or vegetation that will carry fire.

3.13.1.6.  Flame Resistance

(1)  Every tent, and tarpaulins, decorative materials, fabrics and films used in connection with tents, shall be certified to CAN/ULC S-109-M, “Standard for Flame Tests of Flame-Resistant Fabrics and Films”, or NFPA 701 “Standard Method of Fire Tests for Flame-Resistant Textiles and Films”.

3.13.1.7.  Design of Framing and Supports

(1)  The supporting framing structure and anchorage system for tents shall be designed and reviewed by a professional engineer.

3.13.1.8.  Bleachers

(1)  Where bleachers are provided in tents, they shall be designed in conformance with Articles 3.3.2.8., 3.3.2.10., 4.1.6.11., and 4.1.10.6.

3.13.1.9.  Sanitary Facilities

(1)  Except as provided in Sentence (3), the minimum number of water closets for tents shall be determined in accordance with Table 3.7.4.3.E.

(2)  Article 3.7.4.16. applies to sanitary facilities in Sentence (1).

(3)  Sanitary privies, chemical closets or other means for the disposal of human waste may be provided in lieu of toilet fixtures.

3.13.1.10.  Provision for Fire-fighting

(1)  Access shall be provided to all tents for the purpose of fire-fighting.

3.13.2. Air-Supported Structures

3.13.2.1.  Application

(1)  Except as provided in this Subsection, the requirements of the Code apply to air-supported structures.

3.13.2.2.  General

(1)  Air-supported structures shall not be used for Groups B, C, or Group F, Division 1 major occupancies or for classrooms.

(2)  Except where no fire separation is required between major occupancies, air-supported structures shall contain not more than one major occupancy.

(3)  Except as provided in Sentence (5), air-supported structures are exempt from complying with Articles 3.2.2.20. to 3.2.2.83., except for maximum building size.

(4)  Air-supported structures may be designed with interior walls, mezzanines, or similar construction.

(5)  Interior construction contained within air-supported structures must meet the construction requirements of Articles 3.2.2.20. to 3.2.2.83.

3.13.2.3.  Spatial Separation

(1)  Except as provided in Sentences (2), (3) and (4), air-supported structures shall not be erected closer than 3 m to other structures on the same property or to the property line.

(2)  Air-supported structures not occupied by the public need not be separated from one another, and are permitted to be erected closer than 3 m from other structures on the same property where such closer spacing does not create a hazard to the building occupants or the public.

(3)  Except as provided in Sentence (4), an air-supported structure is permitted to be attached to another building provided the building to which it is attached

(a)	conforms to the requirements of other Parts of the Code based on the total building areas of the air-supported structure and the attached building,

(b)	is sprinklered, and

(c)	is separated from the air-supported structure by a fire separation having a fire-resistance rating of not less than 1 h.

(4)  An air-supported structure is permitted to be attached to another building provided the building to which it is attached

(a)	has a building area not more than 200 m2,

(b)	conforms to the requirements of other Parts of the Code based on the building area of the attached building, and

(c)	is sprinklered or separated from the air-supported structure by a fire separation having a fire-resistance rating of not less than 1 h.

3.13.2.4.  Clearances to Flammable Material

(1)  The ground enclosed by an air-supported structure and for not less than 3 m outside of such structure shall be clear of all flammable or combustible material or vegetation that will carry fire.

3.13.2.5.  Flame Resistance

(1)  Air-supported structures shall be constructed of material conforming to CAN/ULC S-109-M, “Standard for Flame Tests of Flame-Resistant Fabrics and Films”, or NFPA 701, “Standard Method of Fire Tests for Flame-Resistant Textiles and Films”.

(2)  Materials for fabrics used in connection with air-supported structures are exempt from compliance with the requirements for flame-spread ratings for interior finishes in Subsection 3.1.13.

3.13.2.6.  Emergency Air Supply

(1)  An air-supported structure designed for an assembly occupancy with an occupant load of more than 200 persons shall have either an automatic emergency engine-generator set capable of powering one blower continuously for 4 h, or a supplementary blower powered by an automatic internal combustion engine.

Section 3.14. Signs

3.14.1. Scope

3.14.1.1.  Application

(1)  Except as provided otherwise in Article 3.14.1.2. this Section shall apply to the erection of all signs.

3.14.1.2.  Exceptions

(1)  The following signs shall not be subject to the provisions of this Section

(a)	signs for regulating traffic or similar devices, legal notices or warnings at railroad crossings,

(b)	signs in display windows including writing, representation, painting or lettering directly on the surface of any window or door, or other signs not affixed to the building interior,

(c)	small signs displayed for the direction of the public including signs which identify rest rooms, freight entrances and such other similar directional signs,

(d)	signs painted directly on a building, and

(e)	incidental signs or other signs subject to municipal approval.

3.14.2. Alterations

3.14.2.1.  Exceptions for Alterations

(1)  The changing of movable parts of signs that are designed for changes, or the repainting of display matter shall not be deemed to be alterations.

3.14.3. Structural Requirements

3.14.3.1.  Structural Design

(1)  Except as provided herein, all sign structures shall be designed in accordance with Part 4.

3.14.3.2.  Professional Design

(1)  A sign structure shall be designed by an architect or professional engineer where it is

(a)	a ground sign which exceeds 7.5 m in height above the adjacent finished ground,

(b)	a projecting sign which weighs more than 115 kg, or

(c)	a roof sign that has any face that is more than 10 m2.

(2)  A projecting sign shall not be attached or fastened in any manner to a parapet wall unless designed by an architect or professional engineer.

3.14.4. Plastic Sign Facing Materials

3.14.4.1.  Combustible Sign Faces

(1)  Plastic materials used in the construction of sign faces shall

(a)	have an average burning rate not greater than 65 mm/min in sheets 1.5 mm thick when tested in accordance with ASTM D635, “Rate of Burning and/or Extent and Time of Burning of Self-supporting Plastics in a Horizontal Position”,

(b)	have an average burning rate not greater than 140 mm/min when tested in accordance with ASTM D568, “Rate of Burning and/or Extent and Time of Burning of Flexible Plastics in a Vertical Position”, and

(c)	have a measurement of material thickness in accordance with Method B-Machinists’ Micrometer Without Ratchet of ASTM D374, “Thickness of Solid Electrical Insulation”.

(2)  Except as provided in Sentence (3), where the exterior cladding of a wall is required to be noncombustible, a plastic sign face or a group of contiguous plastic sign faces may be placed over such cladding provided each such sign face or group of contiguous sign faces

(a)	does not exceed 30% of the wall area of the storey on which it is installed,

(b)	does not exceed 15 m2 in area or 1 200 mm in height at each storey, and

(c)	when located above the first storey, is vertically separated from other plastic sign faces by 1 200 mm of noncombustible construction unless separated by a horizontal noncombustible projection such as a canopy, extending the full width of, and projecting at least 900 mm beyond the exterior sign face.

(3)  Where a plastic exterior sign is mounted as a face on a metal sign box that is at least 200 mm in depth, the requirements of Sentence (2) need not apply provided the sign box is mounted on a noncombustible exterior wall.

(4)  Notwithstanding the requirements of Sentence (5), the plastic portion of an interior sign placed over or forming part of an interior wall surface in corridors, covered or enclosed walkways at or above grade in buildings shall

(a)	not exceed 15% of the wall area in, or over which it may be installed,

(b)	be supported by a device that will not detrimentally affect the fire-resistance rating of the interior wall to which it is attached or of which it may form a part, and encase the edges of the plastic sign face in metal,

(c)	not be positioned or sized in such a manner that it is less than 600 mm from the vertical line separating two adjacent premises,

(d)	be placed so that there is at least 600 mm vertical separation of noncombustible material between the top of the plastic sign surface and the ceiling surface,

(e)	be permitted to have an increase of 100% in area required in Clause (a) and a decrease of 50% of the separation distances required in Clauses (c) and (d) if the area is sprinklered, and

(f)	not have a flame-spreading rating above 250.

(5)  Signs in exits and underground walkways shall have a flame-spread rating not more than 25.

3.14.5. Location Restrictions

3.14.5.1.  Obstructions not Permitted

(1)  No sign shall be located so as to obstruct openings required for light and ventilation, any required means of egress or required access for fire-fighting in accordance with Sentence 3.2.5.4.(2).

3.14.5.2.  Clearance for Exterior Signs

(1)  No exterior sign shall be erected overhanging a sidewalk or other pedestrian walkway unless the vertical distance, measured from the bottom of the overhanging portion of the sign to the surface of the sidewalk, is at least 2 400 mm.

(2)  Except as provided hereinafter, no sign face shall be erected within 600 mm of the vehicular travelled portion of a private lane or roadway, or of a motor vehicle parking area unless the minimum vertical distance between grade and the bottom of the overhanging sign face is at least 4.25 m.

(3)  Where the height of all vehicles using any private road or parking area is permanently restricted, the vertical distance in Sentence (2) may be reduced to the amount of the actual height restriction, for as long as the said height restriction is in existence on the premises.

Section 3.15. Additional Requirements for Change of Use

3.15.1. Scope

3.15.1.1.  Application

(1)  This Section applies where proposed construction in respect of an existing building will result in the following changes of use of all or part of the building

(a)	a change of the major occupancy of all or part of a building that is designated with a “Y” in Table 2.4.1.1.,

(b)	a suite of a Group C major occupancy is converted into more than one suite of Group C major occupancy,

(c)	a farm building or part of a farm building is changed to a major occupancy, or

(d)	the use of a building or part of a building is changed and the previous major occupancy of the building or part of the building cannot be determined.

(2)  For the purposes of this Section and Sentences 11.4.2.1(1) and 11.4.2.5.(4), the changes of use set out in Clauses (1)(b) to (d) shall also be deemed to constitute a change in major occupancy.

(3)  The requirements of this Section are in addition to the requirements of other Parts of the Code as they apply to the proposed construction.

3.15.2. Additional Construction

3.15.2.1.  Change of Use and Compensating Construction

(1)  Where proposed construction will result in a change of use described in Clauses 3.15.1.1.(1)(a) to (d), additional construction shall be required in order that the building or part of a building subject to the change of use conforms to the requirements of Subsection 3.2.6. and Sections 3.7., 3.11. and 3.11A. as they apply to the new major occupancy that the building or part of a building is to support.

(2)  For the purposes of this Article, existing buildings shall be classified as to their construction and occupancy as provided for in Sentence 11.2.1.1.(1).

3.15.2.2.  Performance Level and Compensating Construction

(1)  The performance level of a building after construction shall not be less than the performance level of the building prior to construction.

(2)  For the purposes of Sentence (1), reduction of performance level shall be determined in accordance with Articles 11.4.2.1, 11.4.2.3. and 11.4.2.5.

(3)  Where the proposed construction would reduce the performance level of an existing building, compensating construction shall be required in conformance with Articles 11.4.3.1., 11.4.3.2, 11.4.3.4. and 11.4.3.6.

(4)  Section 11.5. applies in respect of the requirements of Sentences 11.4.3.4.(1), (3) and (4).

O. Reg. 403/97, Part 3; O. Reg. 22/98, ss. 10-16; O. Reg. 102/98, ss. 1, 2; O. Reg. 152/99, ss. 1, 2; O. Reg. 278/99, ss. 3, 4; O. Reg. 593/99, ss. 2, 3; O. Reg. 205/00, ss. 3, 4; O. Reg. 220/02, ss. 4-7; O. Reg. 23/04, ss. 1, 2; O. Reg. 349/06, ss. 4-12.

Part 4
Structural Design

| Section | 4.1. | Structural Loads and Procedures |
| --- | --- | --- |
|  | 4.1.1. | General |
|  | 4.1.2. | Specified Loads and Effects |
|  | 4.1.3. | Limit States Design |
|  | 4.1.4. | Working Stress Design |
|  | 4.1.5. | Dead Loads |
|  | 4.1.6. | Live Loads Due to Use and Occupancy |
|  | 4.1.7. | Live Loads Due to Snow, Ice and Rain |
|  | 4.1.8. | Live Loads Due to Wind |
|  | 4.1.9. | Live Loads Due to Earthquakes |
|  | 4.1.10. | Other Effects |
| Section | 4.2. | Foundations |
|  | 4.2.1. | General |
|  | 4.2.2. | Subsurface Investigations and Reviews |
|  | 4.2.3. | Materials Used in Foundations |
|  | 4.2.4. | Design Requirements |
|  | 4.2.5. | Excavations |
|  | 4.2.6. | Shallow Foundations |
|  | 4.2.7. | Deep Foundations |
|  | 4.2.8. | Special Foundations |
| Section | 4.3. | Design Requirements for Structural Materials |
|  | 4.3.1. | Wood |
|  | 4.3.2. | Plain and Reinforced Masonry |
|  | 4.3.3. | Plain, Reinforced and Prestressed Concrete |
|  | 4.3.4. | Steel |
|  | 4.3.5. | Aluminum |
|  | 4.3.6. | Glass |
| Section | 4.4. | Design Requirements for Special Structures |
|  | 4.4.1. | Air-Supported Structures |
|  | 4.4.2. | Parking Structures |
|  | 4.4.3. | Guards Over Retaining Walls |

Part 4
Structural Design

Section 4.1. Structural Loads and Procedures

4.1.1. General

4.1.1.1.  Scope

(1)  The scope of this Part shall be as described in Section 2.1.

4.1.1.2.  Definitions

(1)  Reserved

4.1.1.3.  Design Requirements

(1)  Buildings and their structural members including formwork and falsework shall be designed to have sufficient structural capacity and structural integrity to resist safely and effectively all loads and effects of loads and influences that may reasonably be expected, having regard to the expected service life of buildings, and shall in any case satisfy the requirements of this Section.

(2)  All permanent and temporary structural members, including formwork and falsework of a building, shall be protected against loads exceeding the specified loads during the construction period except when, as verified by analysis or test, temporary overloading of a structural member would result in no impairment of that member or any other member.

(3)  Reserved

(4)  Precautions shall be taken during all stages of construction to ensure that the building is not damaged or distorted due to loads applied during construction.

4.1.1.4.  Design Basis

(1)  Buildings and their structural members shall be designed by one of the following methods:

(a)	standard design procedures and practices provided by this Part and any standards and specifications referred to therein, except in cases of conflict the provisions of the building code shall govern, or

(b)	one of the following three bases of design:

(i)	analysis based on generally established theory,

(ii)	evaluation of a given full-scale structure or a prototype by a loading test,

(iii)	studies of model analogues,

provided the design is carried out by a person qualified in the specific method applied and provided the design ensures a level of safety and performance at least equivalent to that provided for or implicit in design carried out by the methods referred to in Clause (a).

(2)  Communications towers, dish antennas and their supporting structures shall conform to CAN/CSA-S37-M, “Antennas, Towers, and Antenna Supporting Structures”.

4.1.1.5.  Deflections

(1)  In proportioning structural members to limit deflection, consideration shall be given to

(a)	the intended use of the building or member,

(b)	limiting damage to non-structural members and materials whose physical properties are known at the time of the design,

(c)	limiting damage to the structure itself, and

(d)	creep, shrinkage and temperature.

(2)  Sway effects produced by vertical loads acting on the structure in its displaced configuration shall be taken into account in the design of buildings and their structural members.

(3)  The lateral deflection of buildings due to design wind and gravity loads shall be checked to ensure that nonstructural elements whose nature is known at the time the structural design is carried out will not be damaged.

(4)  Except as provided in Sentence (5), the total drift per storey under specified wind and gravity loads shall not exceed 1/500 of the storey height unless other drift limits are specified in the design standards referenced in Section 4.3.

(5)  The deflection limits required in Sentence (4) do not apply to industrial buildings or sheds if it is known by experience that greater movement will have no significantly adverse effect on the strength and function of the building.

4.1.1.6.  Vibrations

(1)  Floor systems susceptible to vibrations shall be designed so that there will be no significantly adverse effects on the intended occupancy of the building from vibrations.

(2)  Unusually flexible buildings and buildings whose ratio of height to minimum effective width exceeds 4 to 1 shall be designed so that there will be no significant adverse effects on the intended occupancy of the building from vibrations under dynamic wind load.

4.1.1.7.  Stability

(1)  Provision shall be made to ensure adequate stability of a structure as a whole, and adequate lateral, torsional and local stability of all structural parts.

4.1.1.8.  Reserved

4.1.2. Specified Loads and Effects

4.1.2.1.  Loads, Forces and Effects

(1)  Except as provided for in Article 4.1.2.2., the following specified loads, forces and effects shall be considered in the design of a building and its structural members and connections:

D -	dead loads as provided for in Subsection 4.1.5.,

E -	live load due to earthquake as specified in Subsection 4.1.9.,

L -	live load due to static or inertia forces arising from intended use and occupancy (includes vertical loads due to cranes); snow, ice and rain; earth and hydrostatic pressure,

T -	effects due to contraction or expansion caused by temperature changes, shrinkage, moisture changes, creep in component materials, movement due to differential settlement or combination thereof,

W -	live load due to wind as specified in Subsection 4.1.8.

(2)  Minimum specified values of these loads, as set forth in Subsections 4.1.5. to 4.1.10., shall be increased to account for dynamic effects where applicable.

4.1.2.2.  Loads Not Listed

(1)  Where a building or structural member can be expected to be subjected to loads, forces or other effects not listed in Article 4.1.2.1., such effects shall be taken into account in the design based on the most appropriate information available.

(2)  If it can be shown by engineering principles, or if it is known from experience, that neglect of some or all of the effects due to T do not affect the structural safety and serviceability, they need not be considered in the calculations.

4.1.2.3.  Structural Design

(1)  Structural design shall be carried out in accordance with Subsection 4.1.4., Working Stress Design or Subsection 4.1.3., Limit States Design.

4.1.3. Limit States Design

4.1.3.1.  Definitions

(1)  In this Subsection, the term

(a)	limit states means those conditions of a building structure in which the building ceases to fulfil the function for which it was designed,

(Those states concerning safety are called ultimate limit states and include exceeding the load carrying capacity, overturning, sliding, fracture and fatigue, while those states which restrict the intended use and occupancy of the building are called serviceability limit states, and include deflection, vibration, permanent deformation and cracking.)

(b)	specified loads (D, E, L, T and W) mean those loads defined in Article 4.1.2.1. and given in this Section,

(c)	load factor, , means a factor in Sentence 4.1.3.2.(4) applied to a specified load which, for the limit states under consideration, takes into account the variability of the loads and load patterns and analysis of their effects,

(d)	factored load means the product of a specified load and its load factor,

(e)	load combination factor, , means a factor in Sentences 4.1.3.2.(5) and (6) applied to the factored loads other than dead load to take into account the reduced probability of a number of loads from different sources acting simultaneously,

(f)	importance factor, , means a factor in Sentence 4.1.3.2.(7) applied to the factored loads other than dead load to take into account the consequences of collapse as related to the use and occupancy of the building,

(g)	resistance, R, of a member, connection, structure or foundation, is based on the dimensions and on the specified properties of the structural materials,

(h)	resistance factor, , means a factor applied to a specified material property or to the resistance of a member, connection, structure or foundation, which for the limit state under consideration takes into account the variability of dimensions and material properties, workmanship, type of failure and uncertainty in the prediction of resistance, and

(i)	factored resistance means the product of resistance and the applicable resistance factor.

4.1.3.2.  Safety Check for Strength and Stability

(1)  A building and its structural components shall be designed to have sufficient strength and stability so that the factored resistance is greater than or equal to the effect of factored loads, as required in Sentences (3) or (8).

(2)  In cases of overturning, uplift and sliding, anchorage is required if the effect of loads tending to cause overturning, uplift or sliding, multiplied by load factors greater than 1.0 given in Sentence (4), is greater than the stabilizing effect of dead load multiplied by a load factor of 0.85 as given in Sentence (4).

(3)  For load combinations not including earthquake, the effect of factored loads is the structural effect due to the specified loads multiplied by load factors, , in Sentence (4), a load combination factor, , in Sentences (5) and (6) and an importance factor, , in Sentence (7), and the factored load combinations shall be taken as

αDD + γψ [αLL + αWW + αTT]

(4)  The load factors, , shall be equal to

(a)	D = 1.25, except that when the dead load resists overturning, uplift or reversal of load effect, D = 0.85,

(b)	L = 1.5,

(c)	W = 1.5, and

(d)	T = 1.25.

(5)  The load combination factor, , shall be equal to

(a)	1.0 when only 1 of the loads L, W and T in Sentence 4.1.2.1.(1) acts,

(b)	0.70 when 2 of the loads L, W and T in Sentence 4.1.2.1.(1) act, and

(c)	0.60 when all of the loads L, W and T in Sentence 4.1.2.1.(1) act.

(6)  The most unfavourable effect shall be determined by considering the loads L, W and T in Sentence 4.1.2.1.(1) acting alone with  = 1.0 or in combination with  = 0.70 or 0.60.

(7)  The importance factor, , shall be not less than 1.0 for all buildings, except that for buildings where it can be shown that collapse is not likely to cause injury or other serious consequences, it shall be not less than 0.8.

(8)  For load combinations including earthquake, the factored load combinations shall be taken as

(a)	1.0D + (1.0E) and either,

(b)	1.0D + (1.0L + 1.0E) for storage and assembly occupancies, or

(c)	1.0D + (0.5L + 1.0E) for all other occupancies.

4.1.3.3.  Serviceability and Fatigue

(1)  A building and its structural components shall be checked for serviceability limit states as defined in Clause 4.1.4.1.(1)(a) and fatigue under the effect of the specified loads as required in the standards described in Section 4.3.

(2)  Where more than one load contributes to the stress in a member, the combination of loads shall be assumed to be

D+ ψ[L+ W+ T]

where  is in conformance with Sentences 4.1.3.2.(5) and (6).

4.1.4. Working Stress Design

4.1.4.1.  Load Combinations

(1)  In designing buildings and their structural members, all of the loads listed in Article 4.1.2.1. shall be considered to act in the following combinations, whichever combination produces the most unfavourable effects in the building, foundation or structural member concerned, when appropriately reduced according to Article 4.1.4.2.

(a)	D

(b)	D + L

(c)	D + (W or 2/3E)

(d)	D + T

(e)	D + L + (W or 2/3E)

(f)	D + L + T

(g)	D + (W or 2/3E) + T

(h)	D + L + (W or 2/3E) + T

4.1.4.2.  Load Combination Factors

(1)  The total of the combined load effects may be multiplied by the following load combination factors:

(a)	1.0 for the combinations in Clauses 4.1.4.1.(1)(a) to (d),

(b)	0.75 for the combinations in Clauses 4.1.4.1.(1)(e) to (g), and

(c)	0.66 for the combination in Clause 4.1.4.1.(1)(h).

4.1.4.3.  Stress Reversal

(1)  When loads other than D counteract D in a structural member or joint, special caution shall be exercised by the designer to ensure adequate safety for possible stress reversal.

4.1.4.4.  Overturning and Sliding

(1)  A building shall be proportioned to resist an overturning moment and sliding force of not less than twice that due to the loads acting on the structure when the structure is considered as an entire unit acting on or anchored to its bearing stratum or supporting structure.

(2)  The resistance to overturning shall be calculated as the sum of the stabilizing moment of the dead load only, plus the ultimate resistance of any anchoring devices.

4.1.5. Dead Loads

4.1.5.1.  Dead Loads

(1)  The specified dead load for a structural member consists of

(a)	the weight of the member itself,

(b)	the weight of all materials of construction incorporated into the building to be supported permanently by the member,

(c)	the weight of partitions,

(d)	the weight of permanent equipment, and

(e)	forces due to prestressing.

(2)  Except as provided in Sentence (5), in areas of a building where partitions other than permanent partitions are shown on the drawings, or where partitions might be added in the future, allowance shall be made for the weight of such partitions.

(3)  The partition weight allowance in Sentence (2) shall be determined from the actual or anticipated weight of the partitions placed in any probable position, but shall be not less than 1 kPa over the area of floor being considered.

(4)  Partition loads used in design shall be shown on the drawings in sufficient detail to enable the loads due to materials of construction incorporated in the building to be determined.

(5)  In cases where the dead load is counteractive, the load allowances as provided in Sentences (2) and (3) shall not be included in the design calculations.

4.1.6. Live Loads Due to Use and Occupancy

4.1.6.1.  Loads Due to Use of Floors and Roofs

(1)  The specified live load on an area of floor or roof depends on the intended use and occupancy, and shall not be less than the uniformly distributed load patterns in Article 4.1.6.3., the loads resulting from the intended use or the concentrated loads in Article 4.1.6.10., whichever produces the most critical effect.

4.1.6.2.  Uses Not Stipulated

(1)  Where the use of an area of floor or roof is not provided for in Article 4.1.6.3., the specified live loads due to the use and occupancy of the area shall be determined from an analysis of the loads resulting from

(a)	the weight of the probable assembly of persons,

(b)	the weight of the probable accumulation of equipment and furnishings, and

(c)	the weight of the probable storage of materials.

4.1.6.3.  Full and Partial Loading

(1)  The uniformly distributed load shall be not less than the value listed in Table 4.1.6.3., reduced as may be provided for in Article 4.1.6.9., applied uniformly over the entire area, or on any portions of the area, whichever produces the most critical effects in the members concerned.

Table 4.1.6.3.

Specified Uniformly Distributed Live Loads on an Area of Floor or Roof

Forming Part of Sentence 4.1.6.3.(1)

| Use of Area of Floor or Roof | Minimum Specified Load, kPa |
| --- | --- |
| Assembly Areas |  |
| (a) except for those areas listed under (b) and (c), assembly areas with or without fixed seats including |  |
| Arenas, Rinks, Stadia, Auditoria, Gymnasia |  |
| Churches, Museums, Promenades |  |
| Dance floors, Dining areas (1) |  |
| Foyers and entrance halls |  |
| Grandstands, reviewing stands and bleachers |  |
| Stages, Theatres |  |
| and other areas with similar uses | 4.8 |
| (b) assembly areas with fixed seats that have backs over at least 80 per cent of the assembly area for the following uses: |  |
| Churches, Courtrooms, Lecture halls, Theatres | 2.4 |
| (c) classrooms with or without fixed seats | 2.4 |
| Attics |  |
| Accessible by a stairway in residential occupancies only | 1.4 |
| Having limited accessibility so that there is no storage of equipment or materials | 0.5 |
| Balconies |  |
| Exterior | 4.8 |
| Interior and mezzanines that could be used for the assembly of people as a viewing area (2) | 4.8 |
| Interior and mezzanines other than above | (3) |
| Corridors, lobbies and aisles |  |
| Other than those listed below | 4.8 |
| Not over 1 200 mm in width and all upper floor corridors of residential areas only of apartments, hotels and motels (that can not be used for the assembly of people as a viewing area) (2) | (3) |
| Serving corridors in a Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than 6 occupants requiring assistance in evacuation in case of an emergency | 2.4 |
| Equipment areas and service rooms including |  |
| Generator rooms |  |
| Mechanical equipment exclusive of elevators |  |
| Machine rooms |  |
| Pump rooms |  |
| Transformer vaults |  |
| Ventilating or air-conditioning equipment | 3.6(4) |
| Exits and fire escapes | 4.8 |
| Factories | 6.0(4) |
| Footbridges | 4.8 |
| Garages for |  |
| Passenger cars | 2.4 |
| Unloaded buses and light trucks | 6.0 |
| Loaded buses and trucks and all other trucking spaces | 12.0 |
| Kitchens (other than residential) | 4.8 |
| Libraries |  |
| Stack rooms | 7.2 |
| Reading and study rooms | 2.9 |
| Office areas (not including record storage and computer rooms) located in |  |
| Basement and first storey | 4.8 |
| Floors above first storey | 2.4 |
| Operating rooms and laboratories | 3.6 |
| Patients’ bedrooms | 1.9 |
| Recreation areas that cannot be used for assembly purposes including |  |
| Billiard rooms |  |
| Bowling alleys |  |
| Pool rooms | 3.6 |
| Residential areas (within the scope of Article 2.1.1.2.) |  |
| Sleeping and living quarters in apartments, hotels, motels, boarding schools and colleges | 1.9 |
| Work areas within live/work units | 2.4 |
| Residential areas (within the scope of Article 2.1.1.3.) |  |
| Bedrooms | 1.4 |
| Other areas | 1.9 |
| Stairs within dwelling units | 1.9 |
| Retail and wholesale areas | 4.8 |
| Roofs | 1.0(5) |
| Sidewalks and driveways over areaways and basements | 12.0 |
| Storage areas, including locker rooms in apartment buildings | 4.8(4) |
| Toilet areas | 2.4 |
| Underground slabs with earth cover | (4) |
| Warehouses | 4.8(4) |
| Column 1 | 2 |

Notes to Table 4.1.6.3.:

(1) See Article 4.1.6.6.

(2) Reserved

(3) See Article 4.1.6.4.

(4) See Article 4.1.6.7.

(5) See Article 4.1.7.1.

4.1.6.4.  Loads for Occupancy Served

(1)  The following shall be designed to carry not less than the specified load required for the occupancy they serve:

(a)	corridors, lobbies and aisles not over 1 200 mm in width,

(b)	all corridors above the first storey of residential areas of apartments, hotels and motels, and

(c)	interior balconies and mezzanines,

provided they cannot be used by an assembly of people as a viewing area.

4.1.6.5.  Loads on Exterior Areas

(1)  Exterior areas accessible to vehicular traffic shall be designed for their intended use including the weight of fire fighting equipment, but not less than the live loads due to snow, ice and rain prescribed in Subsection 4.1.7.

(2)  Exterior areas accessible to pedestrian traffic, but not vehicular traffic, shall be designed for their intended use, but not less than

(a)	the live load prescribed for assembly areas in Table 4.1.6.3., and

(b)	the live loads due to snow, ice and rain as prescribed in Subsection 4.1.7.

4.1.6.6.  Loads for Dining Areas

(1)  The minimum specified load in Table 4.1.6.3. for dining areas may be reduced to 2.4 kPa for dining areas in buildings that have been converted for such purposes provided that the floor area does not exceed 100 m2 and use of the dining area for other assembly purposes including dancing is precluded.

4.1.6.7.  Floor Loads Due to Intended Use

(1)  Equipment areas and service rooms, factories, storage areas and warehouses shall be designed for the loads due to their intended use but not less than the specified loads listed in Table 4.1.6.3.

4.1.6.8.  More Than One Occupancy

(1)  Where an area of floor or roof is intended for 2 or more occupancies at different times, the value to be used from Table 4.1.6.3. shall be the greatest value for any of the occupancies concerned.

4.1.6.9.  Variation with Tributary Area

(1)  An area used for assembly occupancies designed for a live load of less than 4.8 kPa shall have no reduction for tributary area.

(2)  Where a structural member supports a tributary area of floor, roof or combination thereof greater than 80 m2 used for assembly occupancies designed for a live load of 4.8 kPa or more, or for storage, manufacturing, retail stores, garages or as a footbridge, the specified live load due to use and occupancy, excluding snow, is the load provided for in Article 4.1.6.3. multiplied by

0.5+ (20A)

where A is the tributary area in square metres for this type of use and occupancy, excluding the area supporting snow.

(3)  Where a structural member supports a tributary area of floor, roof or combination of these greater than 20 m2 for any use or occupancy other than assembly occupancies and those indicated in Sentences (1) and (2), the specified live load due to use and occupancy, excluding snow, is the load provided for in Article 4.1.6.3. multiplied by

0.3+ (9.8B)

where B is the tributary area in square metres for this type of use and occupancy, excluding the area supporting snow.

4.1.6.10.  Concentrated Loads

(1)  The specified load due to possible concentrations of load resulting from the use of an area of floor or roof shall not be less than that listed in Table 4.1.6.10. applied over an area of 750 mm by 750 mm located so as to cause maximum effects, except that for occupancies not listed in Table 4.1.6.10., the concentrations of load shall be determined in accordance with Article 4.1.6.2.

4.1.6.11.  Bleacher Seats

(1)  Bleacher seats shall be designed for a uniformly distributed load of 1.75 kN for each linear metre or for a concentrated load of 2.2 kN distributed over a length of 750 mm, whichever produces the greatest effect on the supporting members.

4.1.6.12.  Helicopter Landing Areas

(1)  Helicopter landing areas on roofs shall be constructed in conformance with “Heliport and Helideck Standards and Recommended Practices”, third edition, 1985, published by Transport Canada.

4.1.6.13.  Roof Parking Decks

(1)  Roof parking decks shall be designed for the uniformly distributed loads in Table 4.1.6.3., the concentrated loads in Table 4.1.6.10. or the roof snow load, whichever produces the greatest effect in the members concerned.

Table 4.1.6.10.

Specified Concentrated Live Loads on an Area of Floor or Roof

Forming Part of Sentence 4.1.6.10.(1)

| Area of Floor or Roof | Minimum Specified Concentrated Load, kN |
| --- | --- |
| Roof surfaces | 1.3 |
| Floors of classrooms | 4.5 |
| Floors of offices, manufacturing buildings, hospital wards and stages | 9.0 |
| Floors and areas used by passenger cars | 11 |
| Floors and areas used by vehicles not exceeding 3600 kg gross weight | 18 |
| Floors and areas used by vehicles exceeding 3600 kg but not exceeding 9000 kg gross weight | 36 |
| Floors and areas used by vehicles exceeding 9000 kg gross weight | 54 |
| Driveways and sidewalks over areaways and basements | 54 |
| Column 1 | 2 |

4.1.7. Live Loads Due to Snow, Ice and Rain

4.1.7.1.  Specified Snow Loading

(1)  The specified loading, S, due to snow accumulation on a roof or any other building surface subject to snow accumulation shall be calculated from the formula

S = Ss(Cb⋅Cw⋅Cs⋅Ca)+Sr

| where | Ss | is the ground snow load in kPa, determined in accordance with Subsection 2.5.1., |
| --- | --- | --- |
|  | Sr | is the associated rain load in kPa determined in accordance with Subsection 2.5.1., but not greater than Ss(Cb·Cw·Cs·Ca), |
|  | Cb | is the basic roof snow load factor of 0.8, |
|  | Cw | is the wind exposure factor in Sentences (2) and (3), |
|  | Cs | is the slope factor in Sentences (4), (5) and (6), and |
|  | Ca | is the accumulation factor in Sentence (7). |

(2)  Except as provided for in Sentence (3), the wind exposure factor, Cw, shall be 1.0.

(3)  The wind exposure factor in Sentence (2) may be reduced to 0.75, or in exposed areas north of the treeline to 0.5, where

(a)	the building is in an exposed location, so that the roof is exposed to the winds on all sides, with no obstructions higher than the roof located closer to the building than a distance equal to 10 times the height of the obstruction above the roof,

(b)	the area of roof under consideration is exposed to the wind on all sides with no significant obstructions on the roof, such as parapet walls, within a distance of at least 10 times the difference between the height of the obstruction and Cb·Cw·Ss/ metres, where  is the unit weight of snow on roofs, and

(c)	the loading does not involve accumulation of snow due to drifting from adjacent surfaces.

(4)  Except as provided for in Sentences (5) and (6), the slope factor, Cs, shall be

(a)	1.0 when the roof slope, , is equal to or less than 30°,

(b)	(70° – )/40° when  is greater than 30°, but not greater than 70°, and

(c)	0 when  exceeds 70°.

(5)  The slope factor, Cs, for unobstructed slippery roofs where snow and ice can slide completely off the roof shall be

(a)	1.0 when the roof slope, , is equal to or less than 15°,

(b)	(60° – )/45° when a is greater than 15°, but not greater than 60°, and

(c)	0 when  exceeds 60°.

(6)  The slope factor, Cs, shall be 1.0 when used in conjunction with accumulation factors for increased snow load as given in Subclauses (7)(c)(ii) and (7)(c)(v).

(7)  The accumulation factor, Ca

(a)	shall be 1.0, except that

(b)	for large flat upper or lower roofs it shall be

(i)	1.2 [1 – (30/l*)2] but not less than 1.0, for roofs with Cw = 1.0, or

(ii)	1.6 [1 – (120/l*)2] but not less than 1.0, for roofs with Cw = 0.75 or 0.5,

where

| l* | = | the characteristic length of the upper or lower roof defined as l* = 2w – w2/l, in metres, |
| --- | --- | --- |
| W | = | the smaller plan dimension of the roof, in metres, |
| L | = | the larger plan dimension of the roof, in metres, |

and

(c)	where appropriate for the shape of the roof, shall be assigned other values which account for

(i)	non-uniform snow loads on gable, arched or curved roofs and domes,

(ii)	increased snow loads in valleys,

(iii)	increased non-uniform snow loads due to snow drifting onto a roof which is at a level lower than other parts of the same building or at a level lower than another building within 5 m of it,

(iv)	increased non-uniform snow loads on areas adjacent to roof projections, such as penthouses, large chimneys and equipment, and

(v)	increased snow or ice loads due to snow sliding or drainage of meltwater from adjacent roofs.

4.1.7.2.  Full and Partial Loading

(1)  A roof or other building surface and its structural members subject to loads due to snow accumulation shall be designed for the specified load in Sentence 4.1.7.1.(1), distributed over the entire loaded area.

(2)  In addition to the distribution in Sentence (1), flat roofs and shed roofs, gable roofs of 15º slope or less and arched or curved roofs shall be designed for the specified uniform snow load in Sentence 4.1.7.1.(1), computed using Ca = 1.0, distributed on any one portion of the loaded area, and half of this load on the remainder of the loaded area, in such a way as to produce the greatest effects on the member concerned.

4.1.7.3.  Specified Rain Load

(1)  The specified load due to the accumulation of rain water on a surface, whose position and shape and deflection under load is such as to make such an accumulation possible, is that resulting from the 24 h rainfall determined in conformance with Subsection 2.5.1. over the horizontal projection of the surface and all tributary surfaces.

(2)  The provisions of Sentence (1) apply whether or not the surface is provided with drainage, such as rain water leaders.

(3)  Except as provided for in Sentence 4.1.7.1.(1) and except where a roof is intended to provide rain water retention, loads due to rain need not be considered to act simultaneously with loads due to snow.

4.1.8. Live Loads Due to Wind

4.1.8.1.  Specified Wind Loading

(1)  The specified external pressure or suction due to wind on part or all of a surface of a building shall be calculated from

p=qCeCgCp

| where | p | = | the specified external pressure acting statically and in a direction normal to the surface either as a pressure directed towards the surface or as a suction directed away from the surface, |
| --- | --- | --- | --- |
|  | q | = | the reference velocity pressure as provided for in Sentence (4), |
|  | Ce | = | the exposure factor as provided for in Sentence (5), |
|  | Cg | = | the gust effect factor as provided for in Sentence (6), and |
|  | Cp | = | the external pressure coefficient averaged over the area of the surface considered. |

(2)  The net wind load for the building as a whole shall be the algebraic difference of the loads on the windward and the leeward surfaces, and in some cases may be calculated as the products of the external pressures or suctions and the areas of the surfaces over which they are averaged as provided in Sentence (1).

(3)  The net specified pressure due to wind on part or all of a surface of a building shall be the algebraic difference of the external pressure or suction as provided for in Sentence (1) and the specified internal pressure or suction due to wind calculated from

pi=qCeCgCpi

| where | pi | = | the specified internal pressure acting statically and in a direction normal to the surface either as a pressure (directed outwards) or as a suction (directed inwards), |
| --- | --- | --- | --- |
|  | q | = | the reference velocity pressure, as provided for in Sentence 4, |
|  | Ce | = | the exposure factor, as provided for in Sentence 5, evaluated at the building mid-height instead of the height of the element considered, |
|  | Cg | = | the gust effect factor as provided for in Sentence (6), and |
|  | Cpi | = | the internal pressure coefficient. |

(4)  The reference velocity pressure, q, is the appropriate value determined in conformance with Subsection 2.5.1. for the following conditions:

(a)	the reference velocity pressure, q, for the design of cladding shall be based on a probability of being exceeded in any one year of 1 in 10,

(b)	the reference velocity pressure, q, for the design of structural members for deflection and vibration shall be based on a probability of being exceeded in any one year of 1 in 10,

(c)	for all buildings, except those listed in Clause (d), the reference velocity pressure, q, for the design of structural members for strength shall be based on a probability of being exceeded in any one year of 1 in 30, and

(d)	the reference velocity pressure, q, for the design of structural members for strength for post-disaster buildings shall be based on a probability of being exceeded in any one year of 1 in 100.

(5)  The exposure factor Ce shall be

(a)	the value shown in Table 4.1.8.1. for the appropriate reference height for the surface or part of the surface,

(b)	the value of the function (h/10)1/5 but not less than 0.9 where h is the reference height above grade in metres for the surface or part of the surface, or

(c)	if a dynamic approach to the action of wind gusts is used, an appropriate value depending on both height and shielding.

Table 4.1.8.1.

Exposure Factors, Ce

Forming Part of Sentence 4.1.8.1.(5)

| Height, m | Exposure Factor |
| --- | --- |
| >0 to  6 | 0.9 |
| > 6 to  12 | 1.0 |
| > 12 to  20 | 1.1 |
| > 20 to  30 | 1.2 |
| > 30 to  44 | 1.3 |
| > 44 to  64 | 1.4 |
| > 64 to  85 | 1.5 |
| > 85 to  140 | 1.6 |
| > 140 to  240 | 1.8 |
| > 240 to  400 | 2.0 |
| Column 1 | 2 |

(6)  The gust effect factor Cg is one of the following values:

(a)	1.0 or 2.0 for internal pressures as appropriate,

(b)	2.0 for the building as a whole and main structural members,

(c)	2.5 for small elements including cladding, or

(d)	if a dynamic approach to the action of wind gusts is used, an appropriate value depending on the turbulence of the wind and the size and natural frequency of the structure.

4.1.8.2.  Dynamic Effects of Wind

(1)  Buildings whose height is greater than 4 times their minimum effective width or greater than 120 m and other buildings whose light weight, low frequency and low damping properties make them susceptible to vibration shall be

(a)	designed by experimental methods for the danger of dynamic overloading and vibration and the effects of fatigue, or

(b)	designed using a dynamic approach to the action of wind gusts.

4.1.8.3.  Full and Partial Loading

(1)  Buildings and structural members shall be capable of withstanding the effects of

(a)	the full winds acting along each of the two principal axes considered separately,

(b)	the wind loads as described in (a) but with 25% of the load removed from any portion of the area,

(c)	the wind loads as in (a) but considered simultaneously at 75% of their full value, and

(d)	the wind loads as described in (c) but with 25% of these loads removed from any portion of the area.

4.1.8.4.  Interior Walls and Partitions

(1)  In the design of interior walls and partitions due consideration shall be given to differences in air pressure on opposite sides of the wall or partition which may result from

(a)	pressure differences between the windward and leeward sides of a building,

(b)	stack effects due to a difference in air temperature between the exterior and interior of the building, and

(c)	air pressurization by the mechanical services of the building.

4.1.9. Live Loads Due to Earthquakes

4.1.9.1.  Analysis

(1)  The specified loading due to earthquake motion shall be determined by the analysis given in this Subsection.

(2)  In this Subsection

| Ar | = | response amplification to account for type of attachment of mechanical/electrical equipment, as defined in Sentence 4.1.9.1.(19), |
| --- | --- | --- |
| Ax | = | amplification factor at level x to account for variation of response of mechanical/electrical equipment with elevation within the building, as defined in Sentence 4.1.9.1.(19), |
| Cp | = | seismic coefficient for mechanical/electrical equipment, as defined in Sentence 4.1.9.1.(19), |
| D | = | the dimension of the building in a direction parallel to the applied forces, |
| Dnx | = | plan dimension of the building at level x perpendicular to the direction of seismic loading being considered, |
| Ds | = | dimension of wall or braced frame which constitutes the main lateral-load-resisting system in a direction parallel to the applied forces, |
| ex | = | distance measured perpendicular to the direction of seismic loading between centre of mass and centre of rigidity at the level being considered, |
| F | = | foundation factor as given in Sentence 4.1.9.1.(11), |
| Ft | = | Portion of V to be concentrated at the top of the structure as defined in Sentence 4.1.9.1.(13), |
| Fx | = | lateral force applied to level x, |
| hi,hn,hx | = | the height above the base (i = 0) to level i, n, or x, respectively, where the base of the structure is that level at which the horizontal earthquake motions are considered to be imparted to the structure, |
| hs | = | interstorey height (hi – hi–1), |
| I | = | seismic importance factor of the structure, as described in Sentence 4.1.9.1.(10), |
| J | = | numerical reduction coefficient for base overturning moment as defined in Sentence 4.1.9.1.(23), |
| Jx | = | numerical reduction coefficient for moment at level “x” as defined in Sentence 4.1.9.1.(24), |
| Level i | = | any level in the building, i = 1 for first level above the base, |
| Level n | = | that level which is uppermost in the main portion of the structure, |
| Level x | = | that level which is under design consideration, |
| N | = | total number of storeys above exterior grade to level n, (N is usually numerically equal to n) |
| R | = | force modification factor that reflects the capacity of a structure to dissipate energy through inelastic behaviour, as given in Sentence 4.1.9.1.(8), |
| S | = | seismic response factor, for unit value of zonal velocity ratio, as defined in Sentence 4.1.9.1.(6), |
| Sp | = | horizontal force factor for part or portion of a building and its anchorage, as given in Table 4.1.9.1.D. and Sentences 4.1.9.1.(17) and (19), |
| T | = | fundamental period of vibration of the building or structure in seconds in the direction under consideration, |
| Tx | = | floor torque at level x as defined in Sentence 4.1.9.1.(28), |
| U | = | factor representing level of protection based on experience, as specified in Sentence 4.1.9.1.(4), |
| v | = | zonal velocity ratio = the specified zonal horizontal ground velocity expressed as a ratio to 1 m/s, |
| V | = | minimum lateral seismic force at the base of the structure, to be used with a load factor aE = 1.0, |
| Ve | = | equivalent lateral force at the base of the structure representing elastic response, as specified in Sentence 4.1.9.1.(5), |
| Vp | = | lateral force on a part of the structure, |
| W | = | dead load plus 25% of the design snow load specified in Subsection 4.1.7. plus 60% of the storage load for areas used for storage and the full contents of any tanks, |
| Wi, Wx | = | that portion of W which is located at or is assigned to level i or x, respectively, |
| Wp | = | the weight of a part or portion of a structure, e.g. cladding, partitions and appendages, |
| Za | = | acceleration-related seismic zone, |
| Zv | = | Velocity-related seismic zone. |

(3)  Earthquake forces shall be assumed to act in any horizontal direction, except that independent design about each of the principal axes shall be considered to provide adequate resistance in the structure for earthquake forces applied in any direction.

(4)  The minimum lateral seismic force, V, shall be calculated in accordance with the following formula:

V=(VeR)U

where U = 0.6.

(5)  The equivalent lateral seismic force representing elastic response, Ve, shall be calculated in accordance with the following formula:

Ve=v⋅S⋅I⋅F⋅W

where v is the zonal velocity ratio determined in conformance with Subsection 2.5.1., except when Zv = 0 and Za > 0 the value of Zv shall be taken as 1 and v as 0.05 in all requirements of Subsection 4.1.9.

Table 4.1.9.1.A.

Seismic Response Factors

Forming Part of Sentence 4.1.9.1.(6)

| T | Za/Zv | S |
| --- | --- | --- |
|  | > 1.0 | 4.2 |
|  | 1.0 | 3.0 |
|  0.25 | < 1.0 | 2.1 |
| > 0.25 but < | > 1.0 | 4.2 – 8.4(T – 0.25) |
| 0.50 | 1.0 | 3.0 – 3.6(T – 0.25) |
|  | < 1.0 | 2.1 |
| ≥ 0.50 | All values | 1.5/(T)1/2 |
| Column 1 | 2 | 3 |

(6)  The seismic response factor, S, shall conform to Table 4.1.9.1.A.

(7)  The fundamental period, T, in Sentence (6) shall be determined by

(a)	the formula 0.1 N for any moment-resisting frame, or by the formulae 0.085(hn)3/4 for a steel moment-resisting frame or 0.075(hn)3/4 for a concrete moment-resisting frame, where the moment-resisting system is a frame which resists 100% of the required lateral forces and the frame is not enclosed by or adjoined by more rigid elements that would tend to prevent the frame from resisting lateral forces, and where hn is in metres,

(b)	the formula 0.09 hn/(Ds)1/2 for other structures, where hn and Ds are in metres, and Ds = length of wall or braced frame which constitutes the main lateral-force-resisting system in the direction parallel to the applied forces; if the main lateral-force-resisting system does not have a well-defined length, then D shall be used in lieu of Ds, or

(c)	other established methods of mechanics; the value of Ve used for design shall be not less than 0.80 of the value computed using the period calculated in Clause (a) or (b).

(8)  Except as provided for in Sentences 4.1.9.3.(1), (2) and (3), values of the force modification factor, R, shall conform to Table 4.1.9.1.B.

(9)  For the purpose of applying Table 4.1.9.1.B.

(a)	a ductile moment-resisting frame shall mean a frame that is designed to resist the specified seismic forces and that, in addition, has adequate ductility or energy-absorptive capacity,

(b)	for combinations of different types of lateral-load-resisting systems acting in the same direction, R shall be taken as the lowest value of R corresponding to these systems except as given in Clause (c),

(c)	if one of the lateral-force-resisting systems of the structure is designed to take 100% of the lateral force, R can be selected as appropriate for the system; the components of the structure not considered to be part of the lateral-force-resisting system must be capable of resisting their gravity loads under seismically induced deformations calculated in accordance with Sentence 4.1.9.2.(2),

(d)	if it can be demonstrated through research or experience that the seismic performance of a structural system is at least equivalent to one of Cases 1-8, 10-14, 16-18 or 20-21 in Table 4.1.9.1.B., then such a structural system will qualify for a value of R corresponding to the equivalent case in that Table.

Table 4.1.9.1.B.

Force Modification Factors

Forming Part of Sentence 4.1.9.1.(8)

| Case | Type of Lateral Load Resisting System | R |
| --- | --- | --- |
|  | Steel Structures Designed and Detailed According to CAN/CSA-S16.1-M |  |
| 1 | ductile moment-resisting frame | 4.0 |
| 2 | ductile eccentrically braced frame | 4.0 |
| 3 | ductile steel plate shear wall | 4.0 |
| 4 | ductile braced frame | 4.0 |
| 5 | moment-resisting frame with nominal ductility | 3.0 |
| 6 | nominally ductile steel plate shear wall | 3.0 |
| 7 | braced frame with nominal ductility | 2.0 |
| 8 | ordinary steel plate shear wall | 2.0 |
| 9 | other lateral-force-resisting systems not defined in Cases 1 to 8 | 1.5 |
|  | Reinforced Concrete Structures Designed and Detailed According to CAN/CSA-A23.3-M |  |
| 10 | ductile moment-resisting frame | 4.0 |
| 11 | ductile coupled wall | 4.0 |
| 12 | other ductile wall systems | 3.5 |
| 13 | moment-resisting frame with nominal ductility | 2.0 |
| 14 | wall with nominal ductility | 2.0 |
| 15 | other lateral-force-resisting systems not defined in Cases 10 to 14 | 1.5 |
|  | Timber Structures Designed and Detailed According to CSA-O86.1 |  |
| 16 | nailed shear panel with plywood, waferboard or OSB | 3.0 |
| 17 | concentrically braced heavy timber frame with ductile connections | 2.0 |
| 18 | moment-resisting wood frame with ductile connections | 2.0 |
| 19 | other systems not included in Cases 16 to 18 | 1.5 |
|  | Masonry Structures Designed and Detailed According to CSA-S304.1 |  |
| 20 | reinforced masonry wall with nominal ductility | 2.0 |
| 21 | reinforced masonry | 1.5 |
| 22 | unreinforced masonry | 1.0 |
| 23 | Other Lateral-force-resisting Systems not Defined in Cases 1 to 22 | 1.0 |
| Column 1 | 2 | 3 |

(10)  The seismic importance factor, I, shall equal 1.5 for post-disaster buildings, 1.3 for schools and 1.0 for all other buildings.

(11)  The foundation factor, F, shall conform to Table 4.1.9.1.C., except that the product F.S need not exceed 3.0 where Za does not exceed Zv and need not exceed 4.2 where Za is greater than Zv.

Table 4.1.9.1.C.

Foundation Factors

Forming Part of Sentence 4.1.9.1.(11)

| Categories | Type and Depth of Rock and Soil Measured from the Foundation or Pile Cap Level | F |
| --- | --- | --- |
| 1 | Rock, dense and very dense coarse-grained soils, very stiff and hard fine-grained soils; compact coarse-grained soils and firm and stiff fine-grained soils from 0 to 15 m deep | 1.0 |
| 2 | Compact coarse-grained soils, firm and stiff fine-grained soils with a depth greater than 15 m; very loose and loose coarse-grained soils and very soft and soft fine-grained soils from 0 to 15 m deep | 1.3 |
| 3 | Very loose and loose coarse-grained soils, with depth greater than 15 m | 1.5 |
| 4 | Very soft and soft fine-grained soils with depth greater than 15 m | 2.0 |
| Column 1 | 2 | 3 |

(12)  The weight, W, of the building shall be calculated in accordance with the following formula:

W=i=1nWi	(13)  The total lateral seismic force, V, shall be distributed as follows:

(a)	a portion, Ft, shall be assumed to be concentrated at the top of the building and equal to 0.07 TV, except that Ft, need not exceed 0.25 V and may be considered as zero where T does not exceed 0.7 s; the remainder, V − Ft, shall be distributed along the height of the building, including the top level, in accordance with the formula

Fx=(V−Ft) Wxhxi=1nWihi, or

(b)	by dynamic analysis, with the seismic effects scaled such that the base shear from the dynamic analysis equals V as given in Sentence 4.1.9.1.(4).

(14)  The total shear in any horizontal plane shall be distributed to the various elements of the lateral-force-resisting system in proportion to their rigidities according to rational analysis, with due regard to the capacities and stiffnesses of the nonstructural elements and to the effects of torsion as required by Sentence 4.1.9.1.(28).

(15)  Except as provided for in Sentence (16), parts of buildings as described in Tables 4.1.9.1.D. and 4.1.9.1.E. and their anchorage shall be designed to accommodate the deflections defined in Article 4.1.9.2., and for a lateral force, Vp, equal to v.I.Sp.Wp, distributed according to the distribution of mass of the element under consideration, where v is determined in conformance with Subsection 2.5.1., and I is the same importance factor as used for the building.

(16)  For non post-disaster buildings in zones where Za and Zv are equal to or less than 1.0 and F is equal to or less than 1.3, the requirements of Sentence (15) shall not apply to Table 4.1.9.1.E. or to cases 7, 8, and 9 of Table 4.1.9.1.D.

(17)  Except as provided for in Sentence (21), the values of Sp in Sentences (15) and (16) for architectural components shall conform to Table 4.1.9.1.D.

(18)  All fasteners and anchors in a ductile connection, such as bolts, inserts, welds, or dowels, shall be capable of developing 3 times the yield load of the body of the connection.

(19)  The values of Sp in Sentences (15) and (16) for mechanical/electrical components shall be equal to:

Sp = Cp•Ar•Ax

where

| Cp | = | seismic coefficient for components of mechanical and electrical equipment as given Table 4.1.9.1.E., |
| --- | --- | --- |
| Ar | = | 1.0 for components that are both rigid and rigidly connected and for non-brittle pipes and ducts, |
|  | = | 1.5 for components located on the ground that are flexible or flexibly connected except for non-brittle pipes and ducts, |
|  | = | 3.0 for all other cases, |
| Ax | = | 1.0 + (hx/hn). |

Table 4.1.9.1.D.

Values of Sp for Architectural Parts or Portions of Buildings

Forming Part of Sentence 4.1.9.1.(15)

| Category | Architectural Part or Portion of Building | Direction of Force | Value of Sp |
| --- | --- | --- | --- |
| 1 | All exterior and interior walls except those of Categories 2 and 3 | Normal to flat surface | 1.5 |
| 2 | Cantilever parapet and other cantilever walls except retaining walls | Normal to flat surface | 6.5 |
| 3 | Exterior and interior ornamentations and appendages | Any direction | 6.5 |
| 4 | Connections/attachments for Categories 1, 2 and 3 |  |  |
|  | The body of ductile connections/ attachments | Any direction | 2.5 |
|  | All fasteners and anchors in the ductile connection, such as bolts, inserts, welds or dowels | Any direction | (1) |
|  | Non-ductile connections/ attachments | Any direction | 15.0 |
| 5 | Floors and roofs acting as diaphragms(2) | Any direction | 0.7 |
| 6 | Towers, chimneys, smokestacks and penthouses when connected to or forming part of a building(2) | Any direction | 4.5 |
| 7 | Horizontally cantilevered floors, balconies, beams, etc. | Vertical | 4.5 |
| 8 | Suspended ceilings, light fixtures and other attachments to ceilings with independent vertical support | Any direction | 2.0 |
| 9 | Masonry veneer connections | Normal to flat surface | 5.0 |
| Col. 1 | 2 | 3 | 4 |

Notes to Table 4.1.9.1.D.:

(1) See Sentence 4.1.9.1.(18).

(2) See Sentence 4.1.9.1.(21).

(20)  For the purpose of applying Sentence (19)

(a)	components that are both rigid and rigidly connected are defined as those having a fundamental period for the component and connection less than or equal to 0.06 s, and

(b)	flexible components or connections are defined as those having a fundamental period greater than 0.06 s.

Table 4.1.9.1.E.

Values of Cp for Mechanical/Electrical Parts or Portions of Buildings

Forming Part of Sentence 4.1.9.1.(15)

| Category | Mechanical/Electrical Part or Portion of Building | Direction of Force | Value of Cp |
| --- | --- | --- | --- |
| 1 | Machinery, fixtures, equipment, ducts, tanks and pipes (including contents) except as noted elsewhere in this table(1) | Any direction | 1.0 |
| 2 | Machinery, fixtures, equipment, ducts, tanks and pipes (including contents) containing toxic or explosive materials, materials having a flash point below 38°C or fire fighting fluids. | Any direction | 1.5 |
| 3 | Flat bottom tanks (including contents) attached directly to a floor at or below grade within a building. | Any direction | 0.7 |
| 4 | Flat bottom tanks (including contents) attached directly to a floor at or below grade within a building containing toxic or explosive materials having a flash point below 38°C or fire fighting fluids. | Any direction | 1.0 |
| Column 1 | 2 | 3 | 4 |

(21)  Floors and roofs acting as diaphragms shall be designed for a minimum force corresponding to a value of Sp equal to 0.7 applied to loads tributary from that storey, unless a greater force Fx is assigned to the level under consideration as in Sentences (13) and (14).

(22)  When the mass of a tank plus contents is greater than 10% of the mass of the supporting floor, the lateral forces shall be determined by rational analysis.

(23)  The overturning moment, M, at the base of the structure shall be multiplied by a reduction coefficient, J, where

(a)	J = 1 where T is less than 0.5,

(b)	J = (1.1 – 0.2T) where T is not less than 0.5, but not more than 1.5, and

(c)	J = 0.8 where T is greater than 1.5.

(24)  The overturning moment Mx at any level x shall be

(a)	multiplied by Jx where

Jx=J+(1−J)(hxhn)3, and

(b)	distributed as required in Sentences (25), (26) and (27).

(25)  The incremental changes in the design overturning moments, in the storey under consideration, shall be distributed to the various resisting elements in the same proportion as the distribution of shears in the resisting system.

(26)  Where other vertical members are provided which are capable of partially resisting the overturning moments, a redistribution may be made to these members if framing members of sufficient strength and stiffness to transmit the required loads are provided.

(27)  Where a vertical-resisting element is discontinuous, the overturning moment carried by the lowest storey of that element shall be carried down as loads to the foundation.

(28)  Torsional moments about a vertical axis of the building shall be calculated as

(a)	for an analysis carried out in accordance with Clause 4.1.9.1.(13)(a), the torsional moments applied at each level throughout the building shall be derived for each of the following load cases considered separately

(i)	Tx = Fx(1.5ex + 0.1 Dnx)

(ii)	Tx = Fx(1.5ex – 0.1 Dnx)

(iii)	Tx = Fx(0.5ex + 0.1 Dnx)

(iv)	Tx = Fx(0.5ex – 0.1 Dnx)

where Fx is the lateral floor force at each level as given by Clause 4.1.9.1.(13)(a) and the term 0.1 Dnx·Fx represents the accidental torsional moment applied at each level and where each element in the building is designed for the most severe effect of the above load cases, or

(b)	the effects of accidental torsional moments applied at each level throughout the building shall be derived for each of the following load cases considered separately and shall be added to the effects of a three dimensional dynamic analysis

(i)	Tx = + 0.1 Dnx·Fx

(ii)	Tx = – 0.1 Dnx·Fx

and where each element in the building is designed for the most severe effect of the above load cases and Fx is the lateral floor force at each level as given by Clause 4.1.9.1.(13)(a).

(29)  The building design shall take full account of the possible effects of setbacks.

4.1.9.2.  Deflections

(1)  Lateral deflections of a structure shall be calculated in accordance with accepted practice and based on the loads and requirements defined in this Section.

(2)  Lateral deflections obtained from an elastic analysis using the loads given in Sentences 4.1.9.1.(13) and (14) and incorporating the effects of torsion shall be multiplied by R to give realistic values of anticipated deflections.

(3)  The interstorey deflections based on the lateral deflections as calculated in Sentence (2) shall be limited to 0.01hs for post-disaster buildings and 0.02hs for all other buildings.

(4)  All portions of the structure shall be designed to act as integral units in resisting horizontal forces, unless separated by adequate clearances which permit horizontal deflections of the structure consistent with values of deflections calculated in accordance with Sentence (2).

(5)  The nonstructural components shall be designed so as not to transfer to the structural system any forces unaccounted for in the design, and any interaction of rigid elements such as walls and the structural system shall be designed so that the capacity of the structural system is not impaired by the action or failure of the rigid elements.

(6)  Adjacent structures shall either be separated by the sum of their individual deflections as calculated in Sentence (2), or shall be connected to each other.

(7)  The method of connection in Sentence (6) shall take into account the mass, stiffness, strength, ductility and anticipated motion of the connected buildings and the character of the connection.

(8)  The deflections as calculated in Sentence (2) shall be used to account for sway effects due to seismic loading as required by Sentence 4.1.1.5.(2).

(9)  The connected buildings in Sentence (6) shall be assumed to have the lowest R value of the buildings connected, unless the use of a higher value can be justified by rational analysis.

4.1.9.3.  Special Provisions

(1)  Buildings more than 3 storeys in building height in velocity- or acceleration-related seismic zones of 2 and higher shall have a structural system as described in Cases 1-8, 10-14, 16-18 or 20-21 in Table 4.1.9.1.B.

(2)  For buildings more than 60 m in height with a structural system having R = 2.0 or R = 1.5 as determined from Table 4.1.9.1.B. or as determined from Clause 4.1.9.1.(9)(b), the value of V shall be increased by 50% in velocity-related seismic zones of 4 and higher.

(3)  Elevated tanks plus full contents not supported by a building, shall be designed using R = 1 in the formula in Sentence 4.1.9.1.(4), with the conditions

(a)	the minimum and maximum value of the product S.I shall be taken as 1.5 and 3.0, respectively,

(b)	the overturning moment reduction coefficient, J, as set forth in Sentence 4.1.9.1.(2) shall be 1.0, and

(c)	the torsional requirements of Sentence 4.1.9.1.(28) shall apply.

(4)  For buildings in velocity- or acceleration-related seismic zones of 2 and higher in which discontinuities in columns or shear walls occur, special design provisions shall be made to ensure that failure at the point of discontinuity will not occur before the capacity of the remaining portion of the structure has been realized.

(5)  In velocity- or acceleration-related seismic zones of 2 and higher, reinforcement conforming to Clause 6.3.3. of CSA-S304.1, “Masonry Design for Buildings (Limit States Design)” shall be provided for masonry construction in

(a)	loadbearing and lateral load-resisting masonry,

(b)	masonry enclosing elevator shafts and stairways, or used as exterior cladding, and

(c)	masonry partitions, except for partitions which

(i)	do not exceed 200 kg/m2 in weight, and

(ii)	do not exceed 3 m in height and are laterally supported at the top.

4.1.9.4.  Foundation Provisions

(1)  Foundations shall be designed so that yielding will occur first in the superstructure and not the foundations, unless the design specifically provides otherwise.

(2)  Except in velocity-related seismic Zone 0, individual pile footings, drilled piers and caissons shall be interconnected by ties in at least 2 directions.

(3)  Ties in Sentence (2) shall be designed to carry by tension or compression a horizontal force equal to the greatest factored pile cap loading multiplied by a factor 0.5 v, but not exceeding 10% of the greatest factored pile cap load, unless it can be demonstrated that equivalent restraints can be provided by other means.

(4)  Except in velocity-related seismic Zone 0, piles shall be connected to the pile cap or structure by reinforcement having sufficient anchorage to develop the yield strength of the reinforcement, and the top of the piles (below the pile cap) shall be reinforced to allow ductile behaviour if the design depends upon such action.

(5)  Except in velocity-related seismic Zones 0 and 1, basement walls shall be designed to resist seismic lateral pressures from backfill or natural ground.

4.1.10. Other Effects

4.1.10.1.  Loads on Guards

(1)  The minimum specified horizontal load applied inward or outward at the top of every required guard shall be

(a)	3.0 kN/m for means of egress in grandstands, stadia, bleachers and arenas,

(b)	a concentrated load of 1.0 kN applied at any point for access walkways to equipment platforms, contiguous stairs and similar areas where the gathering of many people is improbable, and

(c)	0.75 kN/m or a concentrated load of 1.0 kN applied at any point, whichever governs, for locations other than described in Clauses (a) and (b).

(2)  Individual elements within the guard, including solid panels and pickets, shall be designed for a concentrated load of 0.5 kN at any point in the element.

(3)  The loads required in Sentence (2) need not be considered to act simultaneously with the loads provided for in Sentences (1) and (4).

(4)  The minimum specified load applied vertically at the top of every required guard shall be 1.5 kN/m and need not be considered to act simultaneously with the horizontal load provided for in Sentence (1).

4.1.10.2.  Loads on Vehicle Guardrails

(1)  Vehicle guardrails for parking garages shall be designed for a concentrated load of 22 kN applied horizontally outward at any point 500 mm above the floor surface.

4.1.10.3.  Loads on Walls Acting As Guards

(1)  Where the floor elevation on one side of a wall, including a wall around a shaft, is more than 600 mm higher than the elevation of the floor or ground on the other side, the wall shall be designed to resist the appropriate lateral design loads prescribed elsewhere in this Section or 0.5 kPa, whichever produces the greatest effect.

4.1.10.4.  Firewalls

(1)  Firewalls shall be designed to resist the maximum effect due to

(a)	the appropriate lateral design loads prescribed elsewhere in this Section, or

(b)	a factored lateral load of 0.5 kPa under fire conditions as described in Sentence (2).

(2)  Under fire conditions, when the fire-resistance rating of the structure is less than that of the firewall

(a)	lateral support shall be assumed to be provided by the structure on one side only, or

(b)	another structural support system capable of resisting the loads imposed by a fire on either side of the firewall shall be provided.

4.1.10.5.  Vibrations and Impact of Machinery and Equipment

(1)  Where vibration effects, such as resonance and fatigue resulting from machinery or equipment, are likely to be significant, a dynamic analysis shall be carried out.

(2)  The minimum specified load due to equipment, machinery or other objects that may produce impact shall be the sum of the weight of the equipment or machinery and its maximum lifting capacity, multiplied by an appropriate factor listed in Table 4.1.10.5.

Table 4.1.10.5.

Factors for the Calculation of Impact Loads

Forming Part of Sentence 4.1.10.5.(2)

| Impact Due to | Factor |
| --- | --- |
| Operation of cab or radio operated cranes | 1.25 |
| Operation of pendant or hand operated cranes | 1.10 |
| Operation of elevators | (1) |
| Supports for light machinery, shaft or motor driven | 1.20 |
| Supports for reciprocating machinery (e.g. compressors) | 1.50 |
| Supports for power driven units (e.g. piston engines) | 1.50 |
| Column 1 | 2 |

Note to Table 4.1.10.5.

(1) See CAN/CSA-B44-M, Clauses 2.6.2. and 2.10.3.

(3)  Crane runway structures shall be designed to resist a horizontal force applied normal to the top of the rails equal to not less than 20% of the sum of the weights of the lifted load and the crane trolley (excluding other parts of the crane).

(4)  The force described in Sentence (3) shall be equally distributed on each side of the runway and shall be assumed to act in either direction.

(5)  Crane runway structures shall be designed to resist a horizontal force applied parallel to the top of the rail equal to not less than 10% of the maximum wheel loads of the crane.

4.1.10.6.  Resonances and Sway Forces

(1)  Where the fundamental vibration frequency of a structural system supporting an assembly occupancy used for rhythmic activities, such as dancing, concerts, jumping exercises or gymnastics, is less than 6 Hz, the effects of resonance shall be investigated by means of a dynamic analysis.

(2)  The floor assembly and other structural elements that support fixed seats in any building used for assembly occupancies to accommodate large numbers of people at one time, such as grandstands, stadia and theatre balconies, shall be designed to resist a horizontal force equal to not less than 0.3 kN for each metre length of seats acting parallel to each row of seats, and not less than 0.15 kN for each metre length of seat acting at right angles to each row of seats, assuming such forces to be acting independently of each other.

4.1.10.7.  Bleachers

(1)  Bleachers shall be checked by the erector after erection to ensure that all structural members including bracing specified in the design have been installed.

(2)  Telescopic bleachers shall be provided with locking devices to ensure stability while in use.

4.1.10.8.  Anchor Systems on Building Exterior

(1)  Where maintenance and window cleaning operations are intended to be carried out on the exterior of a building described in Article 2.1.1.2, anchor systems shall be provided where any portion of the roof is more than 8 m above adjacent ground level.

(2)  Except as provided in Sentence (3), the anchor systems in Sentence (1) shall be designed, installed and tested in conformance with CSA Standard Z91, “Safety Code for Window Cleaning Operations”.

(3)  Other anchor systems may be used where such systems provide an equal level of safety.

(4)  The anchor system material shall be made of stainless steel, aluminum, or other corrosion resistant base material, or from steel that is hot dipped galvanised, in accordance with CSA Standard G164-M81, “Hot Dip Galvanising of Irregularly Shaped Articles”.

Section 4.2. Foundations

4.2.1. General

4.2.1.1.  Application

(1)  This Section applies to excavations and foundation systems for buildings.

4.2.2. Subsurface Investigations and Reviews

4.2.2.1.  Subsurface Investigation

(1)  A subsurface investigation shall be carried out, which shall include groundwater conditions.

4.2.2.2.  Reserved

4.2.2.3.  Review

(1)  A review shall be carried out by the designer or by another suitably qualified person to ascertain that the subsurface conditions are consistent with the design and that construction is carried out in accordance with the design and good engineering practice.

(2)  The review required in Sentence (1) shall be carried out

(a)	on a continuous basis

(i)	during the construction of all deep foundation units with all pertinent information recorded for each unit, and

(ii)	during the installation and removal of retaining structures and related backfilling operations, and

(b)	as required, unless otherwise directed by the chief building official

(i)	in the construction of all shallow foundation units, and

(ii)	in excavating, dewatering and other related works.

4.2.2.4.  Altered Subsurface Condition

(1)  Where, during construction, the soil, rock or groundwater is found not to be of the type or in the condition used in design, and as indicated on the drawings, the design shall be reassessed by the designer.

(2)  Where, during construction, climatic or any other conditions have changed the properties of the soil, rock or groundwater, the design shall be reassessed by the designer.

4.2.3. Materials Used in Foundations

4.2.3.1.  Wood

(1)  Wood used in foundations or in support of soil or rock shall conform with the appropriate requirements of Subsection 4.3.1.

4.2.3.2.  Preservation Treatment of Wood

(1)  Wood exposed to soil or air above the lowest anticipated groundwater table shall be treated with preservative in conformance with CAN/CSA-O80-M, “Wood Preservation” and the requirements of the appropriate commodity standard as follows:

(a)	CSA-O80.2-M, “Preservative Treatment of Lumber, Timber, Bridge Ties and Mine Ties by Pressure Processes”,

(b)	CSA-O80.3-M, “Preservative Treatment of Piles by Pressure Processes”, or

(c)	CSA-O80.15-M, “Preservative Treatment of Wood for Building Foundation Systems, Basements and Crawl Spaces by Pressure Processes”.

(2)  Where timber has been treated as required in Sentence (1), it shall be cared for as provided in AWPA Standard M4, “Care of Preservative Treated Wood Products” as revised by Clause 6 of CAN/CSA-O80, “Wood Preservation”.

4.2.3.3.  Plain and Reinforced Masonry

(1)  Plain or reinforced masonry used in foundations or in support of soil or rock shall conform with the requirements of Subsection 4.3.2.

4.2.3.4.  Prevention of Deterioration of Masonry

(1)  Where plain or reinforced masonry in foundations or in structures supporting soil or rock may be subject to conditions conducive to deterioration, protection shall be provided to prevent such deterioration.

4.2.3.5.  Concrete

(1)  Plain, reinforced or prestressed concrete used in foundations or in support of soil or rock shall conform with the requirements of Subsection 4.3.3.

4.2.3.6.  Chemical Attack of Concrete

(1)  Where concrete in foundations may be subject to chemical attack, it shall be treated in conformance with the requirements in CAN3-A23.1, “Concrete Materials and Methods of Concrete Construction”.

4.2.3.7.  Steel

(1)  Steel used in foundations or in support of soil or rock shall conform with the appropriate requirements of Subsections 4.3.3. or 4.3.4., unless otherwise specified in this Section.

4.2.3.8.  Steel Piles

(1)  Where steel piles are used in deep foundations and act as permanent load-carrying members, the steel shall conform with one of the following standards:

(a)	CAN3-G40.21-M, “Structural Quality Steels”,

(b)	ASTM A252, “Welded and Seamless Steel Pipe Piles”,

(c)	ASTM A283/A283M, “Low and Intermediate Tensile Strength Carbon Steel Plates”,

(d)	ASTM A570/A570M, “Steel, Sheet and Strip, Carbon, Hot-Rolled, Structural Quality”, or

(e)	ASTM A611, “Steel Sheet, Carbon, Cold-Rolled Sheet, Structural Quality”.

4.2.3.9.  High Strength Steel Tendons

(1)  Where high strength steel is used for tendons in anchor systems used for the permanent support of a foundation or in the erection of temporary support of soil or rock adjacent to an excavation, it shall conform with the requirements of CAN3-A23.1, “Concrete Materials and Methods of Concrete Construction”.

4.2.3.10.  Corrosion of Steel

(1)  Where conditions are corrosive to steel, adequate protection of exposed steel shall be provided.

4.2.4. Design Requirements

4.2.4.1.  Design Basis

(1)  The design of foundations, excavations and soil- and rock-retaining structures shall be based on a subsurface investigation carried out by a person competent in this field of work, and one of the following:

(a)	application of generally accepted geotechnical and civil engineering principles by a person especially qualified in this field of work as provided in this Section and other Sections of Part 4,

(b)	established local practice where such practice includes successful experience both with soils and rocks of similar type and condition and with a foundation or excavation of similar type, construction method, size and depth, or

(c)	in situ testing of foundation units such as the load testing of piles, anchors or footings carried out by a person competent in this field of work.

4.2.4.2.  Subsurface Investigation

(1)  A subsurface investigation shall be carried out to the depth and extent to which the building or excavation will significantly change the stress in the soil or rock, or to such a depth and extent as to provide all the necessary information for the design and construction of the excavation or the foundations.

4.2.4.3.  Identification

(1)  The identification and classification of soil, rock and groundwater and descriptions of their engineering and physical properties shall be in accordance with a widely accepted system.

4.2.4.4.  Loads on Foundations

(1)  The foundation of a building shall be capable of resisting all loads as stipulated in Section 4.1., in accordance with limit states design in Subsection 4.1.3. or working stress design in Subsection 4.1.4.

4.2.4.5.  Differential Movements

(1)  The foundation of a building shall be proportioned so that the estimated total and differential movements of the foundation are not greater than the movements that the building is designed to accommodate.

4.2.4.6.  Depth of Foundations

(1)  Except as permitted in Sentence (2), the bearing surface of a foundation shall be below the level of potential damage, including damage resulting from frost action, and the foundation shall be designed to prevent damage resulting from adfreezing and frost jacking.

(2)  The bearing surface of a foundation need not be below the level of potential damage from frost where the foundation

(a)	is designed against frost action, or

(b)	overlies material not susceptible to frost action.

4.2.4.7.  Sloping Ground

(1)  Where a foundation is to rest on, in or near sloping ground, this particular condition shall be provided for in the design.

4.2.4.8.  Eccentric and Inclined Loads

(1)  Where there is eccentricity or inclination of loading in foundation units, this effect shall be fully investigated and provided for in the design.

4.2.4.9.  Dynamic Loading

(1)  Where dynamic loading conditions apply, the effects shall be assessed by a special investigation of these conditions and provided for in the design.

4.2.4.10.  Hydrostatic Uplift

(1)  Where a foundation or any part of a building is subject to hydrostatic uplift the effects shall be provided for in the design.

4.2.4.11.  Groundwater Level Charge

(1)  Where proposed construction will result in a temporary or permanent change in the groundwater level, the effects of this change on adjacent property shall be fully investigated and provided for in the design.

4.2.4.12.  Permafrost

(1)  Where conditions of permafrost are encountered or proven to exist, the design of the foundation shall be based upon analysis of these conditions by a person especially qualified in that field of work.

4.2.4.13.  Swelling and Shrinking Soils

(1)  Where swelling or shrinking soils, in which movements resulting from moisture content changes may be sufficient to cause damage to a structure, are encountered or known to exist, such a condition shall be fully investigated and provided for in the design.

4.2.4.14.  Expanding and Deteriorating

(1)  Where rock which expands or deteriorates when subjected to unfavourable environmental conditions or to stress release is known to exist such condition shall be fully investigated and provided for in the design.

4.2.4.15.  Construction on Fill

(1)  Buildings may be placed on fill if it can be shown by subsurface investigation that

(a)	the fill is or can be made capable of safely supporting the building,

(b)	detrimental movement of the building or services leading to the building will not occur, and

(c)	explosive gases can be controlled or do not exist.

4.2.4.16.  Structural Design

(1)  The structural design of the foundation of a building, the procedures and construction practices shall conform with the appropriate Sections of this Code unless otherwise specified in this Section.

4.2.5. Excavations

4.2.5.1.  Design of Excavations

(1)  The design of excavations and of supports for the sides of excavations shall conform with the requirements of Subsection 4.2.4. and with this Subsection.

4.2.5.2.  Excavation Construction

(1)  Every excavation shall be undertaken in such a manner as to prevent movement which would cause damage to adjacent property, existing structures, utilities, roads and sidewalks at all phases of construction.

(2)  Material shall not be placed nor shall equipment be operated or placed in or adjacent to an excavation in a manner that may endanger the integrity of the excavation or its supports.

4.2.5.3.  Supported Excavations

(1)  The sides of an excavation in soil or rock shall be supported by a retaining structure conforming with the requirements of Articles 4.2.5.1. and 4.2.5.2., except as permitted in Article 4.2.5.4.

4.2.5.4.  Unsupported Excavations

(1)  The sides of an excavation in soil or rock may be unsupported where a design is prepared by a person especially qualified in this field of work in conformance with the requirements of Articles 4.2.5.1. and 4.2.5.2.

4.2.5.5.  Control of Water Around Excavations

(1)  Surface water, all groundwater, perched and in particular artesian groundwater shall be kept under control at all phases of excavation and construction.

4.2.5.6.  Loss of Ground

(1)  At all phases of excavation and construction, loss of ground due to water or any other cause shall be prevented.

4.2.5.7.  Protection and Maintenance at Excavations

(1)  All sides of an excavation, supported and unsupported, shall be continuously maintained and protected from possible deterioration by construction activity or by the action of frost, rain and wind.

4.2.5.8.  Backfilling

(1)  Where an excavation is backfilled, the backfill shall be placed so as to

(a)	provide lateral support to the soil adjacent to the excavation, and

(b)	prevent detrimental movements.

(2)  The material used as backfill or fill supporting a footing, foundation or a floor on grade shall be of a type that is not subject to detrimental volume change with changes in moisture content and temperature.

4.2.6. Shallow Foundations

4.2.6.1.  Design of Shallow Foundations

(1)  The design of shallow foundations shall be in conformance with Subsection 4.2.4. and the requirements of this Subsection.

4.2.6.2.  Support of Shallow Foundations

(1)  Where a shallow foundation is to be placed on soil or rock, the soil or rock shall be cleaned of loose and unsound material and shall be adequate to support the design load taking into account temperature, precipitation, construction activities and other factors which may lead to changes of the properties of soil or rock.

4.2.6.3.  Incorrect Placement of Shallow Foundations

(1)  Where a shallow foundation unit has not been placed or located as indicated on the drawings

(a)	the error shall be corrected, or

(b)	the design of the foundation unit shall be recalculated for the altered conditions by the designer.

4.2.6.4.  Damaged Shallow Foundations

(1)  Where a shallow foundation unit is damaged

(a)	it shall be repaired, or

(b)	the design of the foundation unit shall be recalculated for the damaged condition by the designer.

4.2.7. Deep Foundations

4.2.7.1.  General

(1)  A deep foundation unit shall provide support for a building by transferring loads by end-bearing to a competent stratum at considerable depth below the structure, or by mobilizing resistance by adhesion or friction, or both, in the soil or rock in which it is placed.

4.2.7.2.  Design for Deep Foundations

(1)  Deep foundation units shall be designed in conformance with Subsection 4.2.4. and this Subsection.

(2)  Where deep foundation units are load tested, as required in Clause 4.2.4.1.(1)(c), the determination of the number and type of load test and the interpretation of the results shall be carried out by a person especially qualified in this field of work.

(3)  Where deep foundation units are not load tested as outlined in Clause 4.2.4.1.(1)(c), and where well established local practice as outlined in Clause 4.2.4.1.(1)(b) is not applicable, the design shall be carried out in conformance with Clause 4.2.4.1.(1)(a).

(4)  The design of deep foundations shall be determined on the basis of geotechnical considerations taking into account

(a)	the method of installation,

(b)	the degree of inspection,

(c)	the spacing of foundation units and group effects,

(d)	other requirements of this Subsection, and

(e)	the appropriate structural requirements of Section 4.1. and Subsections 4.3.1., 4.3.3. and 4.3.4.

(5)  The portion of a deep foundation unit permanently in contact with soil or rock shall be structurally designed as a laterally supported compression member.

(6)  The portion of a deep foundation unit which is not permanently in contact with soil or rock shall be structurally designed as a laterally unsupported compression member.

(7)  The structural design of prefabricated deep foundation units shall allow for all stresses resulting from driving, handling and testing.

4.2.7.3.  Tolerance in Alignment and Location

(1)  Permissible deviations from the design alignment and the location of the top of deep foundation units shall be determined by design analysis, and shall be indicated on the drawings.

4.2.7.4.  Incorrect Alignment and Location

(1)  Where a deep foundation unit has not been placed within the permissible deviations referred to in Article 4.2.7.3., the condition of the foundation shall be assessed by the person responsible for the design, any necessary changes made and action taken as required.

4.2.7.5.  Installation of Deep Foundations

(1)  Deep foundation units shall be installed in such a manner as not to impair

(a)	the strength of the deep foundation units and the properties of the soil or rock on or in which they are placed beyond the calculated or anticipated limits,

(b)	the integrity of previously installed deep foundation units, or

(c)	the integrity of neighbouring structures and services.

4.2.7.6.  Damaged Deep Foundation Units

(1)  Where inspection shows that a deep foundation unit is damaged or not consistent with design or good engineering practice

(a)	such a unit shall be reassessed by the designer, and

(b)	any necessary changes shall be made and action taken as required.

4.2.8. Special Foundations

4.2.8.1.  General

(1)  Where special foundation systems are used, such systems shall conform to Subsection 4.2.4.

4.2.8.2.  Use of Existing Foundations

(1)  Existing foundations may be used to support new or altered buildings provided they comply with all pertinent requirements of this Section.

Section 4.3. Design Requirements for Structural Materials

4.3.1. Wood

4.3.1.1.  Design Basis for Wood

(1)  Buildings and their structural members made of wood shall conform to CAN/CSA-O86.1-M, “Engineering Design in Wood (Limit States Design)”.

4.3.1.2.  Glue-Laminated Members

(1)  Glued-laminated members shall be fabricated in plants conforming to CAN/CSA-O177-M, “Qualification Code for Manufacturers of Structural Glued-Laminated Timber”.

4.3.1.3.  Termites

(1)  In areas known to be infested by termites, the requirements in Articles 9.3.2.9., 9.12.1.1. and 9.15.5.1. shall apply.

4.3.2. Plain and Reinforced Masonry

4.3.2.1.  Design Basis for Plain and Reinforced Masonry

(1)  Buildings and their structural members made of plain and reinforced masonry shall conform to

(a)	CAN3-S304-M, “Masonry Design for Buildings”, or

(b)	CSA-S304.1, “Masonry Design for Buildings” (Limit States Design).

4.3.3. Plain, Reinforced and Prestressed Concrete

4.3.3.1.  Design Basis for Plain, Reinforced and Prestressed Concrete

(1)  Buildings and their structural members made of plain, reinforced or prestressed concrete shall conform to CAN/CSA-A23.3-M, “Design of Concrete Structures for Buildings”.

4.3.4. Steel

4.3.4.1.  Design Basis for Structural Steel

(1)  Buildings and their structural members made of structural steel shall conform to CAN/CSA-S16.1-M, “Limit States Design of Steel Structures”.

4.3.4.2.  Design Basis for Cold Formed Steel

(1)  Buildings and their structural members made of cold formed steel shall conform to CAN/CSA-S136-M, “Cold Formed Steel Structural Members”.

4.3.5. Aluminum

4.3.5.1.  Design Basis for Aluminum

(1)  Buildings and their structural members made of aluminum shall conform to CAN3-S157-M, “Strength Design in Aluminum”.

4.3.6. Glass

4.3.6.1.  Design Basis for Glass

(1)  Glass shall be designed in conformance with CAN/CGSB-12.20-M, “Structural Design of Glass for Buildings”.

Section 4.4. Design Requirements for Special Structures

4.4.1. Air-Supported Structures

4.4.1.1.  Design Basis for Air-Supported Structures

(1)  The structural design of air-supported structures shall conform to CAN3-S367-M, “Air-Supported Structures”.

4.4.2. Parking Structures

4.4.2.1.  Design Basis for Parking Structures

(1)  Parking structures shall be designed in conformance with CSA-S413, “Parking Structures”.

4.4.3. Guards Over Retaining Walls

4.4.3.1.  Guards Over Retaining Walls

(1)  Every retaining wall which is a designated structure in Subsection 2.1.2. shall be protected by guards on all open sides where the public has access to open space at the top of the retaining wall.

O. Reg. 403/97, Part 4; O. Reg. 220/02, ss. 8, 9; O. Reg. 349/06, s. 13.

Part 5
Wind, Water and Vapour Protection

| Section | 5.1. | General |
| --- | --- | --- |
|  | 5.1.1. | Scope |
|  | 5.1.2. | Application |
|  | 5.1.3. | Definitions |
|  | 5.1.4. | Environmental Separation Requirements |
|  | 5.1.5. | Other Requirements |
| Section | 5.2. | Loads and Procedures |
|  | 5.2.1. | Environmental Loads |
|  | 5.2.2. | Procedures |
| Section | 5.3. | Heat Transfer |
|  | 5.3.1. | Thermal Resistance of Assemblies |
| Section | 5.4. | Air Leakage |
|  | 5.4.1. | Air Barrier Systems |
| Section | 5.5. | Vapour Diffusion |
|  | 5.5.1. | Vapour Barriers |
| Section | 5.6. | Precipitation |
|  | 5.6.1. | Protection from Precipitation |
|  | 5.6.2. | Sealing, Drainage, Accumulation and Disposal |
| Section | 5.7. | Surface Water |
|  | 5.7.1. | Protection from Surface Water |
| Section | 5.8. | Moisture in the Ground |
|  | 5.8.1. | Foundation and Floor Drainage |
|  | 5.8.2. | Protection from Moisture in the Ground |

Part 5
Wind, Water and Vapour Protection

Section 5.1. General

5.1.1. Scope

5.1.1.1.  Scope

(1)  The scope of this Part shall be as described in Section 2.1.

5.1.2. Application

5.1.2.1.  Separation of Environments

(1)  This Part applies to

(a)	the control of condensation in and on, and the transfer of heat, air and moisture through building elements and interfaces between building elements that separate

(i)	interior space from exterior space,

(ii)	interior space from the ground, and

(iii)	environmentally dissimilar interior spaces, and

(b)	site conditions that may affect moisture loading on building elements that separate interior space from exterior space, and interior space from the ground.

5.1.3. Definitions

5.1.3.1.  Reserved

5.1.4. Environmental Separation Requirements

5.1.4.1.  Resistance to Environmental Loads

(1)  Building components and assemblies that separate dissimilar environments shall

(a)	be designed to have sufficient capacity and integrity to resist or accommodate the environmental loads and effects of those loads, having regard to

(i)	the intended use of the building, and

(ii)	the environment to which the components and assemblies are subject, and

(b)	satisfy the requirements of this Part.

5.1.4.2.  Resistance to Deterioration

(1)  Except as provided in Sentence (2), materials that comprise building components and assemblies that separate dissimilar environments shall be

(a)	compatible with adjoining materials, and

(b)	resistant to any mechanisms of deterioration which would be reasonably expected, given the nature, function and exposure of the materials.

(2)  Material compatibility and deterioration resistance are not required where it can be shown that incompatibility or uncontrolled deterioration will not adversely affect any of

(a)	the health or safety of building users,

(b)	the intended use of the building, or

(c)	the operation of building services.

5.1.5. Other Requirements

5.1.5.1.  Requirements in Other Parts of the Code

(1)  Acoustical, structural and fire safety requirements shall comply with other Parts of the Code.

Section 5.2. Loads and Procedures

5.2.1. Environmental Loads

5.2.1.1.  Exterior Environmental Loads

(1)  Except as provided in Sentences (2) and (3), climatic loads shall be determined according to Section 2.5.

(2)  Except as provided in Sentence (3), below ground exterior environmental loads not described in Section 2.5. shall be determined from existing geological and hydrological data or from site tests.

(3)  Where local design and construction practice has shown soil temperature analysis to be unnecessary, soil temperatures need not be determined.

5.2.1.2.  Interior Environmental Loads

(1)  Interior environmental loads shall be derived from the intended use of the space.

5.2.2. Procedures

5.2.2.1.  Calculations

(1)  Heat, air and moisture transfer calculations shall conform to good engineering practice such as described in the ASHRAE Fundamentals Handbook 1993.

(2)  For the purposes of any analysis conducted to indicate conformance to the thermal resistance levels required in Article 5.3.1.2., soil temperatures shall be determined based on annual average soil temperature, seasonal amplitude of variation and attenuation of variation with depth.

(3)  Wind load calculations shall conform to Subsection 4.1.8.

Section 5.3. Heat Transfer

5.3.1. Thermal Resistance of Assemblies

5.3.1.1.  Required Resistance to Heat Transfer

(1)  Except as provided in Sentence (2), where a building component or assembly will be subjected to an intended temperature differential, the component or assembly shall include materials to resist heat transfer in accordance with the remainder of this Subsection.

(2)  The installation of materials to resist heat transfer in accordance with the remainder of this Subsection is not required where it can be shown that uncontrolled heat transfer will not adversely affect any of

(a)	the health or safety of building users,

(b)	the intended use of the building, or

(c)	the operation of building services.

5.3.1.2.  Properties to Resist Heat Transfer

(1)  Materials and components installed to provide the required resistance to heat transfer shall provide sufficient resistance, for the interior and exterior design temperatures

(a)	to minimize surface condensation on the component or assembly,

(b)	in conjunction with other materials and components in the assembly, to minimize condensation within the component or assembly, and

(c)	in conjunction with systems installed for space conditioning, to meet the interior design thermal conditions for the intended occupancy.

(2)  Except as provided in Sentence (3), where materials or components are installed to provide the required resistance to heat transfer and are covered in the scope of the standards listed below, the materials and components shall conform to the requirements of the respective standards

(a)	CAN/CGSB-12.8-M, “Insulating Glass Units”,

(b)	CAN/CGSB-51.20-M, “Thermal Insulation, Polystyrene, Boards and Pipe Covering”,

(c)	CGSB 51-GP-21M, “Thermal Insulation, Urethane and Isocyanurate, Unfaced”,

(d)	CAN/CGSB-51.23, “Spray-Applied Rigid Polyurethane Cellular Plastic Thermal Insulation”,

(e)	CAN/CGSB-51.25-M, “Thermal Insulation, Phenolic, Faced”,

(f)	CAN/CGSB-52.26-M, “Thermal Insulation, Urethane and Isocyanurate, Boards, Faced”,

(g)	CGSB 51-GP-27-M, “Thermal Insulation, Polystyrene, Loose Fill”,

(h)	CGSB 51-GP-60-M, “Cellulose Fibre Loose Fill Thermal Insulation”,

(i)	CAN/CGSB-82.1-M, “Sliding Doors”,

(j)	CAN/CGSB-82.5-M, “Insulated Steel Doors”,

(k)	CSA A101-M, “Thermal Insulation, Mineral Fibre, for Buildings”, or

(l)	CAN/CSA-A247-M, “Insulating Fibreboard”.

(3)  The requirements for flame-spread ratings contained in the standards listed in Sentence (2) need be applied only as required in Part 3.

(4)  Except as provided in Sentence (5), all metal-framed glazed assemblies separating interior conditioned space from interior unconditioned space or exterior space shall incorporate a thermal break to minimize condensation.

(5)  Metal-framed glazed assemblies need not comply with Sentence (4) where these assemblies are

(a)	storm windows or doors, or

(b)	windows or doors which are required to have a fire-resistance rating.

5.3.1.3.  Location and Installation of Materials Providing Thermal Resistance

(1)  Where a material required by Article 5.3.1.1. is intersected by a building assembly, penetrated by a high conductance component or interrupted by expansion, control or construction joints, and where condensation is likely to occur at these intersections, penetrations or interruptions, materials providing thermal resistance shall be positioned so as to minimize condensation at these locations.

(2)  Materials providing required thermal resistance shall have sufficient inherent resistance to air flow or be positioned in the assembly so as to prevent convection air flow through and around the material.

(3)  Spray-in-place polyurethane insulation shall be installed in accordance with the requirements of CAN/CGSB-51.39, “Spray Application of Rigid Polyurethane Cellular Plastic Thermal Insulation for Building Construction”.

Section 5.4. Air Leakage

5.4.1. Air Barrier Systems

5.4.1.1.  Required Resistance to Air Leakage

(1)  Except as provided in Sentence (2), where a building component or assembly separates interior conditioned space from exterior space, interior space from the ground, or environmentally dissimilar interior spaces, the component or assembly shall contain an air barrier system.

(2)  An air barrier system is not required where it can be shown that uncontrolled air leakage will not adversely affect any of

(a)	the health or safety of building users,

(b)	the intended use of the building, or

(c)	the operation of building services.

5.4.1.2.  Air Barrier System Properties

(1)  Except as provided in Sentence (2), sheet and panel type materials intended to provide the principal resistance to air leakage shall have an air leakage characteristic not greater than 0.02 L/(s∙m2) measured at an air pressure difference of 75 Pa.

(2)  The air leakage limit specified in Sentence (1) is permitted to be increased where it can be shown that the higher rate of leakage will not adversely affect any of

(a)	the health or safety of building users,

(b)	the intended use of the building, or

(c)	the operation of building services.

(3)  Except as provided in Sentence (6), where components of the air barrier system are covered in the scope of the standards listed below, the components shall conform to the requirements of the respective standards

(a)	CAN/CGSB-63.14-M, “Plastic Skylights”,

(b)	CAN/CGSB-82.1-M, “Sliding Doors”,

(c)	CAN/CGSB-82.5-M, “Insulated Steel Doors”, or

(d)	CAN/CSA-A440-M, “Windows”.

(4)  Skylights not covered in the scope of CAN/CGSB-63.14-M, “Plastic Skylights” shall conform to the performance requirements of that standard.

(5)  Except as provided in Sentence (6), windows and sliding doors covered in the scope of CAN/CGSB-82.1-M, “Sliding Doors”, and CAN/CSA-A440-M, “Windows”, and installed as components in an air barrier system shall conform at least to the airtightness requirements in CAN/CSA-A440.1-M, “User Selection Guide to CAN/CSA-A440-M, Windows”.

(6)  Where a wired glass assembly is installed as a component in an air barrier system in a required fire separation, the assembly need not conform to CAN/CSA-A440-M, “Windows” or CAN/CSA-A440.1-M, “User Selection Guide to CAN/CSA-A440-M, Windows”.

(7)  The air barrier system shall be continuous

(a)	across construction, control and expansion joints,

(b)	across junctions between different building assemblies, and

(c)	around penetrations through the building assembly.

(8)  An air barrier system installed in an assembly subject to wind load, and other elements of the separator that will be subject to wind load, shall transfer that load to the structure.

(9)  Except as provided in Sentence (11), an air barrier system installed in an assembly subject to wind load shall be designed and constructed to resist 100% of the specified wind load as determined in Subsection 4.1.8.

(10)  Except as provided in Sentence (11), deflections of the air barrier system and other elements of the separator that will be subject to wind load shall not adversely affect non-structural elements at 1.5 times the specified wind load.

(11)  Where it can be shown by test or analysis that an air barrier system installed in an assembly will be subject to less than 100% of the specified wind load

(a)	the air barrier system is permitted to be designed and constructed to resist 1.5 times the lesser load, and

(b)	deflections of the air barrier system and other elements of the separator that will be subject to wind load shall not adversely affect non-structural elements at 1.5 times the lesser load.

Section 5.5. Vapour Diffusion

5.5.1. Vapour Barriers

5.5.1.1.  Required Vapour Barrier

(1)  Except as provided in Sentence (2), where a building component or assembly will be subjected to a temperature differential and a differential in water vapour pressure, the component or assembly shall include a vapour barrier.

(2)  A vapour barrier is not required where it can be shown that uncontrolled vapour diffusion will not adversely affect any of

(a)	the health or safety of building users,

(b)	the intended use of the building, or

(c)	the operation of building services.

5.5.1.2.  Vapour Barrier Properties and Installation

(1)  The vapour barrier shall have sufficiently low permeance and shall be positioned in the building component or assembly so as to

(a)	minimize moisture transfer by diffusion, to surfaces within the assembly that would be cold enough to cause condensation at the design temperature and humidity conditions, or

(b)	reduce moisture transfer by diffusion, to surfaces within the assembly that would be cold enough to cause condensation at the design temperature and humidity conditions, to a rate that will not allow sufficient accumulation of moisture to cause deterioration or otherwise adversely affect any of

(i)	the health or safety of building users,

(ii)	the intended use of the building, or

(iii)	the operation of building services.

(2)  Where materials installed to provide the required resistance to vapour diffusion are covered in the scope of the standards listed below, the materials shall conform to the requirements of the respective standards

(a)	CAN/CGSB-51.33-M, “Vapour Barrier Sheet, Excluding Polyethylene, for Use in Building Construction”, and

(b)	CAN/CGSB-51.34-M, “Vapour Barrier, Polyethylene Sheet for Use in Building Construction”.

(3)  Coatings applied to gypsum wallboard to provide required resistance to vapour diffusion shall be shown to conform with the requirements of Sentence (1) when tested in accordance with CAN/CGSB-1.501-M, “Method for Permeance of Coated Wallboard”.

(4)  Coatings applied to materials other than gypsum wallboard to provide required resistance to vapour diffusion shall be shown to conform with the requirements of Sentence (1) when tested in accordance with ASTM E96, “Test Methods for Water Vapour Transmission of Materials” by the desiccant method (dry cup).

Section 5.6. Precipitation

5.6.1. Protection from Precipitation

5.6.1.1.  Required Protection from Precipitation

(1)  Except as provided in Sentence (2), where a building component or assembly is exposed to precipitation, the component or assembly shall

(a)	minimize ingress of precipitation into the component or assembly, and

(b)	prevent ingress of precipitation into interior space.

(2)  Protection from ingress of precipitation is not required where it can be shown that such ingress will not adversely affect any of

(a)	the health or safety of building users,

(b)	the intended use of the building, or

(c)	the operation of building services.

5.6.1.2.  Protective Material and Component Properties

(1)  Where materials or components applied to sloped or horizontal assemblies are installed to provide required protection from precipitation and are covered in the scope of the standards listed below, the materials or components shall conform to the requirements of the respective standards

(a)	ASTM-D2178, “Asphalt Glass Felt Used in Roofing and Waterproofing”,

(b)	CAN/CGSB-37.4-M, “Fibrated, Cutback Asphalt, Lap Cement for Asphalt Roofing”,

(c)	CAN/CGSB-37.5-M, “Cutback Asphalt Plastic Cement”,

(d)	CAN/CGSB-37.8-M, “Asphalt, Cutback, Filled, for Roof Coating”,

(e)	CGSB 37-GP-9Ma, “Primer, Asphalt, Unfilled, for Asphalt Roofing, Dampproofing and Waterproofing”,

(f)	CGSB 37-GP-21M, “Tar, Cutback, Fibrated, for Roof Coating”,

(g)	CAN/CGSB-37.50-M, “Hot Applied, Rubberized Asphalt for Roofing and Waterproofing”,

(h)	CGSB 37-GP-52M, “Roofing and Waterproofing Membrane, Sheet Applied, Elastomeric”,

(i)	CGSB 37-GP-54M, “Roofing and Waterproofing Membrane, Sheet Applied, Flexible, Polyvinyl Chloride”,

(j)	CGSB 37-GP-56M, “Membrane, Modified, Bituminous, Prefabricated, and Reinforced for Roofing”,

(k)	CGSB 37-GP-64M, “Mat Reinforcing, Fibrous Glass, for Membrane Waterproofing Systems and Built-Up Roofing”,

(l)	CGSB 37-GP-6M, “Sheets, Thermosetting Polyester Plastics, Glass Fibre Reinforced”,

(m)	CAN2-51.32-M, “Sheathing, Membrane, Breather Type”,

(n)	CAN/CGSB-63.14-M, “Plastic Skylights”,

(o)	CSA A123.1-M, “Asphalt Shingles Surfaced with Mineral Granules”,

(p)	CSA A123.2-M, “Asphalt Coated Roofing Sheets”,

(q)	CSA A123.3-M, “Asphalt or Tar Saturated Roofing Felt,”

(r)	CSA A123.4-M, “Bitumen for Use in Construction of Built-up Roof Coverings and Dampproofing and Waterproofing Systems”,

(s)	CSA A123.5-M, “Asphalt Shingles Made from Glass Felt and Surfaced with Mineral Granules”,

(t)	CSA A123.17, “Asphalt-Saturated Felted Glass-Fibre Mat for Use in Construction of Built-up Roofs”,

(u)	CSA-A220.0-M, “Performance of Concrete Roof Tiles”,

(v)	CSA-0118.1-M, “Western Red Cedar Shingles and Shakes” not less than No. 2 grade, or

(w)	CSA-0118.2-M, “Eastern White Cedar Shingles” not less than B grade.

(2)  Skylights that are not covered in the scope of CAN/CGSB-63.14-M, “Plastic Skylights” shall conform to the performance requirements of that standard.

(3)  Except as provided in Sentence (5), where materials or components applied to vertical assemblies are installed to provide required protection from precipitation and are covered in the scope of the standards listed below, the materials or components shall conform to the requirements of the respective standards

(a)	ASTM C212, “Structural Clay Facing Tile”,

(b)	CAN/CGSB-11.3-M, “Hardboard” types 1, 2 or 5 when not factory finished,

(c)	CAN/CGSB-11.5-M, “Hardboard, Precoated, Factory-Finished, for Exterior Cladding”,

(d)	CAN/CGSB-34.4-M, “Siding, Asbestos-Cement, Shingles and Clapboards”,

(e)	CAN/CGSB-34.5-M, “Sheets, Asbestos-Cement, Corrugated”,

(f)	CAN/CGSB-34.14-M, “Sheets, Asbestos-Cement, Decorative”,

(g)	CAN/CGSB-34.16-M, “Sheets, Asbestos-Cement, Flat, Fully Compressed”,

(h)	CAN/CGSB-34.17-M, “Sheets, Asbestos-Cement, Flat, Semi-Compressed”,

(i)	CAN/CGSB-34.21-M, “Panels, Sandwich, Asbestos-Cement with Insulating Cores”,

(j)	CGSB 41-GP-24Ma, “Siding, Soffits and Fascia, Rigid Vinyl”,

(k)	CAN/CGSB-82.1-M, “Sliding Doors”,

(l)	CAN/CGSB-82.5-M, “Insulated Steel Doors”,

(m)	CAN/CGSB-93.1-M, “Sheet, Aluminum Alloy, Prefinished, Residential”,

(n)	CAN/CGSB-93.2-M, “Prefinished Aluminum Siding, Soffits and Fascia for Residential Use”,

(o)	CAN/CGSB-93.3-M, “Prefinished Galvanized and Aluminum-Zinc Alloy Steel Sheet for Residential Use”,

(p)	CAN/CGSB-93.4-M, “Galvanized and Aluminum-Zinc Alloy Coated Steel Siding, Soffits and Fascia, Prefinished, Residential”,

(q)	CSA-A371, “Masonry Construction for Buildings”, Section 4,

(r)	CAN/CSA-A440-M, “Windows”,

(s)	CSA O115-M, “Hardwood and Decorative Plywood”,

(t)	CSA O118.1-M, “Western Red Cedar Shingles and Shakes” with shakes not less than No. 1 grade and shingles not less than No. 2 grade, except that No. 3 grade may be used for undercoursing,

(u)	CSA O118.2-M, “Eastern White Cedar Shingles” not less than B (clear) grade except that C grade may be used for undercoursing,

(v)	CSA O121-M, “Douglas Fir Plywood”,

(w)	CSA O151-M, “Canadian Softwood Plywood”,

(x)	CSA O153, “Poplar Plywood”,

(y)	CAN/CSA-O325.0, “Construction Sheathing”, or

(z)	CAN/CSA-O437.0, “OSB and Waferboard”.

(4)  Except as provided in Sentence (5), windows and sliding doors exposed to the exterior and covered in the scope of CAN/CSA-A440-M, “Windows” or CAN/CGSB-82.1-M, “Sliding Doors” shall conform at least to the watertightness requirements in CAN/CSA-A440.1-M, “User Selection Guide to CAN/CSA-A440-M Windows”.

(5)  Where a wired glass assembly in a required fire separation is exposed to the exterior, the assembly need not conform to CAN/CSA-A440-M, “Windows” or CAN/CSA-A440.1-M, “User Selection Guide to CAN/CSA-A440-M Windows”.

5.6.1.3.  Installation of Protective Materials

(1)  Where a material applied to a sloped or horizontal assembly is installed to provide required protection from precipitation and its installation is covered in the scope of one of the standards listed below, installation shall conform to the requirements of the respective standard

(a)	CAN/CGSB 37.51-M, “Application of Hot Applied Rubberized Asphalt for Roofing and Waterproofing”,

(b)	CGSB 37-GP-55M, “Application of Sheet Applied Flexible Polyvinyl Chloride Roofing Membrane”,

(c)	CAN3-A123.51-M, “Asphalt Shingle Application on Roof Slopes 1:3 and Steeper”, or

(d)	CAN3-A123.52-M, “Asphalt Shingle Application on Roof Slopes 1:6 to less than 1:3”.

(2)  Protective materials applied to sloped or horizontal assemblies shall be installed to resist wind-uplift loads determined according to Subsection 4.1.8.

(3)  Where masonry applied to vertical assemblies is installed to provide required protection from precipitation, installation shall conform to the requirements of CSA-A371, “Masonry Construction for Buildings”.

(4)  Where protective materials applied to assemblies are installed to provide required protection from precipitation, the materials shall be installed to shed precipitation or otherwise minimize its entry into the assembly and prevent its penetration through the assembly.

5.6.2. Sealing, Drainage, Accumulation and Disposal

5.6.2.1.  Sealing and Drainage

(1)  Except as provided in Sentence (2), materials, components, assemblies, joints in materials, junctions between components and junctions between assemblies exposed to precipitation shall be

(a)	sealed to prevent ingress of precipitation, or

(b)	drained to direct precipitation to the exterior.

(2)  Sealing or drainage are not required where it can be shown that the omission of sealing and drainage will not adversely affect any of

(a)	the health or safety of building users,

(b)	the intended use of the building, or

(c)	the operation of building services.

5.6.2.2.  Accumulation and Disposal

(1)  Where water, snow or ice can accumulate on a building, provision shall be made to minimize the likelihood of hazardous conditions arising from such accumulation.

(2)  Where precipitation can accumulate on sloped or horizontal assemblies, provision shall be made for drainage conforming with Section 7.4.

(3)  Where downspouts are provided and are not connected to a sewer, provisions shall be made to

(a)	divert the water from the building,

(b)	prevent soil erosion, and

(c)	minimize icing hazards.

(4)  Junctions between vertical assemblies, and sloped or horizontal assemblies, shall be designed and constructed to minimize the flow of water from the sloped or horizontal assembly onto the vertical assembly.

5.6.2.3.  Solar Collector Systems

(1)  A solar collector system is permitted to be installed above roofing materials conforming to Sentence 5.6.1.2.(1).

Section 5.7. Surface Water

5.7.1. Protection from Surface Water

5.7.1.1.  Prevention of Accumulation and Ingress

(1)  Except as provided in Sentence (2), the building shall be located, the building site graded, catch basins installed, or foundation walls constructed so that surface water will not

(a)	accumulate against or enter into the building, or

(b)	damage moisture-susceptible materials.

(2)  Buildings specifically designed to accommodate accumulation of water at the building or water ingress need not comply with Clause (1)(a).

Section 5.8. Moisture in the Ground

5.8.1. Foundation and Floor Drainage

5.8.1.1.  Required Drainage

(1)  Except where a wall or floor is subject to continuous hydrostatic pressure, or unless it can be shown to be unnecessary, the bottom of every exterior foundation wall and every floor-on-ground shall be provided with drainage.

5.8.1.2.  Drainage Materials and Installation

(1)  Drainage shall be designed and installed to accommodate the drainage load.

5.8.2. Protection from Moisture in the Ground

5.8.2.1.  Required Moisture Protection

(1)  Except as provided in Sentence (2), where a building element separates interior space from the ground, materials, components or assemblies shall be installed to prevent moisture transfer into the space.

(2)  Materials, components or assemblies need not be installed to prevent moisture transfer from the ground where it can be shown that such transfer will not adversely affect any of

(a)	the health or safety of building users,

(b)	the intended use of the building, or

(c)	the operation of building services.

5.8.2.2.  Protective Material and Component Properties

(1)  Except where it can be shown that lesser protection will not lead to adverse conditions, or as provided in Article 5.8.2.3., materials and components installed to provide required moisture protection shall conform to the requirements of this Article.

(2)  Except as provided in Sentence (3), materials installed to provide required moisture protection shall be capable of bridging

(a)	construction, control and expansion joints,

(b)	junctions between different building assemblies, and

(c)	junctions between building assemblies and elements penetrating building assemblies.

(3)  Where the required moisture protection material is not capable of bridging construction, control and expansion joints, those joints shall be designed to maintain the continuity of the moisture protection.

(4)  Moisture protection materials and components shall have sufficiently low water permeance to resist moisture loads.

(5)  Moisture protection shall be designed and constructed to resist design hydrostatic pressures as determined in accordance with Section 4.2.

(6)  Where materials installed to provide the required resistance to moisture transfer are covered in the scope of the standards listed below, the materials shall conform to the requirements of the respective standards

(a)	CAN/CGSB-37.2-M, “Emulsified Asphalt, Mineral Colloid Type, Unfilled, for Dampproofing and Waterproofing and for Roof Coatings”,

(b)	CGSB 37-GP-9Ma, “Primer, Asphalt for Asphalt Roofing, Dampproofing and Waterproofing”,

(c)	CAN/CGSB-37.16-M, “Filled Cutback Asphalt for Dampproofing and Waterproofing”,

(d)	CAN/CGSB-37.50-M, “Hot Applied Rubberized Asphalt for Roofing and Waterproofing”,

(e)	CGSB 37-GP-52M, “Roofing and Waterproofing Membrane, Sheet Applied, Elastomeric”,

(f)	CGSB 37-GP-54M, “Roofing and Waterproofing Membrane, Sheet Applied, Flexible, Polyvinyl Chloride”,

(g)	CGSB 37-GP-56M, “Membrane, Modified, Bituminous, Prefabricated and Reinforced for Roofing”, or

(h)	CSA A123.4-M, “Bitumen for Use in Construction of Built-up Roof Coverings and Dampproofing and Waterproofing Systems”.

(7)  Except as provided in Sentence (8), materials covered in the scope of the standards listed below shall not be installed to provide the required resistance to moisture transfer

(a)	CGSB 37-GP-6Ma, “Asphalt, Cutback, Unfilled for Dampproofing”, or

(b)	CGSB 37-GP-18Ma, “Tar, Cutback, Unfilled for Dampproofing”.

(8)  Where the substrate is cast-in-place concrete, and a drainage layer is installed between the building assembly and the soil, and the assembly will not be subject to hydrostatic pressure

(a)	materials and components installed to provide the required resistance to moisture transfer need not conform with Sentences 5.8.2.2.(1) to (5), and

(b)	materials covered in the scope of

(i)	CGSB 37-GP-6Ma, “Asphalt, Cutback, Unfilled for Dampproofing”, or

(ii)	CGSB 37-GP-18Ma, “Tar, Cutback, Unfilled for Dampproofing”,

are permitted to be installed to provide the required resistance to moisture transfer where those materials conform to the requirements of the standards.

5.8.2.3.  Installation of Moisture Protection

(1)  Except as provided in Sentence (2), where materials are installed to provide the required resistance to moisture transfer and their installation is covered in the scope of the standards listed below, installation shall conform to the waterproofing requirements of the respective standards

(a)	CAN/CGSB-37.3-M, “Application of Emulsified Asphalts for Dampproofing or Waterproofing”,

(b)	CGSB 37-GP-36M, “Application of Filled Cutback Asphalts for Dampproofing and Waterproofing”,

(c)	CGSB 37-GP-37M, “Application of Hot Asphalt for Dampproofing or Waterproofing”, or

(d)	CAN/CGSB-37.51-M, “Application of Hot Applied Rubberized Asphalt for Roofing and Waterproofing”.

(2)  Where the substrate is cast-in-place concrete, and a drainage layer is installed between the building assembly and the soil, and the assembly will not be subject to hydrostatic pressure

(a)	materials and components installed to provide the required resistance to moisture transfer and whose installation is covered in the scope of the standards listed in Sentence (1), are permitted to be installed in conformance with the dampproofing requirements of the standards listed in Sentence (1), or

(b)	materials installed to provide the required resistance to moisture transfer and whose installation is covered in the scope of the standards listed below, shall be installed in conformance with the requirements of the respective standards:

(i)	CGSB 37-GP-12Ma, “Application of Unfilled Cutback Asphalt for Dampproofing”, or

(ii)	CAN/CGSB 37.22-M, “Application of Unfilled Cutback Tar Foundation Coating for Dampproofing”.

O. Reg. 403/97, Part 5; O. Reg. 349/06, s. 14.

Part 6
Heating, Ventilating and Air-Conditioning

| Section | 6.1. | General |
| --- | --- | --- |
|  | 6.1.1. | Application |
|  | 6.1.2. | Definitions |
|  | 6.1.3. | Plans and Specifications |
| Section | 6.2. | Design and Installation |
|  | 6.2.1. | General |
|  | 6.2.2. | Ventilation |
|  | 6.2.3. | Air Duct Systems |
|  | 6.2.4. | Air Ducts for Low Capacity Systems |
|  | 6.2.5. | Heating Appliances, General |
|  | 6.2.5A. | Carbon Monoxide Detectors |
|  | 6.2.6. | Incinerators |
|  | 6.2.7. | Unit Heaters |
|  | 6.2.8. | Radiators and Convectors |
|  | 6.2.9. | Piping For Heating and Cooling Systems |
|  | 6.2.10. | Refrigerating Systems and Equipment for Air-Conditioning |
|  | 6.2.11. | Storage Bins |
| Section | 6.3. | Chimneys and Venting Equipment |
|  | 6.3.1. | General |

Part 6
Heating, Ventilating and Air-Conditioning

Section 6.1. General

6.1.1. Application

6.1.1.1.  Scope

(1)  The scope of this Part shall be as described in Section 2.1.

(2)  Where the method of operation of an existing heating, ventilating or air-conditioning system is altered, the repair, adjustment or component replacements that change the capacity or extent of safety of the system shall conform to this Code.

6.1.1.2.  Application

(1)  This Part applies to systems and equipment for heating, ventilating and air-conditioning services.

6.1.2. Definitions

6.1.2.1.  Reserved

6.1.3. Plans and Specifications

6.1.3.1.  Reserved

Section 6.2. Design and Installation

6.2.1. General

6.2.1.1.  Good Engineering Practice

(1)  Heating, ventilating and air-conditioning systems, including related mechanical refrigeration systems, shall be designed, constructed and installed to conform to good engineering practice appropriate to the circumstances such as described in

(a)	the ASHRAE Handbooks as follows:

(i)	1993 Fundamentals,

(ii)	1994 Refrigeration,

(iii)	1995 HVAC Applications,

(iv)	1996 HVAC Systems and Equipment, and

(v)	ASHRAE/IES 90.1-1989, “Energy Efficient Design of New Buildings Except Lowrise Residential Buildings”,

(b)	the CAN/CSA-F280-M90, “Determining the Required Capacity of Residential Space Heating and Cooling Appliances”, and the outside winter design temperatures shall conform to Subsection 2.5.1. of this Code,

(c)	the CAN/CSA-F326-M91, “Residential Mechanical Ventilation Requirements”,

(d)	the NFPA Fire Codes (1996 Publication),

(e)	the HRAI Digest 1992,

(f)	the Hydronics Institute Manuals,

(g)	the SMACNA Manuals,

(h)	the Industrial Ventilation Manual, 22nd Edition 1995, published by the American Conference of Governmental Industrial Hygienists,

(i)	CAN/CSA-Z317.2, “Special Requirements for HVAC Systems in Health Care Facilities”,

(j)	the Unified Canadian Guideline for Integrated (Combined) Heating Systems, and

(k)	the Model National Energy Code for Buildings, 1997.

6.2.1.2.  Design Indoor Air Temperatures

(1)  Buildings classified as Group B, Division 2 or 3 occupancies or Group C residential occupancies that are intended for use in the winter months on a continuing basis shall be insulated and be equipped with heating facilities that are capable of maintaining an indoor air temperature of 22°C at the outside winter design temperature referred to in Article 6.2.1.8.

(2)  All other buildings intended for occupancy in the winter months on a continuing basis should be insulated and shall be equipped with heating facilities to maintain a minimum indoor air temperature of 18°C or commensurate with the use of the building at the outside winter design temperature described in Article 6.2.1.8.

6.2.1.3.  Reserved

6.2.1.4.  Structural Movement

(1)  Mechanical systems and equipment shall be designed and installed to accommodate the maximum relative structural movement provided for in the construction of the building.

6.2.1.5.  Installation Standards

(1)  The installation of solid fuel-burning appliances for central heating systems shall comply with CAN/CSA-B365-M, “Installation Code for Solid Fuel-Burning Appliances and Equipment” and the manufacturer’s installation instructions.

(2)  The solid fuel-fired appliances in Sentence (1) shall conform to CAN/CSA-B366.1-M, “Solid Fuel-Fired Central Heating Appliances”.

(3)  The design and installation of ground and water source heat pumps shall conform to CAN/CSA-C445-M, “Design and Installation of Earth Energy Heat Pump Systems for Residential and Other Small Buildings” where

(a)	the maximum standard rated output is 35 kW per dwelling unit for residential applications, or

(b)	small building applications serve a heated floor space area not greater than 1 400 m2.

(4)  The design and installation of ground and water source heat pumps shall conform to CAN/CSA-C447-M, “Design and Installation of Earth Energy Heat Pump Systems for Commercial and Institutional Buildings” where the heated floor space is greater than 1 400 m2.

(5)  The design and installation of Solid fuel-burning stoves, ranges and space heaters, including the requirements for combustion air, shall conform to the requirements of CAN/CSA-B365-M, “Installation Code for Solid Fuel-Burning Appliances and Equipment” and the manufacturer’s installation instructions.

6.2.1.6.  Fireplaces

(1)  Fireplaces shall conform to the requirements of Section 9.22.

6.2.1.7.  Heat Recovery Ventilators

(1)  Except as provided in Sentence (2), heat recovery ventilators with rated capacities of not less than 25 L/s and not more than 200 L/s shall be installed in accordance with Article 9.32.3.11.

(2)  Where electric space heating, other than forced-air electric heating system, is provided in buildings of residential occupancy within the scope of Part 9, the mechanical ventilation system shall include heat recovery ventilators designed to provide the greater of

(a)	the minimum rated efficiency required by the Ontario Energy Efficiency Act, or

(b)	a minimum 55% sensible heat recovery efficiency when tested to the low temperature thermal and ventilation performance test method set out in CAN/CSA-C439-M, “Standard Methods of Test for Rating the Performance of Heat Recovery Ventilators”, at a Station 1 test temperature of -25°C at an air flow not less than 30 L/s.

6.2.1.8.  Outside Design Conditions

(1)  The outside conditions to be used in designing heating, ventilating and air-conditioning systems shall be determined in conformance with Subsection 2.5.1.

6.2.1.9.  Installation — General

(1)  Equipment requiring periodic maintenance and forming part of a heating, ventilating or air-conditioning system shall be installed with provision for access for inspection, maintenance, repair and cleaning.

(2)  Mechanical equipment shall be protected with guards to prevent injury to the public or maintenance staff.

(3)  Equipment forming part of a heating or air-conditioning system that may be adversely affected by freezing temperatures and that is located in an unheated area shall be protected from freezing.

6.2.1.10.  Expansion, Contraction and System Pressure

(1)  Heating and cooling systems shall be designed to allow for expansion and contraction of the heat transfer fluid and to maintain the system pressure within the rated working pressure limits of all components of the system.

6.2.1.11.  Asbestos

(1)  Asbestos shall not be used in air distribution systems or equipment in a form or in a location where asbestos fibres could enter the air supply or return systems.

6.2.1.12.  Access Openings

(1)  Any covering of an access opening through which a person could enter shall be openable from the inside without the use of keys where there is a possibility of the opening being accidentally closed while the system or equipment is being serviced.

6.2.1.13.  Combustible Tubing

(1)  Combustible tubing for pneumatic controls may be used in buildings required to be of noncombustible construction providing it has an outside diameter not exceeding 10 mm.

6.2.2. Ventilation

6.2.2.1.  Required Ventilation

(1)  Except as provided in Sentence (3), all rooms and spaces in buildings shall be ventilated in accordance with this Part.

(2)  Except in storage garages and repair garages covered by Article 6.2.2.3., the rates at which outdoor air is supplied to rooms and spaces in buildings by ventilation systems shall be not less than the rates required by ASHRAE Standard 62, “Ventilation for Acceptable Indoor Air Quality”.

(3)  Self-contained mechanical ventilation systems, serving only one dwelling unit which conform to the requirements of Subsection 9.32.3. shall be considered to satisfy the requirements of this Article.

(4)  Live/work units shall be mechanically ventilated in accordance with the requirement of Sentence (1).

6.2.2.2.  Natural Ventilation

(1)  The ventilation required by Article 6.2.2.1. shall be provided by mechanical ventilation except that it can be provided by natural ventilation or a combination of natural and mechanical ventilation in

(a)	buildings of other than residential occupancy having an occupant load of not more than one person per 40 m2 during normal use,

(b)	buildings of industrial occupancy where the nature of the process contained therein permits or requires the use of large openings in the building envelope even during the winter, or

(c)	seasonal buildings not intended to be occupied during the winter.

6.2.2.3.  Ventilation of Storage and Repair Garages

(1)  Except as provided in Sentences (4) and (6), an enclosed storage garage shall have a mechanical ventilation system designed to

(a)	limit the concentration of carbon monoxide to not more than 100 parts per million of air when measured between 900 mm and 1 200 mm from the floor, or

(b)	provide, during operating hours, a continuous supply of outdoor air at a rate of not less than 3.9 L/s for each square metre of floor area.

(2)  Mechanical ventilation systems provided in accordance with Clause (1)(a) shall be controlled automatically by carbon monoxide monitoring devices, located so as to provide full protection throughout the storage garage.

(3)  Mechanical ventilation systems provided in accordance with Sentence (1) shall be designed such that the pressure in the storage garage is less than the pressure in adjoining buildings of other occupancy, or in adjacent portions of the same building having a different occupancy.

(4)  In storage garages subject to the requirements of Sentence (1), where motor vehicles are parked by mechanical means, the ventilation requirements may be reduced by one half.

(5)  Except as provided in Sentence (6), ticket and attendant booths of storage garages shall be pressurized with a supply of outdoor air.

(6)  The requirements of Sentences (1) to (5) shall not apply to open-air storeys in a storage garage.

(7)  A repair garage shall have a mechanical ventilation system designed to limit the exposure of workers to carbon monoxide to below the time weighted average concentration of 35 parts per million for a normal 8 hour workday or 40 hour work week.

(8)  In a repair garage, when a repair bay is not immediately adjacent to an outside garage door opening, a system capable of providing continuous general ventilation of not less than 700 L/s per internal bay shall be provided.

(9)  The general ventilation system described in Sentence (8) shall be designed to

(a)	operate continuously, or

(b)	be controlled automatically by carbon monoxide monitoring devices, located so as to provide full protection throughout the repair garage.

(10)  The general ventilation system described in Sentence (8) is not required when tail pipes of vehicles are directly connected to local mechanical exhaust systems that terminate outdoors.

6.2.2.4.  Air Contaminants

(1)  Air contaminants released within buildings shall be removed insofar as possible at their points of origin and shall not be permitted to accumulate in concentrations greater than permitted in the Industrial Ventilation Manual published by the American Conference of Governmental Industrial Hygienists.

(2)  Systems serving spaces that contain sources of contamination and systems serving other occupied parts of the building but located in or running through spaces that contain sources of contamination shall be designed in such a manner as to prevent spreading of such contamination to other occupied parts of the building.

(3)  Heating, ventilating and air-conditioning systems shall be designed to minimize growth of micro-organisms according to good engineering practice as described in 6.2.1.1.(1).

(4)  Mechanical rooms containing refrigeration equipment shall be ventilated in accordance with CSA B52-M, “Mechanical Refrigeration Code”.

6.2.2.5.  Hazardous Gases, Dusts or Liquids

(1)  Systems serving spaces that contain hazardous gases, dusts or liquids shall be designed, constructed and installed in conformance with the provisions of the Ontario Fire Code made under the Fire Marshals Act, or in the absence of requirements pertinent to such systems in the Ontario Fire Code, to good engineering practice such as is described in the publications of the National Fire Protection Association and in the National Fire Code of Canada 1995.

6.2.2.6.  Commercial Cooking Equipment

(1)  All commercial cooking equipment shall be provided with ventilation systems designed, constructed and installed to conform to NFPA 96, “Ventilation Control and Fire Protection of Commercial Cooking Operations”, except as required by Sentence 3.6.3.1.(1) and Article 3.6.4.2.

6.2.2.7.  Crawl Spaces and Attic or Roof Spaces

(1)  Every crawl space and every attic or roof space shall be ventilated by natural or mechanical means.

6.2.3. Air Duct Systems

6.2.3.1.  Application

(1)  Except as provided in Sentence (2), the design, construction and installation of air duct distribution systems serving heating, ventilating and air-conditioning systems shall conform to this Subsection.

(2)  The requirements of Subsection 6.2.4. apply to individual dwelling units for the design, construction and installation of air duct distribution systems which serve ventilating or air-conditioning systems or which serve heating systems in which the rated heat input does not exceed 120 kW.

6.2.3.2.  Materials in Air Duct Systems

(1)  Except as provided in Sentences (2) to (4) and in Article 3.6.4.3., all ducts, duct connectors, associated fittings and plenums used in air duct systems shall be constructed of steel, aluminum alloy, copper, clay, asbestos-cement or similar noncombustible material.

(2)  Ducts, associated fittings and plenums are permitted to contain combustible material provided they

(a)	conform to the appropriate requirements for Class 1 duct materials in CAN/ULC-S110-M, “Standard Methods of Test for Air Ducts”,

(b)	conform to Article 3.1.5.14. in a building required to be of noncombustible construction,

(c)	conform to Subsection 3.1.9.,

(d)	are not used in horizontal runs in a building required to be of noncombustible construction,

(e)	are not used in vertical runs serving more than 2 storeys in a building required to be of noncombustible construction, and

(f)	are not used in air duct systems in which the air temperature may exceed 120°C.

(3)  Duct sealants shall have a flame-spread rating of not more than 25 and a smoke developed classification of not more than 50.

(4)  Duct connectors that contain combustible materials and that are used between ducts and air outlet units shall

(a)	conform to the appropriate requirements for Class 1 air duct materials in CAN/ULC-S110-M, “Standard Methods of Test for Air Ducts”,

(b)	be limited to 4 m in length,

(c)	be used only in horizontal runs, and

(d)	not penetrate required fire separations.

(5)  Materials in Sentences (1) to (4) which when used in a location where they may be subjected to excessive moisture shall have no appreciable loss of strength when wet and shall be corrosion-resistant.

6.2.3.3.  Connections and Openings in Air Duct Systems

(1)  Air duct systems shall have

(a)	tight-fitting connections throughout, and

(b)	no openings other than those required for proper operation, inspection and maintenance of the system.

(2)  Except for systems that serve one dwelling unit only, access openings shall be provided in duct systems where lint, grease, debris, paper or other combustible material may accumulate in plenums and ducts.

6.2.3.4.  Coverings, Linings, Adhesives and Insulation

(1)  Coverings, linings and associated adhesives and insulation of air ducts, plenums and other parts of air duct systems shall be of noncombustible material when exposed to heated air or radiation from heat sources that would result in the exposed surface exceeding a temperature of 120°C.

(2)  When combustible coverings and linings, including associated adhesives and insulation, are used, they shall have a flame-spread rating of not more than 25 on any exposed surface or any surface that would be exposed by cutting through the material in any direction, and a smoke developed classification of not more than 50, except that the outer covering of ducts, plenums and other parts of air duct systems used within an assembly of combustible construction may have an exposed surface flame-spread rating of not more than 75 and may have a smoke developed classification greater than 50.

(3)  Combustible coverings and linings in Sentence (2) shall not flame, glow, smoulder or smoke when tested in accordance with the method of test in ASTM C411, “Hot-Surface Performance of High-Temperature Thermal Insulation” at the maximum temperature to which the coverings and linings are to be exposed in service.

(4)  Except as provided in Sentence (5), foamed plastic insulation shall not be used as part of an air duct or for insulating an air duct.

(5)  Foamed plastic insulation may be used in a ceiling space that acts as a return air plenum provided the foamed plastic insulation is protected from exposure to the plenum in accordance with Article 3.1.5.11.

(6)  Combustible coverings and linings of ducts, including associated adhesives and insulation, shall be interrupted at the immediate area of operation of heat sources in a duct system, such as electric resistance heaters or fuel-burning heaters or furnaces, and where the duct penetrates a fire separation.

(7)  Linings of ducts shall be installed so that they will not interfere with the operation of volume or balancing dampers, fire dampers, fire stop flaps and other closures.

6.2.3.5.  Underground Ducts

(1)  Underground ducts shall be constructed to provide interior drainage from and access to all low points and shall not be connected directly to a sewer.

6.2.3.6.  Clearances

(1)  The clearances from combustible material and supply plenums, supply ducts, boots and register boxes of heating systems shall conform to the requirements of Subsection 6.2.4.

6.2.3.7.  Fire Dampers

(1)  Fire dampers shall conform to the requirements of Article 3.1.8.9.

6.2.3.8.  Smoke Detector Control

(1)  Air handling systems shall incorporate smoke detector control where required by Article 3.2.4.13.

6.2.3.9.  Exhaust Ducts and Outlets

(1)  Except as provided in Sentence (2), exhaust ducts of nonmechanical ventilating systems serving separate rooms or spaces shall not be combined.

(2)  Exhaust ducts of nonmechanical ventilating systems serving similar occupancies may be combined immediately below the point of final delivery to the outside, such as at the base of a roof ventilator.

(3)  Exhaust ducts of ventilating systems shall have provision for the removal of condensation where this may be a problem.

(4)  Exhaust outlets shall be designed to prevent back draft under wind conditions.

(5)  Except as permitted in Sentence (6), exhaust systems shall discharge directly to the outdoors.

(6)  Exhaust systems are permitted to exhaust into a storage garage provided such systems serve rooms which

(a)	are accessible only from the storage garage, and

(b)	are not served by duct systems serving other parts of the building.

(7)  Exhaust ducts connected to laundry drying equipment shall be independent of other exhaust ducts.

(8)  Except as provided in Sentence (10) and except for self-contained systems serving individual dwelling units, exhaust ducts serving rooms containing water closets, urinals, basins, showers or slop sinks shall be independent of other exhaust ducts.

(9)  Except as provided in Sentence (10) and except for self-contained systems serving individual dwelling units, exhaust ducts serving rooms containing residential cooking equipment shall be independent of other exhaust ducts.

(10)  Two or more exhaust systems described in Sentences (8) and (9) may be interconnected or connected with exhaust ducts serving other areas of the building provided

(a)	the connections are made at the inlet of an exhaust fan, and

(b)	all interconnected systems are equipped with suitable back pressure devices to prevent passage of odours from one system to another when the fan is not in operation.

(11)  Where exhaust ducts containing air from heated spaces pass through or are adjacent to unheated spaces, the ducts shall be insulated to prevent moisture condensation in the ducts in accordance with Sentence 6.2.4.3.(10).

(12)  Except for wash basins (lavatories), the exhaust air provided shall not be less than 24 L/s for each sanitary fixture listed in Sentence (8).

(13)  Except for wash basins (lavatories), sanitary facilities in a food premises shall be mechanically ventilated and shall be capable of exhausting air at the rate of not less than 24 L/s for each sanitary fixture listed in Sentence (14).

(14)  The mechanical ventilation described in Sentence (13) applies to rooms containing water closets, urinals, basins, showers or slop sinks.

6.2.3.10.  Interconnection of Systems

(1)  Except as provided in Sentence 6.2.3.9.(6), air duct systems serving storage garages shall not be interconnected with other parts of the building.

(2)  In a residential occupancy, air from one suite shall not be circulated to any other suite nor to a public corridor or public stairway.

(3)  Except for Sentence 3.3.1.4.(4) and Sentences (4) and (5), a public corridor or corridor serving the public shall not be used as a portion of a supply, return or exhaust air system serving adjoining areas, other than as part of a supply air system serving toilet rooms, bathrooms, shower rooms and similar auxiliary spaces opening directly to the public corridor or corridor used by the public.

(4)  A public corridor may be used as part of an engineered smoke control system.

(5)  Infiltration due to corridor pressurization is permitted into a residential occupancy from a public corridor.

6.2.3.11.  Ducts in Exit Stairways

(1)  Duct penetration of fire separations separating exits from the remainder of the building shall be in accordance with Article 3.4.4.4.

6.2.3.12.  Make-up Air

(1)  In ventilating systems that exhaust air to the outdoors, provision shall be made for the admission of a supply of make-up air in sufficient quantity so that the operation of the exhaust system and other exhaust equipment or combustion equipment is not adversely affected.

6.2.3.13.  Supply, Return, Intake and Exhaust Air Openings

(1)  Supply, return and exhaust air openings in rooms or spaces in buildings when located less than 2 m above the floor shall be protected by grilles having openings of a size that will not allow the passage of a 15 mm diameter sphere.

(2)  Combustible grilles, diffusers and other devices for supply, return and exhaust air openings in rooms shall conform to the flame-spread rating and smoke developed classification requirements for the interior finish of the surface on which they are installed.

(3)  Outdoor air intakes and exhaust outlets at the building exterior shall be designed or located so that the air entering the building system will not contain more contaminants than the normal exterior air of the locality in which the building is situated.

(4)  Exterior openings for outdoor air intakes and exhaust outlets shall be shielded from the entry of snow and rain and shall be fitted with corrosion-resistant screens of mesh having openings not larger than 15 mm, except where experience has shown that climatic conditions require larger openings to avoid icing over of the screen openings.

(5)  Screens required in Sentence (4) shall be accessible for maintenance.

6.2.3.14.  Filters and Odour Removal Equipment

(1)  Air filters for air duct systems shall conform to the requirements for Class 2 air filter units as described in CAN4-S111, “Standard Method of Fire Tests For Air Filter Units”.

(2)  When electrostatic-type filters are used, they shall be installed so as to ensure that the electric circuit is automatically de-energized when filter access doors are opened and in dwelling units when the system circulating fan is not operating.

(3)  When odour removal equipment of the adsorption type is used it shall be

(a)	installed to provide access so that adsorption material can be reactivated or renewed, and

(b)	protected from dust accumulation by air filters installed on the inlet side.

(4)  Facilities for flushing and drainage shall be provided where filters are designed to be washed in place.

6.2.3.15.  Air Washers and Evaporative Cooling Sections or Towers

(1)  The filter and water evaporation medium of every air washer and evaporative cooling section enclosed within a building shall be made of noncombustible material.

(2)  Sumps for air washer and evaporative cooling sections shall be constructed and installed so that they can be flushed and drained.

(3)  Evaporative cooling sections or towers of combustible material located on or outside buildings shall have a clearance of not less than 12 m from sources of ignition such as chimneys or incinerators when the tower exterior construction is noncombustible, and a clearance of not less than 30 m when the tower exterior construction is combustible.

(4)  Evaporative cooling sections or towers, the main structure of which exceeds a volume of 55 m3, shall comply with the requirements of NFPA 214, “Water-Cooling Towers”.

6.2.3.16.  Fans and Associated Air Handling Equipment

(1)  Fans for heating, ventilating and air-conditioning systems shall be located and installed so that their operation

(a)	does not adversely affect the draft required for proper operation of fuel-fired appliances, and

(b)	does not allow the air in the air duct system to be contaminated by air or gases from the boiler-room or furnace-room.

(2)  Fans and associated air handling equipment, such as air washers, filters and heating and cooling units, when installed on the roof or elsewhere outside the building, shall be of a type designed for outdoor use.

6.2.3.17.  Construction and Installation of Ducts and Plenums

(1)  Rectangular panels in plenums and ducts more than 300 mm wide shall be shaped to provide sufficient stiffness.

(2)  Where the installation of heating supply ducts in walls and floors creates a space between the duct and construction material, the space shall be fire stopped with noncombustible material at each end.

(3)  Ducts shall be securely supported by metal hangers, straps, lugs or brackets, except that where zero clearance is permitted, wooden brackets may be used.

(4)  All round duct joints shall be tight-fitting and lapped not less than 25 mm.

(5)  Rectangular duct connections shall be made with S and drive cleats or equivalent mechanical connections.

(6)  Trunk supply ducts shall not be nailed directly to wood members.

(7)  Branch ducts shall be supported at suitable spacings to maintain alignment and prevent sagging.

(8)  Ducts in or beneath concrete slabs-on-ground shall be watertight, corrosion-, decay- and mildew-resistant.

(9)  Where a supply or return duct is not protected by an insulated exterior wall or where the duct is exposed to an unheated space it shall be insulated to prevent condensation.

6.2.3.18.  Connectors

(1)  Vibration isolation connectors in air duct systems shall be noncombustible, except that combustible fabric connectors are permitted provided they

(a)	do not exceed 250 mm in length,

(b)	comply with the flame-resistance requirements of CAN/ULC-S109, “Standard for Flame Tests of Flame-Resistant Fabrics and Films”, and

(c)	are not used in a location where they are exposed to heated air or radiation from heat sources that may cause the exposed surface to exceed a temperature of 120°C.

6.2.3.19.  Tape

(1)  Tape used for sealing joints in air ducts, plenums and other parts of air duct systems shall meet the flame-resistance requirements for fabric in CAN/ULC-S109, “Standard for Flame Tests of Flame-Resistant Fabrics and Films”.

6.2.3.20.  Return-Air System

(1)  The return-air system shall be designed to handle the entire air supply.

(2)  Where any part of a return duct will be exposed to radiation from the furnace heat exchanger or other radiating part within the furnace, such part of a return duct directly above or within 600 mm of the outside furnace casing shall be noncombustible.

(3)  Return ducts serving solid fuel-fired furnaces shall be constructed of noncombustible material.

(4)  Where combustible return ducts are permitted, they shall be lined with noncombustible material below floor registers, at the bottom of vertical ducts and under furnaces having a bottom return.

(5)  The return-air system shall be designed so that the negative pressure from the circulating fan cannot affect the furnace combustion air supply nor draw combustion products from joints or openings in the furnace or flue pipe.

(6)  Return-air inlets shall not be installed in an enclosed room or crawl space that provides combustion air to a fuel-fired appliance.

6.2.4. Air Ducts for Low Capacity Systems

6.2.4.1.  Application

(1)  Except as provided in Sentence (2), the design, construction and installation of air duct distribution systems serving heating, ventilating and air-conditioning systems shall conform to Subsection 6.2.3.

(2)  The requirements of this Subsection apply to individual dwelling units for the design, construction and installation of air duct distribution systems which serve ventilating or air-conditioning systems or which serve heating systems in which the rated heat input does not exceed 120 kW.

6.2.4.2.  Duct Design

(1)  Materials in supply ducts shall conform to Article 6.2.3.2.

(2)  Galvanized steel or aluminum supply ducts shall conform to Table 6.2.4.2.

Table 6.2.4.2.

Minimum Metal Thickness of Ducts

Forming Part of Sentence 6.2.4.2.(2)

| Type of Duct | Maximum Diameter, Mm | Maximum Width or Depth, mm | Minimum metal thickness, mm |  |
| --- | --- | --- | --- | --- |
|  |  |  | Duct Material |  |
|  |  |  | Galvanized Steel Aluminum |  |
| Round ducts serving single dwelling units | 125 or less | — | 0.254 | 0.30 |
| Round | 350 | — | 0.33 | 0.30 |
|  | over 350 | — | 0.41 | 0.41 |
| Rectangular, | — | 350 | 0.33 | 0.30 |
| enclosed | — | over 350 | 0.41 | 0.41 |
| Rectangular, not enclosed, for single dwelling units, with required clearance up to 12 mm | — — | 350 over 350 | 0.33 0.41 | 0.41 0.48 |
| Rectangular, not enclosed, with required clearance of more than 12 mm | — — | 350 over 350 | 0.41 0.48 | 0.41 0.48 |
| Column 1 | 2 | 3 | 4 | 5 |

(3)  The design of fitting for ducts shall conform to SMACNA, “HVAC Duct Construction Standards — Metal and Flexible”, except that metal thickness shall conform to Table 6.2.4.2.

6.2.4.3.  Construction and Installation of Ducts and Plenums

(1)  Rectangular panels in plenums and ducts more than 300 mm wide shall be shaped to provide sufficient stiffness.

(2)  Where the installation of heating supply ducts in walls and floors creates a space between the duct and construction material, the space shall be fire stopped with noncombustible material at each end.

(3)  Ducts shall be securely supported by metal hangers, straps, lugs or brackets, except that where zero clearance is permitted, wooden brackets may be used.

(4)  All round duct joints shall be tight-fitting and lapped not less than 25 mm.

(5)  Rectangular duct connections shall be made with S and drive cleats or equivalent mechanical connections.

(6)  Trunk supply ducts shall not be nailed directly to wood members.

(7)  Branch ducts shall be supported at suitable spacings to maintain alignment and prevent sagging.

(8)  Combustible ducts in concrete slabs-on-ground that are connected to a furnace supply plenum shall be located not closer than 600 mm to that plenum and not less than 600 mm from its connection to a riser or register.

(9)  Ducts in or beneath concrete slabs-on-ground shall be watertight, corrosion-, decay- and mildew-resistant.

(10)  Where a supply or return duct is not protected by an insulated exterior wall or where the duct is exposed to an unheated space it shall be insulated to provide a thermal resistance of not less than RSI 2.1.

6.2.4.4.  Warm-Air Supply Outlets

(1)  In a dwelling unit, a warm-air supply outlet shall be provided in each finished room which is located adjacent to unheated space, exterior air or exterior soil.

(2)  Except as provided in Sentence (3), when a room described in Sentence (1) is located adjacent to exterior walls, such outlets shall be located so as to bathe not less than one exterior wall or window with warm air, except in bathrooms, utility rooms or kitchens, where this may not be practical.

(3)  Where the heating system is also designed to provide ventilation air, ceiling outlets or outlets located high on interior walls may be installed provided the outlets are

(a)	designed for this purpose, and

(b)	installed with diffusers.

(4)  Not less than one warm-air supply outlet shall be provided for each 40 m2 of floor surface area in unfinished basements serving dwelling units, located so as to provide adequate distribution of warm air throughout the basement.

(5)  Except for pipeless furnaces and floor furnaces, the capacity of warm-air supply outlets serving dwelling units shall be not less than the design heat loss from the area served and shall not exceed 3 kW per outlet.

(6)  In basements and heated crawl spaces, the calculated heat gain from the supply ducts and plenum surfaces may be considered in calculating the design heat loss.

(7)  Warm-air supply outlets located in finished areas shall be provided with diffusers and adjustable openings and shall not be located on a furnace plenum.

(8)  The temperature of supply air at the warm-air supply outlets shall not exceed 70°C.

(9)  Air duct systems serving storage garages shall not be interconnected with other parts of the building.

6.2.4.5.  Concrete Slabs-on-Ground

(1)  Warm-air supply systems for buildings of residential occupancy built on concrete slabs-on-ground

(a)	shall be installed in the slab, and

(b)	shall be of the perimeter loop type or radial perimeter type.

6.2.4.6.  Adjustable Dampers and Balance Stops

(1)  All branch supply ducts for residential systems shall be equipped with volume control dampers at the boot to permit balancing or shall be fitted with a diffuser incorporating an adjustable and lockable volume control device which can be set in a fixed position.

6.2.4.7.  Return-Air System

(1)  The return-air system shall be designed to handle the entire air supply.

(2)  Except as provided in Sentences (3) and (4), return ducts shall be constructed of material having a surface flame-spread rating of not more than 150.

(3)  Where any part of a return duct will be exposed to radiation from the furnace heat exchanger or other radiating part within the furnace, such part of a return duct directly above or within 600 mm of the outside furnace casing shall be noncombustible.

(4)  Return ducts serving solid fuel-fired furnaces shall be constructed of noncombustible material.

(5)  Combustible return ducts shall be lined with noncombustible material below floor registers, at the bottom of vertical ducts and under furnaces having a bottom return.

(6)  Spaces between studs and joists used as return ducts shall be separated from the unused portions of such spaces by tight-fitting metal stops or wood blocking.

(7)  A vertical return duct shall have openings to return air on not more than 1 floor.

(8)  A public corridor shall comply with Sentences 6.2.3.10.(3) and (4).

(9)  The return-air system shall be designed so that the negative pressure from the circulating fan cannot affect the furnace combustion air supply nor draw combustion products from joints or openings in the furnace or flue pipe.

(10)  Return-air from a dwelling unit shall not be recirculated to any other dwelling unit.

(11)  Except for floor levels that are less than 900 mm above or below an adjacent floor level which is provided with a return-air inlet, at least one return-air inlet shall be provided in each floor level in a dwelling unit.

(12)  Provision shall be made for the return of air from all rooms by leaving gaps beneath doors, using louvred doors or installing return duct inlets.

6.2.4.8.  Coverings, Linings and Insulation

(1)  Foamed plastic insulation may be used in a ceiling space that acts as a return air plenum provided the foamed plastic insulation is protected from exposure to the plenum in accordance with Article 3.1.5.11.

(2)  Linings of ducts shall be installed so that they will not interfere with the operation of volume or balancing dampers.

6.2.4.9.  Tape

(1)  Tape used for sealing joints in air ducts, plenums and other parts of air duct systems shall meet the flame-resistance requirements for fabric in CAN/ULC-S109, “Standard for Flame Tests of Flame-Resistant Fabrics and Films”.

6.2.4.10.  Clearances of Ducts and Plenums

(1)  Where the plenum clearance is 75 mm or less, the clearance between a supply duct and combustible material shall

(a)	be equal to the required plenum clearance within 450 mm of the plenum, and

(b)	be not less than 12 mm at a distance of 450 mm or more from the plenum, except that this clearance may be reduced to zero beyond a bend or offset in the duct sufficiently large to shield the remainder of the duct from direct radiation from the furnace heat exchanger.

(2)  Where the plenum clearance is more than 75 mm but not more than 150 mm, the clearance between a supply duct and combustible material shall

(a)	be equal to the required plenum clearance within a horizontal distance of 1 800 mm of the plenum, and

(b)	be not less than 12 mm at a horizontal distance of 1 800 mm or more from the plenum, except that this distance may be reduced to zero beyond a bend or offset in the duct sufficiently large to shield the remainder of the duct from direct radiation from the furnace heat exchanger.

(3)  Where the plenum clearance is more than 150 mm, the clearance between a supply duct and combustible material shall

(a)	be equal to the required plenum clearance within a horizontal distance of 1 000 mm of the plenum,

(b)	be not less than 150 mm within a horizontal distance between 1 000 mm and 1 800 mm from the plenum, and

(c)	be not less than 25 mm at a horizontal distance of 1 800 mm or more from the plenum, except that this distance may be reduced to 8 mm beyond a bend or offset in the duct sufficiently large to shield the remainder of the supply duct from direct radiation from the furnace heat exchanger.

(4)  Where a register is installed in a floor directly over a pipeless furnace, a double-walled register box with not less than 100 mm between walls, or a register box with the warm-air passage completely surrounded by the cold-air passage, shall be permitted in lieu of the clearances listed in Sentences (1), (2) and (3).

6.2.4.11.  Exhaust Ducts and Outlets

(1)  Where an exhaust duct passes through or is adjacent to unheated space, the duct shall be insulated to prevent moisture or condensation in the duct.

(2)  Exhaust outlets shall be designed to prevent back draft under wind conditions.

(3)  Exhaust ducts directly connected to laundry drying equipment shall be independent of other exhaust ducts.

6.2.4.12.  Make-up Air

(1)  In ventilating systems that exhaust air to the outdoors, provision shall be made for the admission of a supply of make-up air in sufficient quantity so that the operation of the exhaust system and other exhaust equipment or combustion equipment is not adversely affected.

(2)  Except as provided in Sentence (3), when electric resistance heating is used to temper make-up air required in Sentence (1) in buildings of residential occupancy within the scope of Part 9, the energy rating for windows and sliding glass doors shall conform to the requirements of Article 9.25.2.7. and the minimum thermal resistance of insulation to be installed shall conform to Column 4 of Table 9.25.2.7.

(3)  Sentence (2) does not apply where

(a)	electric space heating is provided, or

(b)	a heat recovery ventilator meeting the minimum rating requirements of Article 6.2.1.7. is installed.

6.2.4.13.  Supply, Return, Intake and Exhaust Air Openings

(1)  Supply, return and exhaust air openings in rooms or spaces shall be protected by grilles having openings of a size that will not allow the passage of a 15 mm diameter sphere.

(2)  Outdoor air intakes and exhaust outlets at the building exterior shall be designed or located so that the air entering the building system will not contain more contaminants than the normal exterior air.

(3)  Exterior openings for outdoor air intakes and exhaust outlets shall be shielded from the entry of snow and rain and shall be fitted with corrosion-resistant screens of mesh not larger than 15 mm, except where climatic conditions may require larger openings.

(4)  Screens required in Sentence (3) shall be accessible for maintenance.

6.2.4.14.  Air Filters and Equipment

(1)  Air filters for air duct systems shall conform to the requirements for Class 2 air filter units as described in CAN4-S111-M, “Standard Method of Fire Tests For Air Filter Units”.

(2)  When electrostatic-type filters are used, they shall be installed so as to ensure that the electric circuit is automatically de-energized when filter access doors are opened or when the system circulating fan is not operating.

(3)  When odour removal equipment of the adsorption type is used it shall be

(a)	installed to provide access so that adsorption material can be reactivated or renewed, and

(b)	protected from dust accumulation by air filters installed on the inlet side.

6.2.5. Heating Appliances, General

6.2.5.1.  Location of Appliances

(1)  Except for appliances installed in dwelling units, fuel-fired heating appliances shall be located, enclosed or separated from the remainder of the building in conformance with Section 3.6.

6.2.5.2.  Appliances Installed Outside the Building

(1)  Fuel-fired appliances installed on the roof of a building or otherwise outside the building shall be

(a)	designed for outdoor use,

(b)	installed not less than 1 200 mm from the property line, measured horizontally, and

(c)	installed not less than 3 m from an adjacent wall of the same building when such wall contains an opening or openings within 3 storeys above and 5 m horizontally from the appliance, unless such openings are protected by a closure assembly having a 45 min fire-protection rating determined in conformance with Article 3.1.8.4., or by wired glass conforming to Article 3.1.8.14.

6.2.5A. Carbon Monoxide Detectors

6.2.5A.1.  Application

(1)  This subsection applies to every building that

(a)	contains a residential occupancy, and

(b)	contains a fuel-burning appliance or a storage garage.

6.2.5A.2.  Location of Carbon Monoxide Detectors

(1)  Where a fuel-burning appliance is installed in a suite of residential occupancy, a carbon monoxide detector shall be installed adjacent to each sleeping area in the suite.

(2)  Where a fuel-burning appliance is installed in a service room that is not in a suite of residential occupancy, a carbon monoxide detector shall be installed

(a)	adjacent to each sleeping area in every suite of residential occupancy that is adjacent to the service room, and

(b)	in the service room.

(3)  Where a storage garage is located in a building containing a residential occupancy, a carbon monoxide detector shall be installed adjacent to each sleeping area in every suite of residential occupancy that is adjacent to the storage garage.

6.2.5A.3.  Installation and Conformance to Standards

(1)  The carbon monoxide detector required by Article 6.2.5A.2. shall

(a)	be permanently connected to an electrical circuit and shall have no disconnect switch between the overcurrent device and the carbon monoxide detector,

(b)	be wired so that its activation will activate all carbon monoxide detectors within the suite, where located within a suite of residential occupancy,

(c)	be equipped with an alarm that is audible within bedrooms when the intervening doors are closed, where located in a suite of residential occupancy, and

(d)	conform to

(i)	CAN/CGA-6.19, “Residential Carbon Monoxide Detectors”,

(ii)	CSA 6.19, “Residential Carbon Monoxide Alarming Devices”, or

(iii)	UL 2034, “Single and Multiple Station Carbon Monoxide Detectors”.

6.2.6. Incinerators

6.2.6.1.  Applicable Standard

(1)  The design, construction, installation and alteration of every indoor incinerator shall conform to NFPA 82, “Incinerators, Waste and Linen Handling Systems and Equipment”.

6.2.6.2.  Venting

(1)  Every incinerator shall be served by a chimney flue conforming to Section 6.3.

6.2.7. Unit Heaters

6.2.7.1.  Clearances

(1)  Every unit heater using either steam or hot water as the heating medium shall be installed with a clearance of not less than 25 mm between the appliance and adjacent combustible material.

6.2.8. Radiators and Convectors

6.2.8.1.  Lining or Backing

(1)  Every steam or hot water radiator and convector located in a recess or concealed space or attached to the face of a wall of combustible construction shall be provided with a noncombustible lining or backing.

6.2.9. Piping for Heating and Cooling Systems

6.2.9.1.  Piping Materials and Installation

(1)  Piping shall be made from materials designed to withstand the effects of temperatures and pressures that may occur in the system.

(2)  Every pipe used in a heating or air-conditioning system shall be installed to allow for expansion and contraction due to temperature changes.

(3)  Supports and anchors for piping in a heating or air-conditioning system shall be designed and installed to ensure that undue stress is not placed on the supporting structure.

6.2.9.2.  Insulation and Coverings

(1)  Insulation and coverings on pipes shall be composed of material suitable for the operating temperature of the system to withstand deterioration from softening, melting, mildew and mould.

(2)  Insulation and coverings on pipes in which the temperature of the fluid exceeds 120°C

(a)	shall be made of noncombustible material, or

(b)	shall not flame, glow, smoulder or smoke when tested in accordance with the method of test ASTM C411, “Hot-Surface Performance of High-Temperature Thermal Insulation”, at the maximum temperature to which such insulation or covering is to be exposed in service.

(3)  Except as provided in Sentence (7), where combustible insulation is used on piping in a horizontal or vertical service space, the insulation and coverings on such pipes shall have a flame-spread rating throughout the material of not more than 25 in buildings of noncombustible construction and not more than 75 in buildings of combustible construction.

(4)  Except as provided in Sentence (7), insulation and coverings on piping located in rooms and spaces other than the service spaces described in Sentence (3) shall have a flame-spread rating of not more than that required for the interior finish for the ceiling of the room or space.

(5)  Except as provided in Sentence (7), where combustible insulation and covering is used on piping in buildings described in Subsection 3.2.6., they shall have a smoke developed classification of not more than 100.

(6)  Pipes that are exposed to human contact shall be insulated so that the exposed surface does not exceed 70°C.

(7)  No flame-spread rating or smoke developed classification limitations are required where combustible insulation and coverings are used on piping when such piping is

(a)	located within a concealed space in a wall,

(b)	located in a floor slab, or

(c)	enclosed in a noncombustible raceway or conduit.

6.2.9.3.  Clearances

(1)  Clearances between combustible material and bare pipes carrying steam or hot water shall conform to Table 6.2.9.3.

Table 6.2.9.3.

Clearance between Steam or Hot Water Pipes and Combustible Material

Forming Part of Sentence 6.2.9.3.(1)

| Steam or Water Temperature, °C | Minimum Clearance, mm |
| --- | --- |
| up to 120 | 15 |
| above 120 | 25 |
| Column 1 | 2 |

6.2.9.4.  Surface Temperature

(1)  The exposed surface temperature of a steam or hot water radiator shall not exceed 70°C unless precautions are taken to prevent human contact.

6.2.9.5.  Protection

(1)  Where a pipe carrying steam or hot water at a temperature above 120°C passes through a combustible floor, ceiling or wall, the construction shall be protected by a sleeve of metal or other noncombustible material not less than 50 mm larger in diameter than the pipe.

(2)  Unprotected steam or hot water pipes that pass through a storage space shall be covered with not less than 25 mm of noncombustible insulation to prevent direct contact with the material stored.

6.2.9.6.  Piping in Shafts

(1)  Where piping for heating or air-conditioning systems is enclosed in a shaft, the requirements of Article 3.6.3.1. for shafts shall apply.

6.2.10. Refrigerating Systems and Equipment for Air-Conditioning

6.2.10.1.  Cooling Units

(1)  Where a cooling unit is combined with a fuel-fired furnace in the same duct system, the cooling unit shall be installed

(a)	in parallel with the heating furnace,

(b)	upstream of the furnace provided the furnace is designed for such application, or

(c)	downstream of the furnace provided the cooling unit is designed to prevent excessive temperature or pressure in the refrigeration system.

6.2.11. Storage Bins

6.2.11.1.  Storage Bins

(1)  Service pipes passing through a storage bin for solid fuel shall be protected or so located as to avoid damage to the pipes.

(2)  Except for fuel-thawing pipes, every pipe designed to operate at a temperature of 50°C or above shall be located where fuel cannot be stored in contact with it.

(3)  A storage bin for solid fuel shall not be located above a sewer opening or drain opening.

(4)  Storage bins for solid fuel shall be designed and constructed so that the air temperature in the bin or the surface temperature of any part of the floor or walls is below 50°C.

6.2.11.2.  Ash Storage Bins

(1)  Every ash storage bin shall be constructed of noncombustible material and, where the bin is not covered, the ceiling of the room in which it is located shall be of noncombustible material.

(2)  Every opening in an ash storage bin shall be protected by a tight-fitting metal door with metal frame securely fastened to the bin.

Section 6.3. Chimneys and Venting Equipment

6.3.1. General

6.3.1.1.  Requirement for Venting

(1)  Except as provided in Articles 6.3.1.2. and 6.3.1.3., the products of combustion from solid fuel-burning appliances shall be vented in conformance with the requirements in the applicable appliance installation standards listed in Article 6.2.1.5.

6.3.1.2.  Masonry or Concrete Chimneys

(1)  Rectangular masonry or concrete chimneys not more than 12 m in height shall conform to Part 9 if they serve appliances with a combined total rated heat output of 120 kW or less, or that serve fireplaces.

(2)  Masonry or concrete chimneys other than those described in Sentence (1) shall be designed and installed in conformance with the appropriate requirements in NFPA 211, “Standard for Chimneys, Fireplaces, Vents and Solid Fuel-Burning Appliances”.

6.3.1.3.  Metal Smoke Stacks

(1)  Single wall metal smoke stacks shall be designed and installed in conformance with NFPA 211, “Standard for Chimneys, Fireplaces, Vents and Solid Fuel-Burning Appliances”.

6.3.1.4.  Reserved

6.3.1.5.  Access Ladders

(1)  Access ladders for chimneys, when provided, shall consist of steel or bronze rungs, built into the walls of the chimneys.

(2)  Rungs for external ladders shall begin at not less than 2 500 mm from ground level.

O. Reg. 403/97, Part 6; O. Reg. 283/01, s. 4.

Part 7
Plumbing

| Section | 7.1. | General |
| --- | --- | --- |
|  | 7.1.1. | Scope |
|  | 7.1.2. | Application |
|  | 7.1.3. | Definitions and Abbreviations |
|  | 7.1.4. | Equivalents |
|  | 7.1.5. | Plumbing Facilities |
|  | 7.1.6. | Service Connections |
|  | 7.1.7. | Location of Fixtures |
| Section | 7.2. | Materials and Equipment |
|  | 7.2.1. | General |
|  | 7.2.2. | Fixtures |
|  | 7.2.3. | Traps and Interceptors |
|  | 7.2.4. | Pipe Fittings |
|  | 7.2.5. | Non-Metallic Pipe and Fittings |
|  | 7.2.6. | Ferrous Pipe and Fittings |
|  | 7.2.7. | Non-Ferrous Pipe and Fittings |
|  | 7.2.8. | Corrosion Resistant Materials |
|  | 7.2.9. | Jointing Materials |
|  | 7.2.10. | Miscellaneous Materials |
|  | 7.2.11. | Water Service Pipes and Fire Service Mains |
| Section | 7.3. | Piping |
|  | 7.3.1. | Application |
|  | 7.3.2. | Construction and Use of Joints |
|  | 7.3.3. | Joints and Connections |
|  | 7.3.4. | Support of Piping |
|  | 7.3.5. | Protection of Piping |
|  | 7.3.6. | Testing of Drainage and Venting Systems |
|  | 7.3.7. | Testing of Potable Water Systems |
| Section | 7.4. | Drainage Systems |
|  | 7.4.1. | Application |
|  | 7.4.2. | Connections to Drainage Systems |
|  | 7.4.3. | Location of Fixtures |
|  | 7.4.4. | Treatment of Sewage and Wastes |
|  | 7.4.5. | Traps |
|  | 7.4.6. | Arrangement of Drainage Piping |
|  | 7.4.7. | Cleanouts |
|  | 7.4.8. | Minimum Slope and Length of Drainage Pipes |
|  | 7.4.9. | Size of Drainage Pipes |
|  | 7.4.10. | Hydraulic Loads |
| Section | 7.5. | Venting Systems |
|  | 7.5.1. | Vent Pipes for Traps |
|  | 7.5.2. | Stack Venting & Modified Stack Venting, Circuit Venting and Relief Venting |
|  | 7.5.3. | Vent Pipes for Soil or Waste Stacks |
|  | 7.5.4. | Miscellaneous Vent Pipes |
|  | 7.5.5. | Arrangement of Vent Pipes |
|  | 7.5.6. | Minimum Size of Vent Pipes |
|  | 7.5.7. | Sizing of Vent Pipes |
| Section | 7.6. | Potable Water Systems |
|  | 7.6.1. | Arrangement of Piping |
|  | 7.6.2. | Protection from Contamination |
|  | 7.6.3. | Size and Capacity of Pipes |
|  | 7.6.4. | Water Efficiency |
|  | 7.6.5 | Water Temperature Control |
| Section | 7.7. | Non-Potable Water Systems |
|  | 7.7.1. | Connection |
|  | 7.7.2. | Identification |
|  | 7.7.3. | Location |

Part 7
Plumbing

Section 7.1. General

7.1.1. Scope

7.1.1.1.  Scope

(1)  The scope of this Part shall be as described in Section 2.1.

7.1.1.2.  Industrial Systems

(1)  This Part does not apply to industrial process systems unless the industrial process system is interconnected with the plumbing system, in which case the interconnection shall be so designed and installed so that the plumbing system is protected against contamination or malfunction that may be caused by the industrial system.

7.1.2. Application

7.1.2.1.  Application

(1)  This Part applies to the design and construction of plumbing.

7.1.2.2.  Alteration or Repair

(1)  When an existing building is extended or subject to material alteration or repair, this Part is applicable

(a)	to the design and construction of plumbing in the extensions and those parts of the building subject to material alteration and repair, and

(b)	to plumbing which is adversely affected by the extension, alteration or repair.

7.1.3. Definitions and Abbreviations

7.1.3.1.  Reserved

7.1.3.2.  Definitions In Italics

(1)  In this Part,

Storey means the interval between two successive floor levels including mezzanine floors that contain plumbing or between a floor level and roof.

7.1.3.3.  Abbreviations of Names and Organizations

(1)  Reserved

7.1.3.4.  Abbreviations of Words

(1)  Reserved

7.1.4. Equivalents

(1)  Reserved

7.1.5. Plumbing Facilities

7.1.5.1.  Facilities Required

(1)  Plumbing facilities shall be provided in accordance with Subsection 3.7.4. and Section 9.31. of this Code.

7.1.5.2.  Floor Drains

(1)  Where gravity drainage to a sanitary drainage system is possible, a floor drain shall be installed in a basement forming part of a dwelling unit.

(2)  Where gravity drainage to a sanitary drainage system is not possible, the floor drain required by Sentence (1) may be connected to a storm drainage system, dry well or drainage ditch provided it is located where it can receive only clear water waste or storm sewage.

(3)  A floor drain shall be provided in a public laundry room, garbage room, incinerator room, boiler or heating room, serving more than one dwelling unit.

7.1.6. Service Connections

7.1.6.1.  Sanitary Drainage Systems

(1)  Every sanitary drainage system shall be connected to a public sanitary sewer, a public combined sewer or a private sewage disposal system.

(2)  A combined building drain or a combined building sewer shall not be installed.

7.1.6.2.  Storm Drainage Systems

(1)  Every storm drainage system shall be connected to a public storm sewage works, a public combined sewage works or a designated storm water disposal location but shall not be connected to a sanitary sewage works.

7.1.6.3.  Water Distribution Systems

(1)  Except as provided in Sentence (2), every water distribution system shall be connected

(a)	to a watermain that is part of a municipal drinking-water system, or

(b)	to a drinking-water system, if a watermain described in Clause (a) is not available.

(2)  Storm sewage or greywater that is free of solids may be used for the flushing of water closets, urinals or the priming of traps.

(3)  Piping conveying the non-potable water described in Sentence (2) shall be installed in conformance with Section 7.7.

7.1.6.4.  Separate Services

(1)  Piping in any building shall be connected to the public services separately from piping of any other building, except that an ancillary building on the same property may be served by the same service.

(2)  No plumbing serving a dwelling unit shall be installed under another unit of the building unless the piping is located in a tunnel, pipe corridor, common basement or parking garage, so that the piping is accessible for servicing and maintenance throughout its length without encroachment on any private living space, but this Sentence does not prevent plumbing serving a unit located above another unit from being installed in or under the lower unit.

7.1.6.5.  Private Sewers and Private Water Supply

(1)  Private sewers and private water supply pipes shall be installed according to the Guidelines for the Design of Sanitary Sewage Work Systems, Guidelines for the Design of Storm Sewers and Guidelines for the Design of Water Distribution Systems issued by the Environmental Approvals and Projects Engineering Branch of the Ministry of the Environment.

7.1.7. Location of Fixtures

7.1.7.1.  Lighting and Ventilation Requirements

(1)  Plumbing fixtures shall not be installed in a room that is not lighted and ventilated in accordance with the appropriate requirements in Parts 3 and 9.

7.1.7.2.  Accessibility

(1)  Every fixture, plumbing appliance, interceptor, cleanout, valve, device or piece of equipment shall be so located that it is readily accessible for use, cleaning and maintenance.

(2)  Except for Eastern-Style toilets, where a water closet is installed in a washroom for public use it shall be of the elongated type and provided with a seat of the open front type.

Section 7.2. Materials and Equipment

7.2.1. General

7.2.1.1.  Reserved

7.2.1.2.  Exposure of Materials

(1)  Where unusual conditions exist such as excessively corrosive soil or water, only materials suited for use in such locations shall be used.

(2)  Materials and equipment used in a drainage system where excessively corrosive wastes are present shall be suitable for the purpose.

7.2.1.3.  Restrictions on Re-Use

(1)  Used materials and equipment, including fixtures, shall not be reused unless they meet the requirements of this Part for new materials and equipment and are otherwise satisfactory for their intended use.

(2)  Materials and equipment that have been used for a purpose other than the distribution of potable water shall not be subsequently used in a potable water system.

7.2.1.4.  Identification and Certification

(1)  Every length of pipe and every fitting shall have cast, stamped or indelibly marked on it the maker’s name or mark and the weight or class or quality of the product, or it shall be marked in accordance with the relevant standard, and such markings shall be visible after installation.

(2)  Where a component of a plumbing system is required by this Code to comply with a standard and the compliance is not certified by a testing agency accredited by the Standards Council of Canada for the testing of the component in question and, when an inspector requests proof of the compliance, proof of compliance shall be produced by the person proposing to install or have installed the component, and without such proof the component shall not be installed as a permanent part of any plumbing system.

(3)  The lack of certification markings on a product or plumbing component shall be regarded as proof, in the absence of evidence to the contrary that no certification exists.

(4)  If a component of a plumbing system is required to be certified to a standard, the certification shall be made by a testing agency accredited for that purpose by the Standards Council of Canada.

7.2.1.5.  Pipe or Piping

(1)  Where the term pipe or piping and fittings is used, it shall also apply to tube or tubing and fittings unless otherwise stated.

7.2.1.6.  Withstanding Pressure

(1)  Piping, fittings and joints used in pressure sewer, forcemain or sump pump discharge applications shall be capable of withstanding at least one and one-half times the maximum potential pressure.

7.2.2. Fixtures

7.2.2.1.  Surface Requirements

(1)  Except for the area designed to be slip proof in such fixtures, every exposed area of a fixture shall have a smooth, hard corrosion-resistant surface that is free from flaws and blemishes that may interfere with cleaning.

7.2.2.2.  Reserved

7.2.2.3.  Showers

(1)  Every shower receptor shall be constructed and arranged so that water cannot leak through the walls or floor.

(2)  Not more than 6 shower heads shall be served by a single shower drain.

(3)  Where two or more shower heads are served by a shower drain, the floor shall be sloped and the drain located so that water from one head cannot flow over the area that serves another head.

(4)  Except for column showers, when a battery of shower heads is installed, the horizontal distance between two adjacent shower heads shall be at least 750 mm.

7.2.2.4.  Concealed Overflows

(1)  A dishwashing sink and a food preparation sink shall not have concealed overflows.

7.2.2.5.  Lavatories

(1)  A lavatory that does not have an overflow shall be equipped with a centre outlet waste fitting.

7.2.2.6.  Trough Urinals

(1)  No trough urinal shall be used as part of a plumbing system.

7.2.3. Traps and Interceptors

7.2.3.1.  Traps

(1)  Except as provided for in Sentence (2), every trap shall

(a)	have a trap seal depth of at least 38 mm,

(b)	be so designed that failure of the seal walls will cause exterior leakage, and

(c)	have a water seal that does not depend on the action of moving parts.

(2)  The trap seal depth on fixtures draining to an acid waste system shall be a minimum of 50 mm.

(3)  Every trap that serves a lavatory, a sink or a laundry tray shall

(a)	be provided with a cleanout plug of a minimum 3/4 in. size located at the lowest point of the trap and of the same material as the trap, except that a cast iron trap shall be provided with a brass cleanout plug, or

(b)	be designed so that part of the trap can be completely removed by screwed connections for cleaning purposes.

(4)  A bell trap or an S-trap shall not be installed in a drainage system.

(5)  A drum trap shall not be installed in a drainage system.

(6)  Except as permitted in Sentence (7), no bottle trap shall be used in a plumbing system.

(7)  A bottle trap may be used on a laboratory sink or other fixture equipped with corrosion resistant fittings.

(8)  No running trap shall be installed in a plumbing system unless an accessible handhole is provided for cleaning of the trap, and where the trap is too small to accommodate a handhole, a cleanout shall be provided.

7.2.3.2.  Interceptors

(1)  Every interceptor shall be designed so that it can be readily cleaned.

(2)  Every grease interceptor shall be designed so that it does not become air bound.

7.2.3.3.  Tubular Traps

(1)  Tubular metal or plastic traps that conform to CAN/CSA-B125, “Plumbing Fittings” shall be used in accessible locations.

7.2.4. Pipe Fittings

7.2.4.1.  T and Cross Fittings

(1)  A T fitting shall not be used in a drainage system except to connect a vent pipe.

(2)  A cross fitting shall not be used in a drainage system.

7.2.4.2.  Sanitary T Fittings

(1)  Reserved

(2)  A double sanitary T fitting shall not be used to connect the fixture drains of two urinals where no cleanout fitting is provided above the connection.

(3)  No pipe fitting, joint or connection that would tend to intercept solids or reduce the flow through a pipe by more than 10% shall be used in a plumbing system.

7.2.4.3.  One-Quarter Bends

(1)  Except as permitted in Sentence (3), a 1/4 bend of 4 in. size or less that has a centre-line radius that is less than the size of the pipe shall not be used to join two soil or waste pipes.

(2)  A 1/4 bend of 4 in. size or less shall not be used on a horizontal building drain, a branch of the building drain, or building sewer except to change direction from horizontal to vertical.

(3)  A 1/4 bend that is part of a pre-engineered wastewater heat recovery system is permitted to have a centre-line radius that is less than the size of the pipe.

7.2.4.4.  Fittings Restricted in Use

(1)  No double Y, double TY, double T or double waste fitting shall be installed in a nominally horizontal soil or waste pipe.

7.2.4.5.  Assembled Pipe or Tubing

(1)  Pipe or tubing assembled to comprise a standard drain waste and venting system shall be connected with drain, waste and vent fittings in conformance with Table 7.2.4.5.

Table 7.2.4.5.

Pipe Arrangement for DWV Fittings

Forming Part of Sentence 7.2.4.5.(1)

Insert regs\graphics\1997\403\403724au.tif

7.2.5. Non-Metallic Pipe and Fittings

7.2.5.1.  Asbestos-Cement Drainage Pipe and Fittings

(1)  Except as provided in Sentence (2), asbestos-cement pipe and its fittings for use in a drain, waste or vent system shall conform to

(a)	CAN/CGSB-34.22, “Pipe, Asbestos-Cement, Drain”, or

(b)	CSA B127.1, “Components for Use in Asbestos Cement Drain, Waste and Vent Systems”.

(2)  Asbestos-cement pipe and fittings used underground either outside a building or under a building shall conform to Sentence (1) or to

(a)	CAN/CGSB-34.9, “Pipe, Asbestos-Cement, Sewer”,

(b)	CAN/CGSB-34.23, “Pipe, Asbestos-Cement, Sewer, House Connection”, or

(c)	CSA B127.2, “Components for Use in Asbestos-Cement Building Sewer Systems”.

7.2.5.2.  Reserved

7.2.5.3.  Concrete Pipe and Fittings

(1)  Concrete pipe shall conform to CSA A257 Series, “Standards for Circular Concrete Pipe and Manholes”.

(2)  Reserved

(3)  Joints with external elastomeric gaskets shall be made with corrosion resistant external band type flexible mechanical couplings that conform to CAN/CSA-B602, “Mechanical Couplings for Drain, Waste, and Vent Pipe and Sewer Pipe”.

(4)  Concrete fittings field fabricated from lengths of pipe shall not be used.

(5)  Concrete pipe shall not be used above ground inside a building.

(6)  Precast reinforced circular concrete manhole sections, catch basins and fittings shall conform to CAN/CSA-A257.4-M, “Precast Reinforced Circular Concrete Manhole Sections, Catch Basins, and Fittings”.

7.2.5.4.  Vitrified Clay Pipe and Fittings

(1)  Vitrified clay pipe and fittings shall be certified to CSA A60.1, “Vitrified Clay Pipe”.

(2)  Couplings and joints for vitrified clay pipe shall be certified to CSA A60.3, “Vitrified Clay Pipe Joints”.

(3)  Vitrified clay pipe and fittings shall not be used except for an underground part of a drainage system.

7.2.5.5.  Polyethylene Water Pipe and Fittings

(1)  Polyethylene water pipe and fittings shall be certified to CAN/CSA-B137.1, “Polyethylene Pipe, Tubing and Fittings for Cold Water Pressure Services”, Series 160, and shall have a rated working pressure of 1034 kPa or more.

(2)  Except as permitted in Sentence (4), polyethylene water pipe or tube shall only be used in underground installations of cold water distributing pipe.

(3)  Butt fusion fittings for polyethylene pipe shall conform to ASTM D3261, “Butt Heat Fusion Polyethylene (PE) Plastic Fittings for Polyethylene (PE) Plastic Pipe and Tubing”.

(4)  Cross-linked polyethylene pressure pipe or tube and fittings used in above-ground or underground installations of water distributing pipe shall be certified to CAN/CSA-B137.5, “Cross-linked Polyethylene (PEX) Tubing Systems for Pressure Applications”.

7.2.5.6.  PVC Pipe and Fittings

(1)  PVC water pipe, fittings and solvent cement shall be certified to CAN/CSA-B137.3, “Rigid Poly (Vinyl Chloride) (PVC) Pipe for Pressure Applications” or CAN/CSA-B137.2, “PVC Injection-Moulded Gasketed Fittings for Pressure Applications”, and have a minimum pressure rating of 1034 kPa.

(2)  PVC water pipe and fittings in Sentence (1) shall not be used in a hot water system.

7.2.5.7.  CPVC Pipe, Fittings and Solvent Cements

(1)  CPVC hot and cold water pipe, fittings and solvent cements shall be certified to CSA B137.6, “CPVC Pipe, Tubing and Fittings for Hot and Cold Water Distribution Systems”.

(2)  The design temperature and design pressure of a CPVC piping system shall conform to the Standard referenced in Sentence (1).

7.2.5.8.  Polybutylene Pipe and Fittings

(1)  Polybutylene pipe and its associated fittings shall be certified to CAN3-B137.8, “Polybutylene (PB) Piping for Pressure Applications”.

(2)  Polybutylene pipe and fittings shall not be used for a continuously circulating hot water line or the first metre of any branch off of the continuously circulating hot water line.

7.2.5.9.  Plastic Pipe, Fittings and Solvent Cement Used Underground

(1)  Plastic pipe, fittings and solvent cement used underground outside a building or under a building in a drainage system shall be certified to

(a)	CAN/CSA-B181.1, “ABS Drain, Waste, and Vent Pipe and Pipe Fittings”,

(b)	CAN/CSA-B181.2, “PVC Drain, Waste, and Vent Pipe and Pipe Fittings”,

(c)	CAN/CSA-B182.1, “Plastic Drain and Sewer Pipe and Pipe Fittings”,

(d)	CAN/CSA-B182.2, “PVC Sewer Pipe and Fittings, (PSM Type)”,

(e)	CAN/CSA-B182.4, “Profile (Ribbed) PVC Sewer Pipe and Fittings”,

(f)	CAN/CSA-B182.6, “Profile Polyethylene Sewer Pipe and Fittings”,

(g)	CAN/CSA-B137.2, “PVC Injection-Moulded Gasketed Fittings for Pressure Applications”, or

(h)	CAN/CSA-B137.3, “Rigid Poly (Vinyl Chloride) (PVC) Pipe for Pressure Applications”.

(2)  Except as permitted in Clauses (g) and (h), plastic pipe used as described in Sentence (1) shall have a stiffness equal or greater than 320 kPa.

7.2.5.10.  Plastic Pipe, Fittings and Solvent Cement Used in Buildings

(1)  Plastic pipe, fittings and solvent cement used inside or under a building in a sanitary drainage system or venting system shall be certified to

(a)	CAN/CSA-B181.1, “ABS Drain, Waste, and Vent Pipe and Pipe Fittings”, or

(b)	CAN/CSA-B181.2, “PVC Drain, Waste, and Vent Pipe and Pipe Fittings”.

(2)  Plastic pipe, fittings and solvent cement used inside a building in a storm drainage system shall be certified to

(a)	CAN/CSA-B181.1, “ABS Drain, Waste, and Vent Pipe and Pipe Fittings”,

(b)	CAN/CSA-B181.2, “PVC Drain, Waste, and Vent Pipe and Pipe Fittings”,

(c)	CAN/CSA-B182.1, “Plastic Drain and Sewer Pipe and Pipe Fittings”, or

(d)	CAN/CSA-B182.2, “PVC Sewer Pipe and Fittings, (PSM Type)”.

(3)  Plastic pipe used as described in Sentence (2) shall have a pipe stiffness equal or greater than 320 kPa.

(4)  Requirements for combustible piping in relation to fire safety shall conform to Articles 3.1.5.15., 3.1.9.4., 9.10.9.6. and 9.10.9.7. of this Code.

(5)  Where noncombustible piping pierces a fire separation or a fire stop, the requirements for fire stopping of Subsection 3.1.9., Articles 9.10.9.6. and 9.10.15.4. shall apply.

7.2.5.11.  Transition Solvent Cement

(1)  Solvent cement for transition joints shall conform to

(a)	CAN/CSA-B181.1, “ABS Drain, Waste, and Vent Pipe and Pipe Fittings”, or

(b)	CAN/CSA-B181.2, “PVC Drain, Waste, and Vent Pipe and Pipe Fittings”.

(2)  Transition solvent cement shall only be used for joining an ABS plumbing system to a PVC plumbing system.

7.2.5.12.  Polyethylene/Aluminum/Polyethylene Composite Pipe and Fittings

(1)  PE/AL/PE composite pipe and fittings used for potable water systems shall conform to CAN/CSA-B137.9, “Polyethylene/Aluminum/Polyethylene Composite Pressure Pipe Systems”.

(2)  PE/AL/PE pipe and fittings shall not be used in a hot water system.

7.2.5.13.  Crosslinked Polyethylene/Aluminum/Polyethylene Composite Pipe and Fittings

(1)  PEX/AL/PEX composite pipe and fittings used for potable water systems shall conform to CAN/CSA-B137.10, “Crosslinked Polyethylene/Aluminum/Crosslinked Polyethylene Composite Pressure Pipe Systems”.

7.2.5.14.  Polypropylene Pipe and Fittings

(1)  Polypropylene pipe and fittings used for hot and cold potable water systems shall conform to CSA-B137.11, “Polypropylene (PP-R) Pipe and Fittings for Pressure Applications”.

7.2.6. Ferrous Pipe and Fittings

7.2.6.1.  Cast Iron Drainage and Vent Pipe and Fittings

(1)  Drainage piping, vent piping and fittings made of cast iron shall be certified to CSA B70, “Cast Iron Soil Pipe, Fittings and Means of Joining”.

(2)  Cast iron soil pipe and fittings shall not be used in a water system.

7.2.6.2.  Cast Iron Fittings for Asbestos-Cement Drainage Pipe

(1)  Cast iron fittings designed for use with asbestos-cement pipe for drainage purposes shall conform to the applicable requirements of CSA B127.1, “Components for Use in Asbestos Cement Drain, Waste and Vent Systems” or CSA B127.2, “Components for Use in Asbestos Cement Building Sewer Systems”.

7.2.6.3.  Threaded Cast Iron Drainage Fittings

(1)  Threaded cast iron drainage fittings shall conform to ANSI B16.12, “Cast Iron Threaded Drainage Fittings”.

(2)  Threaded cast iron drainage fittings shall not be used in a water system.

7.2.6.4.  Cast Iron Water Pipe

(1)  Cast iron water pipes shall conform to ANSI/AWWA C151/A21.51, “Ductile-Iron Pipe, Centrifugally Cast in Metal Molds or Sand-Lined Molds, for Water or Other Liquids”.

(2)  Cement mortar lining for cast iron water pipes shall conform to ANSI/AWWA C104/A21.4, “Cement-Mortar Lining for Ductile-Iron and Gray-Iron Pipe and Fittings for Water”.

(3)  Iron fittings for cast iron or ductile-iron water pipes shall conform to ANSI/AWWA C110/A21.10, “Ductile-Iron and Gray-Iron Fittings, 3-in. Through 48-in., for Water and Other Liquids”.

(4)  Rubber gasket joints for cast iron and ductile-iron pressure pipe for water piping shall conform to ANSI/AWWA C111/A21.11, “Rubber-Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings”.

7.2.6.5.  Screwed Cast Iron Water Fittings

(1)  Screwed cast iron water fittings shall conform to ANSI B16.4, “Cast Iron Threaded Fittings (Classes 125 and 250)”.

(2)  Screwed cast iron water fittings used in a water system shall be cement-mortar lined or galvanized.

(3)  Screwed cast iron water fittings shall not be used in a drainage system.

7.2.6.6.  Screwed Malleable Iron Water Fittings

(1)  Screwed malleable iron water fittings shall conform to ANSI B16.3, “Malleable Iron Threaded Fittings (Classes 150 and 300)”.

(2)  Screwed malleable iron water fittings used in a water system shall be cement-mortar lined or galvanized.

(3)  Screwed malleable iron water fittings shall not be used in a drainage system.

7.2.6.7.  Steel Pipe

(1)  Except as provided in Sentences (2) and (3), welded and seamless steel pipe shall not be used in a plumbing system.

(2)  Galvanized steel pipe may be used in a drainage system or a venting system above ground inside a building.

(3)  Galvanized steel pipe and fittings shall not be used in a water distribution system except

(a)	in buildings of industrial occupancy, or

(b)	for the repair of existing galvanized steel piping systems.

(4)  Galvanized steel pipe and fittings shall conform to ASTM A53, “Pipe, Steel, Black and Hot Dipped, Zinc-Coated Welded and Seamless”.

(5)  Where galvanized steel pipe is used in a drainage system, it shall be used with drainage fittings.

(6)  All steel pipe of 4 in. size and smaller shall be schedule 40 or heavier and fittings of less than 2 in. size shall be galvanized screw fittings.

7.2.6.8.  Corrugated Steel Pipe and Couplings

(1)  Corrugated steel pipe and couplings shall be certified to CAN3-G401, “Corrugated Steel Pipe Products”.

(2)  Corrugated steel pipe shall only be used underground outside a building in a storm drainage system.

(3)  Couplings for corrugated steel pipe shall be constructed so that when installed they shall

(a)	maintain the pipe alignment,

(b)	resist the separation of adjoining lengths of pipe,

(c)	prevent root penetration, and

(d)	prevent the infiltration of surrounding material.

7.2.6.9.  Sheet Metal Leaders

(1)  A sheet metal leader shall not be used except above ground outside a building.

7.2.7. Non-Ferrous Pipe and Fittings

7.2.7.1.  Copper and Brass Pipe

(1)  Copper pipe shall conform to ASTM B42, “Seamless Copper Pipe, Standard Sizes”.

(2)  Brass pipe shall conform to ASTM B43, “Seamless Red Brass Pipe, Standard Sizes”.

7.2.7.2.  Brass or Bronze Pipe Flanges and Flanged Fittings

(1)  Brass or bronze pipe flanges and flanged fittings shall conform to ANSI B16.24, “Bronze Pipe Flanges and Flanged Fittings (Class 150 and 300)”.

7.2.7.3.  Brass or Bronze Threaded Water Fittings

(1)  Brass or bronze threaded water fittings shall conform to ANSI B16.15, “Cast Bronze Threaded Fittings (Classes 125 and 250)”.

(2)  Brass or bronze threaded water fittings shall not be used in a drainage system.

7.2.7.4.  Copper Tube

(1)  Copper tube in a plumbing system shall

(a)	be certified to ASTM B88, “Seamless Copper Water Tube”, or

(b)	comply with ASTM B306, “Copper Drainage Tube (DWV)”.

(2)  The use of copper tube shall conform to Table 7.2.7.4.

(3)  Copper tube used in a plumbing appliance shall conform to

(a)	ASTM B88 “Seamless Copper Water Tube”, or

(b)	ASTM B68 “Seamless Copper Tube”.

(4)  Type K or L copper tube shall be used for the potable water side of a heat exchanger in a pre-engineered wastewater heat recovery system.

Table 7.2.7.4.

Permitted Use of Copper Tube and Pipe

Forming Part of Sentence 7.2.7.4.(2)

| Type of Copper Tube or Pipe | Water Distribution System |  | Building Sewer | Drainage System |  | Venting System |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Under ground | Above ground |  | Under ground | Above ground | Under ground | Above ground |
| K&L hard | N | P | P | P | P | P | P |
| K&L soft | P | P | N | N | N | N | N |
| M hard | N | P | N | N | P | N | P |
| M soft | N | N | N | N | N | N | N |
| DWV | N | N | N | N | P | N | P |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |

Note to Table 7.2.7.4.:

P-Permitted
N-Not Permitted

7.2.7.5.  Solder-Joint Drainage Fittings

(1)  Solder-joint fittings for drainage systems shall conform to

(a)	CSA B158.1, “Cast Brass Solder Joint Drainage, Waste and Vent Fittings”, or

(b)	ANSI B16.29, “Wrought Copper and Wrought Copper Alloy Solder Joint Drainage Fittings - DWV”.

(2)  Solder-joint fittings for drainage systems shall not be used in a water system.

7.2.7.6.  Solder-Joint Water Fittings

(1)  Except as provided in Sentence (2), solder-joint fittings for water systems shall conform to

(a)	ANSI B16.18, “Cast Copper Alloy Solder Joint Pressure Fittings”, or

(b)	ANSI B16.22, “Wrought Copper and Copper Alloy Solder Joint Pressure Fittings”.

(2)  Solder-joint fittings for water systems not made by casting or the wrought process shall conform to the applicable requirements of ANSI B16.18, “Cast Copper Alloy Solder Joint Pressure Fittings”.

7.2.7.7.  Flared-Joint Fittings for Copper Water Systems

(1)  Flared-joint fittings for copper tube water systems shall conform to ANSI B16.26, “Cast Copper Alloy Fittings for Flared Copper Tubes”.

(2)  Flared-joint fittings for copper tube water systems not made by casting shall conform to the applicable requirements of ANSI B16.26, “Cast Copper Alloy Fittings for Flared Copper Tubes”.

7.2.7.8.  Lead Waste Pipe and Fittings

(1)  Lead waste pipe and fittings shall conform to CSA B67, “Lead Service Pipe, Waste Pipe, Traps, Bends and Accessories”.

(2)  When there is a change in size of a lead closet bend, the change shall be in the vertical section of the bend or made in such a manner that there shall be no retention of liquid in the bend.

(3)  Lead waste pipe and fittings shall not be used in a water system or for a building sewer.

7.2.7.9.  Aluminum DWV Pipe and Components

(1)  Drainage piping and vent piping made of aluminum and its components shall be certified to CAN/CSA-B281, “Aluminum Drain, Waste, and Vent Pipe and Components”.

(2)  Aluminum DWV pipe shall not be used in water systems.

(3)  Aluminum drain waste and vent pipe to be buried underground shall be protected by a factory applied coating in accordance with CAN/CSA-B281, “Aluminum Drain, Waste, and Vent Pipe and Components”.

7.2.8. Corrosion Resistant Materials

7.2.8.1.  Pipe and Fittings

(1)  Pipes and fittings to be used for drainage and venting of acid and corrosive wastes shall conform to

(a)	ASTM A518M, “Specification for Corrosion-Resistant High-Silicon Iron Castings”,

(b)	ASTM C1053, “Specification for Boronsilicate Glass Pipe and Fittings for Drain, Waste, and Vent (DWV) Applications”, or

(c)	CAN/CSA-B181.3, “Polyolefin Laboratory Drainage Systems”.

7.2.9. Jointing Materials

7.2.9.1.  Cement Mortar

(1)  Cement mortar shall not be used for jointing.

7.2.9.2.  Wiping Solder and Caulking Lead

(1)  Wiping solder and caulking lead shall conform to CSA B67, “Lead Service Pipe, Waste Pipe, Traps, Bends and Accessories”.

(2)  Solders for solder joint fittings shall conform to ASTM B32, “Solder Metal” in accordance with the recommended use.

(3)  Solders and fluxes having a lead content in excess of 0.2% shall not be used in a potable water system.

7.2.10. Miscellaneous Materials

7.2.10.1.  Brass Floor Flanges

(1)  Brass floor flanges shall be certified to CSA B158.1, “Cast Brass Solder Joint Drainage, Waste and Vent Fittings”.

(2)  ABS floor flanges shall be certified to CAN/CSA-B181.1, “ABS Drain, Waste, and Vent Pipe and Pipe Fittings”.

(3)  PVC floor flanges shall be certified to CAN/CSA-B181.2, “PVC Drain, Waste, and Vent Pipe and Pipe Fittings”.

(4)  Cast iron, copper and aluminum floor flanges shall be suitable for the purpose.

7.2.10.2.  Brass Screws, Bolts, Nuts and Washers

(1)  Every screw, bolt, nut and washer shall be of brass or equally corrosion resistant material when used

(a)	to connect a water closet to a water closet flange,

(b)	to anchor the water closet flange to the floor,

(c)	to anchor the water closet to the floor, or

(d)	to hold cleanout covers or floor drain grates.

7.2.10.3.  Cleanout Fittings

(1)  Every plug, cap, nut or bolt that is intended to be removable from a ferrous fitting shall be of a non-ferrous material.

(2)  A cleanout fitting that as a result of normal maintenance operations cannot withstand the physical stresses of removal and reinstallation or cannot ensure a gas-tight seal shall not be installed.

(3)  A screw cap or test cap shall not be used as a cleanout plug or cover.

7.2.10.4.  Groove and Shoulder Type Mechanical Pipe Couplings

(1)  Groove and shoulder type mechanical pipe couplings shall conform to CSA B242, “Groove and Shoulder Type Mechanical Pipe Couplings”.

(2)  Mechanical Couplings for DWV and Sewer Pipe shall be certified to CAN/CSA-B602, “Mechanical Couplings for Drain, Waste, and Vent Pipe and Sewer Pipe”.

7.2.10.5.  Saddle Hubs

(1)  Except as provided in Sentence (2), a saddle hub or fitting shall not be installed in drainage systems, venting systems or water systems.

(2)  A saddle hub or saddle clamp may be installed in a building drain or building sewer of nominal diameter not less than eight inches and that is in service provided that the connecting branch is at least two pipe sizes smaller than the run of the building drain or building sewer to which it is connected.

7.2.10.6.  Supply and Waste Fittings

(1)  Supply and waste fittings shall be certified to CAN/CSA-B125, “Plumbing Fittings”.

7.2.10.7.  Reserved

7.2.10.8.  Direct Flush Valves

(1)  Every direct flush valve shall

(a)	open fully and close positively under service pressure,

(b)	complete its cycle of operation automatically,

(c)	be provided with a means of regulating the volume of water that it discharges, and

(d)	be provided with a vacuum breaker unless the fixture is designed so that back-siphonage cannot occur.

7.2.10.9.  Drinking Fountain Bubblers

(1)  The orifice of every drinking fountain bubbler shall

(a)	be of the shielded type, and

(b)	direct the water upward to an angle of approximately 45°.

(2)  Every drinking fountain bubbler shall include a means of regulating the flow to the orifice.

7.2.10.10.  Back-Siphonage Preventers and Backflow Preventers

(1)  Except as provided in Sentence (2) back-siphonage preventers and backflow preventers shall be certified to

(a)	CAN/CSA-B64.0, “Definitions, General Requirements and Test Methods for Vacuum Breakers and Backflow Preventers”,

(b)	CAN/CSA-B64.1.1, “Vacuum Breakers, Atmospheric Type (AVB)”,

(c)	CAN/CSA-B64.1.2, “Vacuum Breakers, Pressure Type (PVB)”,

(d)	CAN/CSA-B64.2, “Vacuum Breakers, Hose Connection Type (HCVB)”,

(e)	CAN/CSA-B64.2.1, “Vacuum Breakers, Hose Connection Type (HCVB) with Manual Draining Feature,”

(f)	CAN/CSA-B64.2.2, “Vacuum Breakers, Hose Connection type (HCVB) with Automatic Draining Feature,”

(g)	CAN/CSA-B64.3, “Backflow Preventers, Dual Check Valve with Atmospheric Port Type (DCAP)”,

(h)	CAN/CSA-B64.4, “Backflow Preventers, Reduced Pressure Principle Type (RP)”,

(i)	CAN/CSA-B64.5, “Backflow Preventers, Double Check Valve Type (DCVA)”,

(j)	CAN/CSA-B64.6, “Backflow Preventers, Dual Check Valve Type (DuC)”,

(k)	CAN/CSA-B64.7, “Vacuum Breakers, Laboratory Faucet Type (LFVP)”,

(l)	CAN/CSA-B64.8, “Backflow Preventers, Dual Check with Intermediate Vent Type (DuCV)”, or

(m)	CAN/CSA-B64.10, “Backflow Prevention Devices – Selection, Installation, Maintenance and Field Testing”.

(2)  Back-siphonage preventers for tank type water closets shall be certified to CAN/CSA-B125, “Plumbing Fittings”.

7.2.10.11.  Relief Valves

(1)  Temperature relief, pressure relief, combined temperature and pressure relief and vacuum relief valves shall conform to CAN1-4.4, “Temperature, Pressure, Temperature and Pressure Relief Valves and Vacuum Relief Valves”, or ANSI Z21.22, “Relief Valves and Automatic Gas Shut-off Devices for Hot Water Supply Systems”.

7.2.10.12.  Reducing Valves

(1)  Direct acting water pressure reducing valves for domestic water supply systems shall conform to CSA-B356, “Water Pressure Reducing Valves for Domestic Water Supply Systems”.

7.2.10.13.  Solar Domestic Hot Water

(1)  Equipment forming part of a packaged system for solar heating of potable water, shall conform to CAN/CSA-F379.1, “Solar Domestic Hot Water Systems (Liquid to Liquid Heat Transfer)”.

7.2.10.14.  Vent Pipe Flashing

(1)  Flashing fabricated on-site for vent pipes shall be fabricated from

(a)	copper sheet at least 0.33 mm thick,

(b)	aluminum sheet at least 0.61 mm thick,

(c)	alloyed zinc sheet at least 0.35 mm thick,

(d)	lead sheet at least 2.16 mm thick,

(e)	galvanized steel sheet at least 0.41 mm thick, or

(f)	polychloroprene (neoprene) at least 2.89 mm thick.

(2)  Prefabricated flashing for vent pipes shall be certified to CSA B272, “Prefabricated Self-Sealing Vent Flashings”.

7.2.11. Water Service Pipes and Fire Service Mains

7.2.11.1.  Design, Construction, Installation and Testing

(1)  Except as provided in Articles 7.2.11.2., 7.2.11.3., 7.2.11.4. and 7.3.7.2, the design, construction, installation and testing of fire service mains and water service pipe combined with fire service mains shall be in conformance with NFPA 24, “Standard for the Installation of Private Fire Service Mains and Their Appurtenances”.

7.2.11.2.  Certification or Conformance

(1)  Water service pipes and fire service mains shall be certified or conform to the standards for the materials listed in Table 7.2.11.2.

7.2.11.3.  Tracer Wire

(1)  Except as provided in Sentence (2), a 14 gauge TW solid copper light coloured plastic coated tracer wire shall be attached to every non-metallic water service pipe or fire service main.

(2)  Where a water service pipe or fire service main is detectable without the tracer wire referenced in Sentence (1), the tracer wire may be omitted.

7.2.11.4.  Required Check Valve

(1)  Where a water service pipe is supplied with water by more than one drinking-water system, a check valve shall be installed at each connection with a drinking-water system.

(2)  Where a fire service main is supplied with water by more than one source, a check valve shall be installed at each connection with a source of water.

Table 7.2.11.2.

Water Service Pipe and Fire Service Main Materials

Forming Part of Sentence 7.2.11.2.(1)

| Material | Standard | Limitations |
| --- | --- | --- |
| Polyethylene pipe and fittings | certified to CAN/CSA-B137.1, “Polyethylene Pipe, Tubing and Fittings for Cold Water Pressure Services” | Pipe and fittings must have a rated working pressure of 1034 kPa or more. Can only be used in underground installations. |
| Cross-linked polyethylene pressure pipe or tube and fittings | certified to CAN/CSA-B137.5, “Cross-linked Polyethylene (PEX) Tubing Systems for Pressure Applications” |  |
| PVC pipe and fittings | certified to CAN/CSA-B137. 3, “Rigid Poly (Vinyl Chloride) (PVC) Pipe for Pressure Applications”, or certified to CAN/CSA-B137.2, “PVC Injection-Moulded Gasketed Fittings for Pressure Applications” | Pipe and fittings must have a rated working pressure of 1034 kPa or more |
| CPVC pipe and fittings | certified to CAN/CSA-B137.6, “CPVC Pipe, Tubing and Fittings for Hot and Cold Water Distribution Systems” | The design temperature and pressure shall conform to the requirements of the CSA B137.6, “CPVC Pipe, Tubing and Fittings for Hot and Cold Water Distribution Systems” |
| Polybutylene pipe and fittings | certified to CAN/CSA-B137.7, “Polybutylene (PB) Piping for Cold Water Distribution Systems” | Pipe must have an SDR of 11 or less |
| Cast iron water pipe | conform to ANSI/AWWA C151/A21.51, “Ductile-Iron Pipe, Centrifugally Cast in Metal Molds or Sand-Lined Molds, for Water or Other Liquids” | Pipe shall have a cement mortar lining conforming to ANSI/AWWA C104/A21.4, “Cement-Mortar Lining for Ductile-Iron and Gray-Iron Pipe and Fittings for Water” |
| Iron fittings for cast iron or ductile-iron water pipes | conform to ANSI/AWWA C110/A21.10, “Ductile-Iron and Gray-Iron Fittings, 3-in. Through 48 in., for Water and Other Liquids” | Pipe shall have a cement mortar lining conforming to ANSI/AWWA C104/A21.4, “Cement-Mortar Lining for Ductile-Iron and Gray-Iron Pipe and Fittings for Water” |
| Rubber gasket joints for cast iron and ductile-iron water pipes | conform to ANSI/AWWA C111/A21.11, “Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings” |  |
| Screwed cast iron water fittings | conform to ANSI B16.4, “Cast Iron Threaded Fittings (Classes 125 and 250)” | Screwed cast iron water fittings shall be cement-mortar lined or galvanized |
| Type K soft copper tube | certified to ASTM B88, “Seamless Copper Water Tube” |  |
| Solder-joint fittings for copper water systems | conform to ANSI B16.18, “Cast Copper Alloy Solder Joint Pressure Fittings”, or conform to ANSI B16.22, “Wrought Copper and Copper Alloy Solder Joint Pressure Fittings” | Solder-joint fittings not made by casting or the wrought process shall conform to the applicable requirements of ANSI B16.18, “Cast Copper Alloy Solder Joint Pressure Fittings” |
| Flared-joint fittings for copper water systems | conform to ANSI B16.26, “Cast Copper Alloy Fittings for Flared Copper Tubes” | Flared-joint fittings not made by casting shall conform to ANSI B16.26, “Cast Copper Alloy Fittings for Flared Copper Tubes” |
| PE/AL/PE pipe and fittings | certified to CAN/CSA B137.9, “Polyethylene/Aluminum/Polyethylene Composite Pressure Pipe Systems” |  |
| PEX/AL/PEX pipe and fittings | certified to CAN/CSA B137.10, “Crosslinked Polyethylene/ Aluminum/Crosslinked Polyethylene Composite Pressure Pipe Systems” |  |
| Column 1 | 2 | 3 |

Section 7.3. Piping

7.3.1. Application

7.3.1.1.  Application

(1)  This Section applies to the construction and use of joints and connections, and the arrangement, protection, support and testing of piping.

7.3.2. Construction and Use of Joints

7.3.2.1.  Caulked Lead Drainage Joints

(1)  Every caulked lead drainage joint shall be firmly packed with oakum and tightly caulked with lead to a depth of at least 25 mm.

(2)  No paint, varnish or other coating shall be applied on the lead until after the joint has been tested.

(3)  Caulked lead drainage joints shall not be used except for cast iron pipe in a drainage system or venting system, or between such pipe, and

(a)	other ferrous pipe,

(b)	brass and copper pipe,

(c)	a caulking ferrule, or

(d)	a trap standard.

(4)  A length of hub and spigot pipe and pipe fittings in a drainage system shall be installed with the hub at the upstream end.

7.3.2.2.  Wiped Joints

(1)  Wiped joints shall not be used except for sheet lead or lead pipe, or between such pipe and copper pipe or a ferrule.

(2)  Every wiped joint in straight pipe shall

(a)	be made of solder,

(b)	have an exposed surface on each side of the joint at least 19 mm wide, and

(c)	be at least 10 mm thick at the thickest part.

(3)  Every wiped flanged joint shall be reinforced with a lead flange that is at least 19 mm wide.

7.3.2.3.  Screwed Joints

(1)  In making a screwed joint the ends of the pipe shall be reamed or filed out to the size of the bore and all chips and cuttings shall be removed.

(2)  No pipe-joint cement or paint shall be applied to the internal threads.

(3)  Aluminum DWV pipe shall not be used with a screwed joint.

7.3.2.4.  Solder Joints

(1)  In making a soldered joint the surface to be soldered shall be cleaned bright and the joint shall be properly fluxed, made with solder and thoroughly cleaned of all residue.

(2)  Aluminum DWV pipe shall not be used with soldered joints.

7.3.2.5.  Flared Joints

(1)  In making a flared joint the pipe shall be expanded with a proper flaring tool.

(2)  Flared joints shall not be used for hard (drawn) copper tube.

7.3.2.6.  Burned Lead Joints

(1)  In making a burned lead joint the lead shall be lapped and fused to form a weld that is at least 1-1/2 times as thick as the wall of the pipe.

(2)  In lead pipe the width of the weld shall be at least

(a)	13 mm where the size of the pipe is less than 3 in.,

(b)	16 mm where the size of the pipe is 3 in., or

(c)	19 mm where the size of the pipe is 4 in.

(3)  In sheet lead the width of the weld shall be as specified in Table 7.3.2.6.

Table 7.3.2.6.

Minimum Permitted Width of Weld for Sheet Lead

Forming Part of Sentence 7.3.2.6.(3)

| Weight of Sheet Lead, kg/m2 | Minimum Width of Weld, mm |
| --- | --- |
| 12.2 to 14.6 | 6 |
| 19.5 to 24.4 | 10 |
| 29.3 to 39.1 | 20 |
| 48.8 to 58.6 | 25 |
| 58.6 to 146.5 | 32 |
| Column 1 | 2 |

7.3.2.7.  Mechanical Joints

(1)  Mechanical joints shall be made with compounded elastomeric couplings or rings held by stainless steel or cast iron clamps or contained within a compression connection or groove and shoulder type mechanical coupling.

7.3.2.8.  Cold-Caulked Joints

(1)  Cold-caulked joints shall not be used except for bell and spigot pipe in a water system, a drainage system or a venting system.

(2)  The caulking compound used in cold-caulked joints shall be applied according to the manufacturer’s directions.

(3)  Every cold-caulked joint in a drainage system shall be firmly packed with oakum and tightly caulked with cold caulking compound to a depth of at least 25 mm.

(4)  Every cold-caulked joint in a water system shall be made by tightly caulking the entire depth of the socket with caulking compound.

7.3.3. Joints and Connections

7.3.3.1.  Drilled and Tapped Joints

(1)  Except as provided in Sentences (2) to (4), no water distributing pipe, drainage pipe or fittings shall be drilled, tapped or swaged.

(2)  A water distributing pipe may be drilled or tapped to provide for a mechanically extracted T in copper tubing of Type L or K provided that all branch connections shall be notched and dimpled to limit depth of insertion and conform to the inner contour of the main.

(3)  A copper water distributing pipe of 1 in. size or larger may be mechanically swaged to permit the joining of other copper pipe of equal size.

(4)  A drainage pipe or fitting may be drilled or tapped

(a)	to provide for the connection of a trap seal primer line,

(b)	to connect a device designed to dispense germicidal or odour control chemicals or trap seal water to a floor drain downstream of a vacuum breaker or flush valve in a flush tube connected to a sanitary unit,

(c)	to provide a hole for a branch connection to a drainage pipe, where the branch connection is made with a saddle hub as permitted by Article 7.2.10.5. and where the hole is drilled to provide a smooth clean hole of the required size and orientation, or

(d)	to provide for the connection of pipe or fittings to metal or rigid plastic pipe and fittings where the pipe or fittings are thick enough to be threaded or are bossed for tapping.

(5)  No pipe adaption shall be made by the use of a bushing that leaves a square edge or shoulder on the inside of the pipe or fitting.

7.3.3.2.  Reserved

7.3.3.3.  Prohibition of Welding of Pipes and Fittings

(1)  Cast iron soil pipe and fittings shall not be welded.

(2)  Galvanized steel pipe and fittings shall not be welded.

(3)  Aluminum DWV pipe shall not be welded.

7.3.3.4.  Unions and Slip Joints

(1)  Running thread and packing nut connections and unions with a gasket seal shall not be used downstream of a trap weir in a drainage system or in a venting system.

(2)  A slip joint shall not be used

(a)	in a venting system, or

(b)	in a drainage system, except to connect a fixture trap to a fixture drain in an accessible location.

7.3.3.5.  Increaser or Reducer

(1)  Every connection between two pipes of different size shall be made with an increaser or a reducer fitting installed so that it will permit the system to be completely drained.

7.3.3.6.  Burned Lead Joints

(1)  Every joint in hard lead shall be made with a burned lead joint.

7.3.3.7.  Dissimilar Connections

(1)  Adapters, connectors or mechanical joints used to join dissimilar materials shall be designed to accommodate the required transition.

7.3.3.8.  Connection of Roof Drain to Leader

(1)  Every roof drain shall be securely connected to a leader and provision shall be made for expansion.

7.3.3.9.  Connection of Floor Outlet Fixtures

(1)  Every pedestal urinal, floor-mounted water closet or S-trap standard shall be connected to a fixture drain by a floor flange, except that a cast iron trap standard may be caulked to a cast iron pipe.

(2)  Except as provided in Sentence (3), every floor flange shall be of brass.

(3)  Where cast iron or plastic pipe is used, a floor flange of the same material may be used.

(4)  Every floor flange shall be securely set on a firm base and bolted to the trap flange of the fixture, and every joint shall be sealed with a natural rubber, synthetic rubber or asbestos graphite gasket, or with a closet setting compound.

(5)  Where a lead water closet stub is used, the length of the stub below the floor flange shall be at least 75 mm.

7.3.3.10.  Expansion and Contraction

(1)  The design and installation of every piping system shall, where necessary, include means to accommodate expansion and contraction of the piping system caused by temperature change or movement of the soil.

7.3.3.11.  Copper Tube

(1)  Types M and DWV copper tube shall not be bent.

(2)  Aluminum DWV pipe shall not be bent.

(3)  Bends in copper tubing of soft or bending temper shall be made with tools manufactured and sized for the purpose.

7.3.3.12.  Indirect Connections

(1)  Where a fixture or device is indirectly connected, the connections shall be made by terminating the fixture drain above the flood level rim of a directly connected fixture to form an air break.

(2)  The size of the air break shall be at least 25 mm.

7.3.4. Support of Piping

7.3.4.1.  Capability of Support

(1)  Piping shall be provided with support that is capable of keeping the pipe in alignment and bearing the weight of the pipe and its contents.

(2)  Every floor or wall mounted water closet bowl shall be securely attached to the floor or wall by means of a flange and shall be stable.

(3)  Every wall mounted fixture shall be supported so that no strain is transmitted to the piping.

7.3.4.2.  Independence of Support

(1)  Piping, fixtures, tanks or devices shall be supported independently of each other.

7.3.4.3.  Insulation of Support

(1)  Where a hanger or support for copper tube or brass or copper pipe is of a material other than brass or copper, it shall be suitably separated and electrically insulated from the pipe to prevent galvanic action.

(2)  Where a hanger or support for aluminum DWV pipe is of a metal other than aluminum, the hanger or support shall be suitably separated and electrically insulated from the pipe.

7.3.4.4.  Support for Vertical Piping

(1)  Except as provided in Sentences (2) and (3), vertical piping shall be supported at its base and at the floor level of alternate storeys by metal rests, each of which can bear the weight of pipe that is between it and the metal rest above it.

(2)  The maximum spacing of supports shall be 7.5 m.

(3)  The maximum spacing of supports for PE/AL/PE and PEX/AL/PEX composite pipe shall be 2 500 mm.

7.3.4.5.  Support for Horizontal Piping

(1)  Nominally horizontal piping that is inside a building shall be braced to prevent swaying and buckling and to control the effects of thrust.

(2)  Nominally horizontal piping shall be supported so that

(a)	galvanized iron or steel pipe is supported at intervals not exceeding

(i)	3.75 m if the pipe size is 6 in. or more, and

(ii)	2 500 mm if the pipe size is less than 6 in.,

(b)	lead pipe is supported throughout its length,

(c)	cast iron pipe is supported

(i)	at or adjacent to each hub or joint,

(ii)	at intervals not exceeding 3 m, and

(iii)	at intervals not exceeding 1 000 mm if the pipe has mechanical joints and the length of pipe between adjacent fittings is 300 mm or less,

(d)	asbestos-cement pipe is supported

(i)	at intervals not exceeding 2 000 mm or have two supports for every 4 m length of pipe, and

(ii)	at intervals not exceeding 1 000 mm where the length of pipe between adjacent fittings is 300 mm or less,

(e)	ABS or PVC plastic DWV pipe is supported

(i)	at intervals not exceeding 1 200 mm,

(ii)	at the ends of branches,

(iii)	at changes of direction or elevation, and

(iv)	if the pipe is a fixture drain that is more than 1 000 mm in length, as close as possible to the trap,

(f)	plastic water pipe is supported at intervals not exceeding 1 000 mm,

(g)	copper tube and copper and brass pipe is supported at intervals not exceeding

(i)	3 m if the tube or pipe is hard temper and larger than 1 in. in size,

(ii)	2 500 mm if the tube or pipe is hard temper and 1 in. in size or less, and

(iii)	2 500 mm if the tube is soft temper,

(h)	aluminum DWV pipe is supported

(i)	at intervals not greater than 3 m,

(ii)	at both sides of all joints,

(iii)	at all branch ends,

(iv)	at all points where there is a change in direction, and

(v)	as close to all traps as possible,

(i)	supports and hangers for aluminum DWV pipe shall have a broad support base and shall be free of burrs and rough edges to prevent abrasion of the pipe,

(j)	where joints in the piping are less rigid than the pipe, the support points shall be selected so as to minimize the shear and bending forces imposed on the joints,

(k)	PE/AL/PE or PEX/AL/PEX composite pipe is supported at intervals not exceeding 1 m, and

(l)	PP-R plastic pipe is supported

(i)	at intervals not exceeding 1 000 mm

(ii)	at the end of branches, and

(iii)	at changes of direction and elevation.

(3)  Where plastic pipe or a composite pipe incorporating a plastic component is installed

(a)	the pipe shall be aligned without added strain on the piping,

(b)	the pipe shall not be bent or pulled into position after being welded or joined, and

(c)	hangers shall not compress, cut or abrade the pipe.

(4)  Where hangers are used to support nominally horizontal piping they shall be

(a)	metal rods of at least 9.5 mm diam. for pipe over 4 in. in size, and

(b)	solid or perforated metal strap hangers for pipe 4 in. or less in size.

(5)  Where a hanger is attached to concrete or masonry, it shall be fastened by metal or expansion-type plugs that are inserted or built into the concrete or masonry.

7.3.4.6.  Support for Underground Horizontal Piping

(1)  Except as provided in Sentence (2), nominally horizontal piping that is underground shall be supported on a base that is firm and continuous under the whole of the pipe.

(2)  Nominally horizontal piping installed underground that is not supported as described in Sentence (1) may be installed using hangers fixed to a foundation or structural slab provided that the hangers are capable of keeping the pipe in alignment and supporting the weight of the pipe, its contents and the fill over the pipe.

7.3.4.7.  Support for Vent Pipe Above a Roof

(1)  Where a vent pipe terminates above the surface of a roof it shall be supported or braced to prevent misalignment.

7.3.4.8.  Compression Fittings

(1)  No compression fitting connecting to plain end pipe or tube shall be used in a plumbing system unless the pipe or tube and fittings are sufficiently stayed, clamped, anchored or buttressed so as to prevent separation during normal service of the system allowing for surge pressures.

7.3.4.9.  Thrust Restraint of Water Service Pipes

(1)  Pipe clamps and tie-rods, thrust blocks, locked mechanical or push-on joints, mechanical joints utilizing set screw retainer glands, or other suitable means of thrust restraint shall be provided at each change of direction of a water service pipe 4 in. or more in size and at all tees, plugs, caps and bends.

(2)  Backing for underground water service pipes shall be placed

(a)	between undisturbed earth and the fitting to be restrained and shall be of sufficient bearing area to provide adequate resistance to the thrust to be encountered, and

(b)	so that the joints will be accessible for inspection and repair.

(3)  Concrete thrust blocks shall have a minimum compressive strength of not less than 10 MPa after 28 days.

(4)  Thrust blocks shall not be used to restrain vertical pipe.

7.3.5. Protection of Piping

7.3.5.1.  Backfill of Pipe Trench

(1)  Where piping is installed underground, the backfill shall be carefully placed and tamped to a height of 300 mm over the top of the pipe and shall be free of stones, boulders, cinders and frozen earth.

7.3.5.2.  Protection of Non-Metallic Pipe

(1)  Where asbestos-cement drainage pipe or vitrified clay is located less than 600 mm below a basement floor and the floor is constructed of other than 75 mm or more of concrete, the pipe shall be protected by a 75 mm layer of concrete installed above the pipe.

7.3.5.3.  Isolation from Loads

(1)  Where piping passes through or under a wall, it shall be installed so that the wall does not bear on the pipe.

7.3.5.4.  Protection from Frost

(1)  Where piping may be exposed to freezing conditions it shall be protected from frost.

7.3.5.5.  Protection from Mechanical Damage

(1)  Plumbing, piping and equipment exposed to mechanical damage shall be protected.

7.3.5.6.  Spatial Separation

(1)  Except as permitted in Sentence (2), a buried water service pipe shall be separated from the building drain, building sewer and a private sewage disposal system, by not less than 2 440 mm measured horizontally, of undisturbed or compacted earth.

(2)  The water service pipe may be closer than 2 440 mm or be placed in the same trench with the building drain or building sewer if

(a)	(i)	the bottom of the water service pipe at all points is at least 500 mm above the top of the building drain or building sewer, and

(ii)	when in a common trench with the building drain or building sewer, the water service pipe is placed on a shelf at one side of the common trench,

(b)	the water service pipe is constructed of a single run of pipe with no joints or fittings between the street line or source of supply on the property and the inside face of the building, or

(c)	the building drain or building sewer is constructed of piping which is pressure tested in accordance with Subsection 7.3.7. at 345 kPa.

(3)  A buried water service pipe shall be constructed of a single run of pipe with no joints or fittings between the street line or source of supply on the property and the inside face of the building if the water service pipe is less than 15 m from

(a)	a private sewage disposal system, or

(b)	a source of pollution other than a private sewage disposal system.

7.3.6. Testing of Drainage and Venting Systems

7.3.6.1.  Tests and Inspection of Drainage or Venting Systems

(1)  Except in the case of an external leader, after a section of drainage system or a venting system has been roughed in, and before any fixture is installed or piping is covered, a water or an air test shall be conducted.

(2)  Where a chief building official requires a final test, it shall be carried out after every fixture is installed and before any part of the drainage system or venting system is placed in operation.

(3)  Where a prefabricated system is assembled off the building site in such a manner that it cannot be inspected and tested on site, off-site inspections and tests shall be conducted.

(4)  Where a prefabricated system is installed as part of a drainage system and venting system, all other plumbing work shall be tested and inspected and a final test shall be carried out on the complete system.

(5)  A ball test shall be carried out on a sanitary building drain, sanitary building sewer, storm building drain and a storm building sewer buried underground.

7.3.6.2.  Tests of Pipes in Drainage Systems

(1)  Every pipe in a drainage system, except an external leader or fixture outlet pipe, shall be capable of withstanding without leakage a water test, air test and final test.

7.3.6.3.  Tests of Venting Systems

(1)  Every venting system shall be capable of withstanding without leakage a water test, air test and final test.

7.3.6.4.  Water Tests

(1)  Where a water test is made it shall be applied to

(a)	the system as a whole, or

(b)	sections of the system, each of which is at least 3 m high and includes at least 1 500 mm of the section below.

(2)  In making a water test

(a)	every opening except the highest shall be tightly closed with a testing plug or a test cap, and

(b)	the system or the section shall be kept filled with water for 15 min.

7.3.6.5.  Air Tests

(1)  Where an air test is made

(a)	every opening in the system shall be closed,

(b)	air shall be forced into the system until a pressure of 35 kPa is created, and

(c)	this pressure shall be maintained for 15 min without the addition of more air.

7.3.6.6.  Final Tests

(1)  Where a final test is made

(a)	every trap shall be filled with water,

(b)	the bottom of the system being tested shall terminate at the building trap, test plug or cap,

(c)	except as provided in Sentence (2), smoke from smoke-generating machines shall be forced into the system,

(d)	when the smoke appears from all roof terminals they shall be closed, and

(e)	a pressure equivalent to a 25 mm water column shall be maintained for 15 min without the addition of more smoke.

(2)  The smoke referred to in Clauses 7.3.6.6.(1)(c) and (d) may be omitted provided the roof terminals are closed and the system is subjected to an air pressure equivalent to a 25 mm water column maintained for 15 min without the addition of more air.

7.3.6.7.  Ball Tests

(1)  Where a ball test is made, a hard ball dense enough not to float shall be rolled through the pipe.

(2)  The diameter of the ball shall be not less than 50 mm where the size of the pipe is 4 in. or more.

7.3.7. Testing of Potable Water Systems

7.3.7.1.  Application of Tests

(1)  After a section of a potable water system has been completed, and before it is placed in operation, a water test or an air test shall be conducted.

(2)  A test may be applied to each section of the system or to the system as a whole.

(3)  Where a prefabricated system is assembled off the building site in such a manner that it cannot be inspected and tested on site, off-site inspections and tests shall be conducted.

(4)  Where a prefabricated system is installed as part of a water system, all other plumbing work shall be tested and inspected, and the complete system shall be pressure tested.

7.3.7.2.  Tests of Potable Water Systems

(1)  Every potable water system shall be capable of

(a)	withstanding without leakage a water pressure that is at least 1000 kPa for at least 1 h, or

(b)	withstanding for at least 2 h without a drop in pressure an air pressure that is at least 700 kPa.

7.3.7.3.  Water Tests

(1)  Where a water test is made all air shall be expelled from the system before fixture control valves or faucets are closed.

(2)  Potable water shall be used to test a potable water system.

Section 7.4. Drainage Systems

7.4.1. Application

7.4.1.1.  Application of Drainage Systems

(1)  This Section applies to sanitary drainage systems and storm drainage systems.

7.4.2. Connections to Drainage Systems

7.4.2.1.  Connections to Sanitary Drainage Systems

(1)  Every fixture shall be directly connected to a sanitary drainage system, except that

(a)	drinking fountains may be

(i)	indirectly connected to a sanitary drainage system, or

(ii)	connected to a storm drainage system provided that where the system is subject to backflow, a check valve is installed in the fountain waste pipe,

(b)	laundry plumbing appliances may be indirectly connected to a sanitary drainage system,

(c)	fixtures or plumbing appliances, other than floor drains, except as provided in Sentence 7.1.5.2.(2), that discharge only clear water waste may be connected to a storm drainage system,

(d)	the following devices shall be indirectly connected to a drainage system

(i)	a device for the display, storage, preparation or processing of food or drink,

(ii)	a sterilizer,

(iii)	a device that uses water as a cooling or heating medium,

(iv)	a water operated device,

(v)	a water treatment device,

(vi)	a drain or overflow from a water system or a heating system, or

(vii)	a drain line from a HVAC system or equipment,

(e)	fixtures that have a hydraulic load totalling not more than 1-1/2 fixture units may be connected to a vertical section of a circuit vent provided

(i)	the fixtures are located in the same storey as the fixtures served by the vent pipes,

(ii)	not more than 2 fixtures are connected to the vent pipe, and

(iii)	where 2 fixtures are connected to the vent pipe, the connection is done with a double fitting in conformance with Table 7.2.4.5.,

(f)	fixtures that have a hydraulic load totalling not more than 1-1/2 fixture units may be connected to the vertical section of a yoke vent provided

(i)	not more than 2 fixtures are connected to the vent pipe, and

(ii)	where 2 fixtures are connected to the vent pipe, the connection is done with a double fitting in conformance with Table 7.2.4.5., and

(g)	fixtures may be connected to a vent stack provided

(i)	the total hydraulic load of the connected fixtures does not exceed 8 fixture units,

(ii)	at least 1 fixture is connected to a vertical portion of the vent stack and upstream of any other fixtures,

(iii)	no other fixture is connected downstream of a water closet, and

(iv)	all fixtures are located in the lowest storey served by the vent stack.

(2)  The connection of a soil or waste pipe to a nominally horizontal soil or waste pipe or to a nominally horizontal offset in a soil or waste stack shall be respectively at least 1 500 mm measured horizontally from the bottom of a soil or waste stack or from the bottom of the upper vertical section of the soil or waste stack that

(a)	receives a discharge of 30 or more fixture units, or

(b)	receives a discharge from fixtures located on 2 or more storeys.

(3)  No other fixture shall be connected to a lead bend or stub that serves a water closet.

7.4.2.2.  Connection of Overflows from Rainwater Tanks

(1)  An overflow from a rainwater tank shall not be directly connected to a storm drainage system.

7.4.2.3.  Direct Connections

(1)  Two or more fixture outlet pipes that serve outlets from a single fixture that is listed in Clause 7.4.2.1.(1)(d) may be directly connected to a branch that

(a)	has a size of at least 1-1/4 in., and

(b)	is terminated above the flood level rim of a directly connected fixture with a minimum diameter waste of 1-1/2 in. to form an air break.

(2)  Fixture drains from fixtures that are listed in Subclauses (i) and (ii) of Clause 7.4.2.1.(1)(d) may be directly connected to a pipe that

(a)	is terminated to form an air break above the flood level rim of a fixture that is directly connected to a sanitary drainage system, and

(b)	is extended through the roof when fixtures that are on 3 or more storeys are connected to it.

(3)  Fixture drains from fixtures that are listed in Subclauses (iii) to (vi) of Clause 7.4.2.1.(1)(d) may be directly connected to a pipe that

(a)	is terminated to form an air break above the flood level rim of a fixture that is directly connected to a storm drainage system, and

(b)	is extended through the roof when fixtures that are on 3 or more storeys are connected to it.

(4)  Every waste pipe carrying waste from a device for the display, storage, preparation or processing of food or drink shall be trapped and have a minimum diameter equal to the diameter of the drain outlet from the device.

7.4.3. Location of Fixtures

7.4.3.1.  Plumbing Fixtures

(1)  Sanitary units, bathtubs and shower baths shall not be installed adjacent to wall and floor surfaces that are pervious to water.

7.4.3.2.  Restricted Locations of Indirect Connections and Traps

(1)  Indirect connections or any trap that may overflow shall not be located in a crawl space or any other unfrequented area.

7.4.3.3.  Equipment Restrictions Upstream of Interceptors

(1)  Except as provided in Sentence (2), garbage grinders, potato peelers and other similar types of equipment shall not be located upstream of an interceptor.

(2)  If a food scrap interceptor has been installed upstream of the grease interceptor, garbage grinders, potato peelers and other similar equipment may discharge through a grease interceptor.

7.4.3.4.  Fixtures Located in Chemical Storage Locations and Elevator Pits

(1)  A floor drain or other fixture located in an oil transformer vault, a high voltage room or any room where flammable, dangerous or toxic chemicals are stored or handled shall not be connected to a drainage system.

(2)  If a floor drain is provided in an elevator pit, it shall be installed in accordance with Section 2.7. of the CAN/CSA-B44, “Safety Code for Elevators, Escalators, Dumbwaiters, Moving Walks and Freight Platform Lifts”.

7.4.4. Treatment of Sewage and Wastes

7.4.4.1.  Sewage Treatment

(1)  Where a fixture or equipment discharges sewage or waste that may damage or impair the sanitary drainage system or the functioning of a sanitary sewage works or sanitary sewage system, provision shall be made for treatment of the sewage or waste before it is discharged to the sanitary drainage system.

7.4.4.2.  Protection for Drainage System

(1)  Where a fixture discharges sewage or clear water waste that has been heated, the drainage system shall be suitable for the temperature of the sewage or clear water waste being discharged.

7.4.4.3.  Interceptors

(1)  Except for suites of residential occupancy, a grease interceptor shall be required anywhere that food is cooked, processed or prepared.

(2)  Except as provided in Sentence (3), oil interceptors shall be provided as follows:

(a)	service stations, repair shops and garages or any establishment where motor vehicles are repaired, lubricated or maintained shall be provided with an oil interceptor, and

(b)	establishments which use oily or flammable liquids or have such wastes as a result of an industrial process shall be provided with an engineered oil interceptor.

(3)  Oil interceptors are not required for a drain in a hydraulic elevator pit, parking lot, car wash or a garage used exclusively as a motor vehicle parking area.

(4)  Where a fixture discharges sand, grit or similar materials, an interceptor designed for the purpose of intercepting such discharges shall be installed.

(5)  Every interceptor shall have sufficient capacity to perform the service for which it is provided.

(6)  An on site constructed interceptor shall be constructed to the requirements of a manufactured interceptor.

(7)  A grease interceptor shall be located as close as possible to the fixture or fixtures it serves.

(8)  The flow rate through a grease interceptor shall not exceed its rated capacity and the flow rate shall be determined using the following:

Q=(1N(0.75VDDT))+PD

where Q is the flow rate to a grease interceptor in L/s,

where V is the volume of the fixture in l,

where DDT is the drain down time, 60 or 120 seconds (1 or 2 minutes),

where PD is any pump discharge in L/s,

where N is the number of fixtures to go through the interceptor.

(9)  All grease and oil interceptors shall have an internal flow control and where the head will exceed five feet, a secondary flow control shall be required.

(10)  Floor drains that conform to Sentence 7.4.5.1.(3) are not required to be separately trapped and vented, and may be gang trapped when discharging through an oil interceptor.

7.4.4.4.  Neutralizing and Dilution Tanks

(1)  Where a fixture or equipment discharges corrosive or acid waste, it shall discharge into a neutralizing or diluting tank which shall be connected to the sanitary drainage system through

(a)	a trap, or

(b)	indirect connection.

(2)  Each neutralizing or diluting tank shall have a method for neutralizing the liquid.

7.4.5. Traps

7.4.5.1.  Traps for Sanitary Drainage Systems

(1)  Except as provided in Sentences (2) and (3) and Article 7.4.5.2., every fixture shall be protected by a separate trap.

(2)  One trap may protect

(a)	all the trays or compartments of a two or three compartment sink,

(b)	a two or three compartment laundry tray, or

(c)	two similar type single compartment fixtures located in the same room.

(3)  One trap may serve a group of floor drains and hub drains, a group of shower drains, a group of washing machines or a group of laboratory sinks if the fixtures

(a)	are in the same room, and

(b)	are not located where they can receive food or other organic matter.

(4)  Reserved

(5)  A grease interceptor shall not serve as a fixture trap and each fixture discharging through the interceptor shall be trapped and vented.

7.4.5.2.  Traps for Storm Drainage Systems

(1)  Where a storm drainage system is connected to a public combined sewer, a trap shall be installed between any opening in the system and the drain or sewer, except that no trap is required if the opening is the upper end of a leader that terminates

(a)	at a roof that is used only for weather protection, and

(b)	at least 900 mm above or at least 3.5 m in any other direction from any air inlet, openable window or door, and at least 2 000 mm from a property line.

7.4.5.3.  Connection of Subsoil Drainage Pipe to a Sanitary Drainage System

(1)  Except as permitted in Sentence (2), no foundation drain or subsoil drainage pipe shall connect to a sanitary drainage system.

(2)  Where a storm drainage system is not available or soil conditions prevent drainage to a culvert or dry well, a foundation drain or subsoil drainage pipe may connect to a sanitary drainage system.

(3)  Where a subsoil drainage pipe may be connected to a sanitary drainage system, the connection shall be made on the upstream side of a trap with a cleanout or a trapped sump.

7.4.5.4.  Location and Cleanout for Building Traps

(1)  Where a building trap is installed, it shall

(a)	be provided with a cleanout fitting on the upstream side of and directly over the trap,

(b)	be located upstream of the building cleanout, and

(c)	be located

(i)	inside the building as close as practical to the place where the building drain leaves the building, or

(ii)	outside the building in a manhole.

7.4.5.5.  Trap Seals

(1)  Provision shall be made for maintaining the trap seal of a floor drain or a hub drain by the use of a trap seal primer, by using the drain as a receptacle for an indirectly connected drinking fountain, or by equally effective means.

(2)  Where a mechanical device is installed to furnish water to a trap, the pipe or tube conveying water from the device to the trap shall be at least 3/8 in. inside diameter.

7.4.6. Arrangement of Drainage Piping

7.4.6.1.  Separate Systems

(1)  No vertical soil or waste pipe shall conduct both sanitary sewage and storm sewage.

(2)  There shall be no unused open ends in a drainage system and dead ends shall be so graded that water will not collect in them.

7.4.6.2.  Location of Soil or Waste Pipes

(1)  A soil or waste pipe shall not be located directly above

(a)	non-pressure potable water storage tanks,

(b)	manholes in pressure potable water storage tanks, or

(c)	food-handling or processing equipment.

7.4.6.3.  Sumps or Tanks

(1)  Only piping that is too low to drain into a building sewer by gravity shall be drained to a sump or receiving tank.

(2)  Where the sump or tank receives sanitary sewage, it shall be water and air-tight and shall be vented.

(3)  Equipment such as a pump or ejector that can lift the contents of the sump or tank and discharge it into the sanitary building drain or sanitary building sewer shall be installed.

(4)  Where the equipment does not operate automatically, the capacity of the sump shall be sufficient to hold at least a 24-hour accumulation of liquid.

(5)  Where there is a building trap, the discharge pipe from the equipment shall be connected to the sanitary building drain downstream of the trap.

(6)  The discharge pipe from every sanitary sewage sump shall be equipped with a union, a check valve and a shut-off valve installed in that sequence in the direction of discharge.

(7)  The discharge piping from a pump or ejector shall be sized for optimum flow velocities at pump design conditions.

7.4.6.4.  Protection from Backflow

(1)  A backwater valve or a gate valve shall not be installed in a building drain or in a building sewer.

(2)  Except as provided in Sentences (3), (4) and (5), where a building drain or a branch may be subject to backflow, a gate valve or a backwater valve shall be installed on every fixture drain connected to them when the fixture is located below the level of the adjoining street.

(3)  Where the fixture is a floor drain, a removable screw cap or other device may be installed on the upstream side of the trap.

(4)  Where more than one fixture is located on a storey and all are connected to the same branch, the gate valve or backwater valve may be installed on the branch.

(5)  A subsoil drainage pipe that drains into a sanitary drainage system that is subject to surcharge shall be connected in such a manner that sewage cannot back up into the subsoil drainage pipe.

7.4.6.5.  Mobile Home Sewer Service

(1)  A building sewer intended to serve a mobile home shall

(a)	be not less than 4 in. in size,

(b)	be terminated above ground,

(c)	be provided with

(i)	a tamperproof terminal connection that is capable of being repeatedly connected, disconnected and sealed,

(ii)	a protective concrete pad, and

(iii)	a means to protect it from frost heave, and

(d)	be designed and constructed in accordance with good engineering practice.

7.4.6.6.  Building Drain Ends

(1)  Where a building drain enters a building above the elevation of the bottom of the wall of a building, the building drain may be deemed to terminate at the first point that the drainage pipe changes direction from the horizontal to the vertical.

7.4.7. Cleanouts

7.4.7.1.  Cleanouts for Drainage Systems

(1)  Every sanitary drainage system and storm drainage system shall be provided with cleanouts that will permit cleaning of the entire system.

(2)  A cleanout fitting shall be provided on the upstream side and directly over every running trap.

(3)  Every interior leader shall be provided with a cleanout fitting at the bottom of the leader or not more than 1 000 mm upstream from the bottom of the leader.

(4)  Where a cleanout is required on a building sewer 8 in. or larger in size, it shall be a manhole.

(5)  Where there is a change of direction greater than 45° in a sanitary building drain or a sanitary building sewer, a cleanout shall be installed at each change in direction.

(6)  Every sanitary building drain or storm building drain shall be provided with a cleanout fitting that is located as close as practical to the place where the drain leaves the building.

(7)  Every soil or waste stack shall be provided with a cleanout fitting

(a)	at the bottom of the stack,

(b)	not more than 1 000 mm upstream of the bottom of the stack, or

(c)	on a Y fitting connecting the stack to the building drain or branch.

(8)  A cleanout shall be provided to permit the cleaning of the piping immediately downstream of an interceptor.

(9)  Every indirect drainage pipe carrying waste from a food receptacle shall have a cleanout access at every change of direction of more than 45°.

(10)  A cleanout shall be installed on a fixture drain serving a kitchen sink.

7.4.7.2.  Size and Spacing of Cleanouts

(1)  Except as provided in Sentences (2) and (3), on drainage piping of 4 in. size and smaller, the minimum size cleanout opening shall be the same size as the drainage pipe and on drainage piping larger than the 4 in. size, the cleanout opening shall be 4 in. or larger and the maximum spacing between cleanouts on horizontal pipe shall be

(a)	in the case of a sink waste pipe, 6 m,

(b)	in the case of a horizontal sanitary drainage pipe, or storm drainage pipe, other than a waste pipe from a sink, 15 m, and

(c)	in the case of a horizontal sanitary drainage pipe or storm drainage pipe larger than 4 in. size, 30 m.

(2)  The spacing between manholes serving a building sewer

(a)	24 in. or less in size shall not exceed 90 m, and

(b)	over 24 in. in size shall not exceed 150 m.

(3)  The developed length of a building sewer between the building and the first manhole to which the building sewer connects shall not exceed 30 m.

(4)  Cleanouts capable of rodding in one direction only shall be installed to rod in the direction of flow.

(5)  Manholes shall be located at all junctions, all changes in grade, size or alignment (except for curvilinear alignment) on a sanitary building sewer.

(6)  Manholes shall be located at changes of grade, size or alignment (except for curvilinear alignment) on a storm building sewer.

7.4.7.3.  Manholes

(1)  A manhole including the cover shall be designed to support all loads imposed upon it.

(2)  A manhole shall be provided with

(a)	a cover which shall provide an airtight seal if located within a building,

(b)	a rigid ladder of a corrosion-resistant material where the depth exceeds 1 000 mm, and

(c)	a vent to the exterior if the manhole is located within a building.

(3)  A manhole shall have a minimum horizontal dimension of 1 200 mm, except that the top 1 500 mm may be tapered from 1 200 mm down to a minimum of 600 mm at the top.

(4)  A manhole in a sanitary drainage system shall be channelled to direct the flow of effluent.

7.4.7.4.  Location of Cleanouts

(1)  Cleanouts and access covers shall be located so that the openings are readily accessible for rodding and cleaning purposes.

(2)  A cleanout shall not be located in a floor assembly in a manner that may constitute a hazard and shall not be used as a floor drain.

(3)  Reserved

(4)  Each change of direction of the piping between a cleanout fitting and the drainage piping or vent piping that it serves shall be accomplished by using 45o bends.

(5)  A cleanout shall be provided to serve vertical drainage piping from a wall hung urinal and shall extend above the flood level rim of the fixture.

7.4.8. Minimum Slope and Length of Drainage Pipes

7.4.8.1.  Minimum Slope

(1)  Every drainage pipe that has a size of 3 in. or less, and every fixture drain shall have a downward slope in the direction of flow of at least 1 in 50.

(2)  Sentence (1) does not apply to a force main.

7.4.8.2.  Length of Fixture Outlet Pipe

(1)  Except as provided in Sentence 7.4.5.1.(3), the developed length of every fixture outlet pipe shall not exceed 900 mm.

7.4.9. Size of Drainage Pipes

7.4.9.1.  No Reduction in Size

(1)  Except as permitted in Sentence (3), no soil or waste pipe that is of minimum size required by this Part for the purpose for which it is installed shall be so connected as to drain to other drainage pipe of lesser size.

(2)  Where a building drain connects to a stack through a wall or floor, the drain shall retain its full size through the wall or floor.

(3)  A sanitary drainage pipe may be connected to a pre-engineered wastewater heat recovery system that incorporates piping of a lesser size than required by Sentence (1) provided that it does not convey sewage

(a)	from a sanitary unit, or

(b)	that contains solids.

7.4.9.2.  Serving Water Closets

(1)  The size of every drainage pipe that serves a water closet shall be at least 3 in.

(2)  The size of every horizontal branch downstream of the third water closet fixture drain connection shall be at least 4 in.

(3)  The size of every soil stack that serves more than 6 water closets shall be at least 4 in.

7.4.9.3.  Size of Fixture Outlet Pipes

(1)  Except as provided in Sentence (2) the size of every fixture outlet pipe shall conform to Table 7.4.9.3.

(2)  The part of the fixture outlet pipe that is common to 3 compartments of a sink shall be one size larger than the largest fixture outlet pipe of the compartments that it serves.

7.4.9.4.  Minimum Size of Building Drains and Sewers

(1)  Except as permitted in Sentence (3), no soil or waste pipe that is of minimum size required by this Part for the purpose for which it is installed shall be so connected as to drain to other drainage pipe of lesser size.

(2)  Every storm building drain and every storm building sewer shall be at least 4 in. size.

Table 7.4.9.3.

Minimum Permitted Size of Fixture Outlet Pipe and Hydraulic Loads for Fixtures

Forming Part of Sentences 7.4.9.3.(1) and 7.4.10.2.(1)

| Fixture | Min. Size of Fixture Outlet Pipe, in. | Hydraulic Load, fixture units |
| --- | --- | --- |
| Autopsy table | 1½ | 2 |
| Bathroom group |  |  |
| (a) with flush tank |  | 6 |
| (b) with direct flush valve |  | 8 |
| Bathtub (with or without shower) | 1½ | 1½ |
| Bath: foot, sitz or slab | 1½ | 1½ |
| Bed pan washer | 3 | 6 |
| Beer cabinet | 1½ | 1½ |
| Bidet | 1¼ | 1 |
| Chinese range | 1½ | 3 |
| Clothes washer |  |  |
| (a) domestic | N/A | 1½ with 1½ in. trap |
| (b) commercial | N/A | 2 with 1½ in. trap |
| Dental unit or cuspidor | 1¼ | 1 |
| Dishwasher |  | ½ |
| (a) domestic | 1½ | no load when connected to garbage grinder or domestic sink |
| (b) commercial type | 2 | 3 |
| Drinking fountain | 1¼ | ½ |
| Fish tank or tray | 1½ | 1½ |
| Floor drain | 2 | 2 with 2 in. trap 3 with 3 in. trap |
| Garbage grinder, commercial type | 2 | 3 |
| Icebox | 1¼ | 1 |
| Laundry tray |  |  |
| (a) single or double units or 2 single units with common trap | 1½ | 1½ |
| (b) 3 compartments | 1½ | 2 |
| Lavatory |  |  |
| (a) barber or beauty parlour | 1½ | 1½ |
| (b) dental | 1¼ | 1 |
| (c) domestic type single, or 2 single with common trap | 1¼ | 1 with 1¼ in. trap 1½ with 1½ in. trap |
| (d) multiple or industrial type | 1½ | 3 |
| Potato Peeler | 2 | 3 |
| Shower drain |  |  |
| (a) from 1 head | 1½ | 1½ |
| (b) from 2 or 3 heads | 2 | 3 |
| (c) from 4 to 6 heads | 3 | 6 |
| Sink |  |  |
| (a) domestic and other small type with or without garbage grinders, single, double or 2 single with a common trap | 1½ | 1½ |
| (b) other sinks | 1½ | 1½ with 1½ in. trap 2 with 2 in. trap 3 with 3 in. trap |
| Urinal |  |  |
| (a) pedestal, siphon jet or blowout type | 2 | 4 |
| (b) stall, washout type | 2 | 2 |
| (c) wall |  |  |
| (i) washout type | 1½ | 1½ |
| (ii) other types | 2 | 3 |
| Water closet |  |  |
| (a) with flush tank | 3 | 4 |
| (b) with direct flush | 3 | 6 |
| Column 1 | 2 | 3 |

7.4.10. Hydraulic Loads

7.4.10.1.  Total Load on a Pipe

(1)  The hydraulic load on a pipe is the total load from

(a)	every fixture that is connected to the system upstream of the pipe, and

(b)	every fixture for which provision is made for future connection upstream of the pipe.

7.4.10.2.  Hydraulic Loads for Fixtures

(1)  The hydraulic load from a fixture that is listed in Table 7.4.9.3. is the number of fixture units set forth in the Table.

(2)  Except as provided in Sentence (1), the hydraulic load from a fixture that is not listed in Table 7.4.9.3. is the number of fixture units set forth in Table 7.4.10.2. for the size of the trap that serves the fixture.

Table 7.4.10.2.

Permitted Hydraulic Load from a Fixture Based on Size of Trap

Forming Part of Sentence 7.4.10.2.(2)

| Size of Trap, in. | Hydraulic Load, fixture units |
| --- | --- |
| 1¼ | 1 |
| 1½ | 2 |
| 2 | 3 |
| 2½ | 4 |
| 3 | 5 |
| 4 | 6 |
| Column 1 | 2 |

7.4.10.3.  Fixture Loading for Horizontal Drain

(1)  No horizontal sanitary drainage pipe of less than 3 in. size shall have a fixture loading in excess of that permitted by Table 7.4.10.3.A.

Table 7.4.10.3.A.

Maximum Permitted Hydraulic Load Drained to a Branch

Forming Part of Sentence 7.4.10.3.(1)

| Size of Branch, in. | Maximum Load, fixture units |
| --- | --- |
| 1¼ | 2 |
| 1½ | 4 |
| 2 | 6 |
| Column 1 | 2 |

(2)  Reserved

(3)  The horizontal sanitary drainage pipe size shall be that size determined from Table 7.4.10.3.C. after the total connected load in fixture units on a horizontal sanitary drainage pipe is converted to gallons per minute in accordance with Table 7.4.10.3.B.

(4)  Horizontal sanitary drainage pipe shall be designed to carry no more than 65% of its full capacity.

Table 7.4.10.3.B.

Maximum Probable Drainage Rate, gal/min

Forming Part of Sentences 7.4.10.3.(3), 7.4.10.4.(1), 7.4.10.5.(3)

| Fixture Units in Service | Fixture Units Col. 1 | Fixture Units Col. 1 x 10 | Fixture Units Col. 1 x 100 |
| --- | --- | --- | --- |
| 100 | 53 | 174 | 900 |
| 90 | 51 | 164 | 835 |
| 80 | 49 | 153 | 750 |
| 70 | 47 | 140 | 680 |
| 60 | 44 | 128 | 600 |
| 50 | 41 | 115 | 520 |
| 40 | 38 | 102 | 435 |
| 30 | 33 | 88 | 350 |
| 20 | 27 | 72 | 262 |
| 10 | 21 | 53 | 174 |
| Column 1 | 2 | 3 | 4 |

Table 7.4.10.3.C.

Capacity of Horizontal Drainage Pipe, gal/min

Forming Part of Sentences 7.4.10.3.(3) and 7.4.10.4.(1)

| Drain Size, Nominal in. | Loading | Slope(1) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1:400 | 1:200 | 1:125 | 1:100 | 1:50 | 1:25 |
| 3 | 65% Full |  |  |  |  | 46 | 67 |
| 4 | 65% Full |  |  |  | 63 | 91 | 132 |
| 5 | 65% Full |  | 81 | 96 | 116 | 165 | 240 |
| 6 | 65% Full | 94 | 127 | 156 | 185 | 272 | 396 |
| 8 | 65% Full | 182 | 269 | 341 | 390 | 578 | 835 |
| 10 | 65% Full | 347 | 507 | 618 | 735 | 1050 | 1540 |
| 12 | 65% Full | 585 | 825 | 975 | 1180 | 1750 | 2460 |
| 15 | 65% Full | 720 | 1010 | 1180 | 1390 | 1990 | 2790 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |

Note to Table 7.4.10.3.C.:

(1) Slope is the ratio of rise to run, in whatever measurement units are chosen.

7.4.10.4.  Hydraulic Loads from Continuous Flows

(1)  For the purposes of determining the size of sanitary drainage pipe in accordance with Table 7.4.10.3.C., pumped discharge and other continuous or semi-continuous flows shall be calculated in gallons per minute and added to the drainage rate in gallons per minute from Table 7.4.10.3.B.

7.4.10.5.  Hydraulic Loads for Vertical Drains

(1)  No vertical waste pipe, branch or stack of less than 3 in. diameter shall have a hydraulic load in excess of that permitted by Table 7.4.10.5.A.

(2)  Reserved

(3)  The vertical sanitary drainage pipe size shall be that size determined from Table 7.4.10.5.B. after the total connected load in fixture units on a vertical drainage pipe is converted to gallons per minute in accordance with Table 7.4.10.3.B.

(4)  Vertical sanitary drainage pipe shall be designed to carry no more than 33% of its full capacity.

Table 7.4.10.5.A.

Maximum Load on Vertical Drainage Pipe, fixture units

Forming Part of Sentence 7.4.10.5.(1)

| Pipe Size, in. | Stack Height 3 Storeys or less | Stack Height more than 3 Storeys | For Each Storey in Stack of more than 3 Storeys |
| --- | --- | --- | --- |
| 1¼ | 3 | 3 | 3 |
| 1½ | 8 | 8 | 5 |
| 2 | 16 | 24 | 10 |
| Column 1 | 2 | 3 | 4 |

7.4.10.6.  Hydraulic Loads from Roofs or Paved Surfaces

(1)  Except as provided in Sentence (2), the hydraulic load in litres from a roof or paved surface is the maximum 15 mm rainfall determined in accordance with Subsection 2.5.1., multiplied by the sum of

(a)	the area in square metres of horizontal projection of the surface drained, and

(b)	one-half the area in square metres of the largest adjoining vertical surface.

(2)  Flow control roof drains may be installed provided,

(a)	the maximum drain down time does not exceed 24 h,

(b)	the roof structure has been designed to carry the load of the stored water,

(c)	one or more scuppers are installed so that the maximum depth of water on the roof cannot exceed 150 mm,

(d)	they are located not more than 15 m from the edge of the roof, and not more than 30 m from adjacent drains, and

(e)	there is at least one drain for each 900 m2.

(3)  Hydraulic loads in litres per second for flow control roof drains and restricted paved area drains shall be determined according to rain intensity-duration frequency curves as compiled by Environment Canada, using 25-year frequencies.

Section 7.5. Venting Systems

7.5.1. Vent Pipes for Traps

7.5.1.1. Venting for Traps

(1)  Except as provided in Sentences (2) and (3) and Article 7.5.2.1., every trap shall be vented.

(2)  A trap that serves a floor drain or hub drain, directly connected to a sanitary building drain is not required to be vented where

(a)	the size of the trap is at least 3 in.,

(b)	the length of the fixture drain is at least 900 mm,

(c)	the total fall on the fixture drain does not exceed its inside diameter, and

(d)	the minimum slope on a 3 in. fixture drain is 1 in 50 and on sizes larger than 3 in. is 1 in 100.

(3)  A trap is not required to be vented where

(a)	it serves a subsoil drainage pipe,

(b)	it serves a storm drainage system, or

(c)	it forms part of an indirect drainage system, less than three storeys high.

Table 7.4.10.5.B.

Maximum Load on Vertical Drainage Pipe in GPM and Maximum Length of Vent Stacks

Forming Part of Sentences 7.4.10.5.(3), 7.5.3.2.(3) and 7.5.7.2.(1)

| Stack Size, in. (Drain) | Water Occupied Area | Flow Rate, gal/min | Vent Stack Size, in. and Maximum Length, metres |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 1½ | 2 | 2½ | 3 | 4 | 5 | 6 | 8 | 10 | 12 | 14 |
| 3 | 0.15 | 18.4 | 12.8 | 44.2 | 108.0 | 317.0 |  |  |  |  |  |  |  |
|  | .20 | 29.4 | 9.8 | 33.5 | 82.3 | 245.4 |  |  |  |  |  |  |  |
|  | .25 | 43.0 | 8.2 | 28.7 | 70.1 | 207.3 |  |  |  |  |  |  |  |
|  | .29 | 55.7 | 7.6 | 26.2 | 64.0 | 189.0 |  |  |  |  |  |  |  |
|  | .30 | 58.4 | 7.3 | 25.9 | 62.5 | 185.9 |  |  |  |  |  |  |  |
|  | .33 | 69.5 | 7.0 | 24.7 | 61.0 | 178.3 |  |  |  |  |  |  |  |
| 4 | 0.15 | 39.6 |  | 10.7 | 25.9 | 76.2 | 297.2 |  |  |  |  |  |  |
|  | .20 | 64.0 |  | 8.2 | 19.8 | 59.4 | 228.6 |  |  |  |  |  |  |
|  | .25 | 92.5 |  | 7.0 | 16.8 | 50.3 | 193.5 |  |  |  |  |  |  |
|  | .29 | 120.0 |  | 6.4 | 15.2 | 45.7 | 176.8 |  |  |  |  |  |  |
|  | .30 | 126.0 |  | 6.1 | 14.9 | 44.8 | 173.7 |  |  |  |  |  |  |
|  | .33 | 150.0 |  | 5.8 | 14.3 | 42.7 | 166.1 |  |  |  |  |  |  |
| 5 | 0.15 | 72.0 |  |  | 8.5 | 25.0 | 97.5 | 300.2 |  |  |  |  |  |
|  | .20 | 116.0 |  |  | 6.4 | 19.2 | 74.7 | 231.6 |  |  |  |  |  |
|  | .25 | 168.0 |  |  | 5.5 | 16.2 | 63.1 | 195.1 |  |  |  |  |  |
|  | .29 | 217.0 |  |  | 4.9 | 14.9 | 57.6 | 178.3 |  |  |  |  |  |
|  | .30 | 228.0 |  |  | 4.9 | 14.6 | 56.7 | 175.3 |  |  |  |  |  |
|  | .33 | 272.0 |  |  | 4.6 | 14.0 | 54.6 | 169.2 |  |  |  |  |  |
| 6 | 0.15 | 117.0 |  |  |  | 10.1 | 39.6 | 121.9 | 304.8 |  |  |  |  |
|  | .20 | 189.0 |  |  |  | 7.9 | 30.5 | 94.5 | 236.2 |  |  |  |  |
|  | .25 | 274.0 |  |  |  | 6.7 | 25.6 | 79.2 | 199.6 |  |  |  |  |
|  | .29 | 354.0 |  |  |  | 6.1 | 23.5 | 73.2 | 181.4 |  |  |  |  |
|  | .30 | 370.0 |  |  |  | 5.8 | 23.2 | 71.6 | 179.8 |  |  |  |  |
|  | .33 | 441.0 |  |  |  | 5.8 | 22.3 | 68.6 | 172.2 |  |  |  |  |
| 8 | 0.15 | 251.0 |  |  |  |  | 9.4 | 29.0 | 73.2 | 286.5 |  |  |  |
|  | .20 | 406.0 |  |  |  |  | 7.3 | 22.3 | 56.4 | 219.5 |  |  |  |
|  | .25 | 589.0 |  |  |  |  | 6.1 | 18.9 | 47.2 | 185.9 |  |  |  |
|  | .29 | 762.0 |  |  |  |  | 5.5 | 17.1 | 42.7 | 169.2 |  |  |  |
|  | .30 | 798.0 |  |  |  |  | 5.5 | 17.1 | 42.7 | 167.6 |  |  |  |
|  | .33 | 950.0 |  |  |  |  | 5.2 | 16.2 | 41.1 | 160.0 |  |  |  |
| 10 | 0.15 | 455.0 |  |  |  |  |  | 9.4 | 23.8 | 93.0 | 292.6 |  |  |
|  | .20 | 736.0 |  |  |  |  |  | 7.3 | 18.3 | 71.6 | 224.0 |  |  |
|  | .25 | 1070.0 |  |  |  |  |  | 6.1 | 15.5 | 61.0 | 190.5 |  |  |
|  | .29 | 1380.0 |  |  |  |  |  | 5.5 | 14.0 | 54.9 | 173.7 |  |  |
|  | .30 | 1440.0 |  |  |  |  |  | 5.5 | 14.0 | 54.9 | 170.7 |  |  |
|  | .33 | 1730.0 |  |  |  |  |  | 5.2 | 13.4 | 51.8 | 163.1 |  |  |
| 12 | 0.15 | 740.0 |  |  |  |  |  |  | 9.4 | 36.6 | 115.8 | 286.5 |  |
|  | .20 | 1200.0 |  |  |  |  |  |  | 7.3 | 28.7 | 89.9 | 219.5 |  |
|  | .25 | 1730.0 |  |  |  |  |  |  | 6.1 | 24.1 | 76.2 | 185.9 |  |
|  | .29 | 2240.0 |  |  |  |  |  |  | 5.5 | 21.9 | 68.6 | 169.2 |  |
|  | .30 | 2350.0 |  |  |  |  |  |  | 5.5 | 21.6 | 68.6 | 167.6 |  |
|  | .33 | 2800.0 |  |  |  |  |  |  | 5.2 | 20.7 | 65.5 | 160.0 |  |
| 15 | 0.15 | 1340.0 |  |  |  |  |  |  |  | 12.2 | 38.1 | 93.0 | 146.3 |
|  | .20 | 2170.0 |  |  |  |  |  |  |  | 9.4 | 29.3 | 71.6 | 112.8 |
|  | .25 | 3140.0 |  |  |  |  |  |  |  | 7.9 | 24.7 | 61.0 | 94.5 |
|  | .29 | 4070.0 |  |  |  |  |  |  |  | 7.3 | 22.6 | 54.9 | 88.4 |
|  | .30 | 4260.0 |  |  |  |  |  |  |  | 7.0 | 22.3 | 54.9 | 85.3 |
|  | .33 | 5080.0 |  |  |  |  |  |  |  | 6.7 | 21.3 | 51.8 | 82.3 |
| Col. 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |

7.5.2. Stack Venting & Modified Stack Venting, Circuit Venting and Relief Venting

7.5.2.1.  Vertical Stacks

(1)  A vertical soil stack that is not less than 3 inches diameter that is extended as a stack vent shall be deemed to vent a fixture trap where the connection of the fixture drain meets the following requirements:

(a)	the number of stack vented fixtures connected to one stack above the water closet is not greater than 4,

(b)	all fixtures of the stack vented group numbering four or less above the water closet are on the same floor level or storey and the stack receives no waste at a higher level,

(c)	the number of stack vented water closets is not greater than 2,

(d)	where two water closets are installed, they are connected at the same level to a vertical part of the stack,

(e)	where there are two water closets in a stack vented group and they are installed as described in Clause (d), the remaining fixtures of the group are connected directly and independently to the stack above the centre-line of the connection of the two water closets and the uppermost fixture is connected to the vertical portion of the stack,

(f)	where there is only one water closet in the stack vented group it is connected to the vertical stack or the horizontal continuation of the stack and the remaining fixtures upstream of the water closet are connected directly and independently to the stack and the uppermost fixture is connected to the vertical portion of the stack,

(g)	the total number of fixture units connected above the water closet is not greater than 8, and

(h)	no fixture drain connected above the water closet is of more than 2 in. trade size and is not serving a siphonic trap.

7.5.2.2.  Horizontal Branches and Relief Vents

(1)  A horizontal branch off a stack or off a sanitary building drain may be circuit vented where

(a)	the circuit vented branch is of a size 3 in. or greater,

(b)	the number of circuit vented fixtures is less than 7 per vent and in any group of 6 or less circuit vented fixtures all but the last of the group are downstream of the point where the circuit vent connects to the branch,

(c)	the circuit vented fixture is a sanitary unit, floor drain, hub drain, shower drain or trap standard slop sink,

(d)	all fixtures connected to the circuit vented branch are on the same floor level,

(e)	no soil or waste stack connects to the circuit vented branch,

(f)	no circuit vented trap has a horizontal run of waste pipe of more than 1 500 mm, and

(g)	in a water closet installation, no circuit vented trap has a horizontal run of waste pipe of more than 1 500 mm nor a vertical run of more than 900 mm.

(2)  Where a stack or a sanitary building drain has a circuit vented branch connected to it and the stack or sanitary building drain carries more than eight fixture units of drainage upstream of the connection or has connected to it a sanitary drainage pipe larger than 2 in. size or receives drainage from a higher floor level, the circuit vented branch shall be relief vented.

(3)  A relief vent required by Sentence (2) may be a wet vent if it is of 2 in. size or greater and not more than one fixture having a maximum of 1-1/2 fixture units is drained into it.

(4)  Where circuit vented fixture traps are connected to 2 or more horizontal branches that connect to the same horizontal branch, the horizontal branches may have a combined relief vent.

7.5.3. Vent Pipes for Soil or Waste Stacks

7.5.3.1.  Stack Vents

(1)  The upper end of every soil or waste stack shall terminate in a stack vent and the stack vent shall terminate in open air outside the building or connect directly or through a header to another stack vent or vent stack that does terminate in open air outside the building.

7.5.3.2.  Vent Stacks

(1)  Except as provided in Sentence (2), where back vents, relief vents or circuit vents are installed in two or more storeys served by a soil stack or waste stack, a vent stack shall be installed in conjunction with the soil or waste stack.

(2)  A vent stack is not required to be installed in conjunction with the soil or waste stack in a residential building of 3 storeys or less.

(3)  A vent stack shall

(a)	have its lower end connected to

(i)	the waste stack or soil stack at or below the lowest horizontal sanitary drainage pipe connected to the waste stack or soil stack, or

(ii)	the sanitary building drain immediately downstream of the stack connection,

(b)	extend to the open air independently or through a header,

(c)	except as provided for in Clause (d), where it is connected to the soil stack, waste stack or sanitary building drain, of a size and length as determined from Table 7.4.10.5.B., and

(d)	at each point of interconnection with a branch vent be not smaller than the minimum size permitted by Table 7.5.7.2.

(4)  Where a plumbing system is installed in a building, every storey in which plumbing is or may be installed, including the basement of a single family dwelling, shall have extended into it or passing through it a vent pipe that is at least 1-1/2 in. size for the provision of future connections.

(5)  Where a single family dwelling, built prior to April 7, 1976, has a vent pipe installed in the basement that is at least 1-1/4 in. trade size and there is no larger vent pipe in the area, the 1-1/4 in. pipe may be used to vent one water closet and one wash basin where both fixtures are located in the basement and where the vent connecting the water closet or the wash basin and the water closet to the vent pipe is at least 1-1/2 in. trade size.

(6)  Where a vent stack is installed as a result of additions or alterations to a plumbing system in an existing building, the vent stack may be erected outside the building, provided that

(a)	no single change of direction of the stack exceeds 45°,

(b)	all parts of the stack are vertical,

(c)	the stack terminates above the roof of the building where the building is 4 storeys in height or less, and

(d)	the requirements set out in Sentence 7.5.5.5.(3) are met.

7.5.3.3.  Yoke Vents

(1)  Except as provided in Sentence (4), where a soil stack or a waste stack receives the discharge from fixtures located on more than eleven storeys, a yoke vent shall be installed

(a)	for each section of five storeys or part thereof counted from the top down, and

(b)	at or immediately above each offset or double offset.

(2)  The yoke vent shall be connected to the soil or waste stack by means of a drainage fitting at or immediately below the lowest soil or waste pipe from the lowest storey of the section described in Sentence (1).

(3)  The yoke vent shall connect to the vent stack at least 1 000 mm above the floor level of the lowest storey in the section described in Sentence (1).

(4)  A yoke vent is not required to be installed where the soil or waste stack is interconnected to the vent stack in each storey by means of a fixture or a group of vented fixtures installed in accordance with Subsection 7.5.2.

7.5.4. Miscellaneous Vent Pipes

7.5.4.1.  Venting of Sanitary Sewage Sumps

(1)  Every tank that receives sanitary sewage shall be provided with a vent pipe that is connected to the top of the tank and that is sized in accordance with Article 7.5.6.5.

7.5.4.2.  Venting of Interceptors

(1)  Every oil interceptor shall be provided with two vent pipes that

(a)	connect to the interceptor at opposite ends,

(b)	extend independently to open air,

(c)	terminate at least 2 000 mm above ground and at elevations differing by at least 300 mm, and

(d)	do not connect to each other or any other vent pipe.

(2)  Adjacent compartments within an oil interceptor shall be connected to each other by a vent opening.

(3)  Every grease interceptor shall have a vent pipe that is at least 1-1/2 in. size connected to the outlet pipe, that connects to the plumbing venting system.

(4)  A vent pipe shall be provided within 1 500 mm of the inlet to a grease interceptor complete with a cleanout to provide cleaning of the vent pipe.

(5)  Where a secondary receiver is installed in conjunction with an oil interceptor, it shall be vented as per manufacturer’s recommendations, but in no case shall the vent be less than 1-1/2 in. trade size and shall extend independently to open air.

(6)  Where an acid waste dilution tank is installed, it shall be provided with a vent pipe connected at the top of the tank and that is sized in accordance with Article 7.5.6.5.

(7)  Where a manufacturer of an oil interceptor makes no recommendations with respect to the size of the vent pipe venting an oil interceptor, the interceptor shall be vented at each end with a vent pipe that is not more than one size smaller than the largest connected drainage pipe and not less than 1-1/4 in. nominal pipe size.

(8)  Every vent pipe serving an oil interceptor that is built in location shall be at least 3 in. size throughout its length.

(9)  Every vent pipe serving an oil or grease interceptor that is located outside a building shall be a minimum 3 in. size.

7.5.4.3.  Fresh Air Inlet

(1)  Where a building trap is installed in a plumbing system, a fresh air inlet not less than 4 in. size shall be connected upstream of the building trap and within 1 200 mm of the building trap and downstream of any other connection.

7.5.4.4.  Venting of Corrosive Drain Piping and Dilution Tanks

(1)  Vents connecting to the corrosive drain piping or dilution tank shall extend independently to and terminate in open air.

7.5.5. Arrangement of Vent Pipes

7.5.5.1.  Drainage of Vent Pipes

(1)  Every waste pipe shall be installed and back vented at the same time.

(2)  Every vent pipe shall be installed without a sag or depression and shall have no unused open ends.

7.5.5.2.  Vent Pipe Connections

(1)  Every vent pipe in a plumbing system shall be installed so as to be direct as possible to a vent stack or open air, as the case may be, and so that any horizontal run below the flood level of the fixture to which the vent pipe is installed is eliminated where structurally possible.

(2)  Except as provided in Sentence (3), where a vent pipe is connected to a nominally horizontal soil or waste pipe, the connection shall be above the horizontal centre line of the soil or waste pipe.

(3)  A wet vent is not required to be connected above the horizontal centre line of the soil or waste pipe.

7.5.5.3.  Location of Vent Pipes

(1)  Except as provided in Sentences (2) and (3), a vent pipe that protects a fixture trap shall be so located that

(a)	the developed length of a fixture drain measured from the trap weir is

(i)	not less than twice the pipe size of the fixture drain, and

(ii)	not more than 1 500 mm,

(b)	the total fall of the fixture drain from a P-trap is not greater than the size of the fixture drain,

(c)	no fixture drain has a cumulative change of direction of more than 135°, and

(d)	except as permitted in Article 7.5.7.1., no waste pipe is connected to the fixture drain between the trap and its protecting vent.

(2)  No fixture drain of a water closet, S-trap standard or a fixture that depends on siphonic action for the proper functioning of the fixture and that discharges vertically shall have a cumulative change of direction of more than 225°.

(3)  No vertical leg of the waste pipe from a water closet or other fixture that has an integral siphonic flushing action shall exceed 900 mm.

(4)  The vent pipe from a water closet or other fixture that has an integral siphonic flushing action may be connected to the vertical leg of its waste pipe.

7.5.5.4.  Connection of Vents Above Fixtures Served

(1)  The upper end of every vent pipe shall be above the flood level of the highest fixture it serves before connection to another vent pipe.

(2)  No vent piping shall be so arranged that it will serve as a bypass in the event of an obstruction in the drainage pipe.

7.5.5.5.  Terminals

(1)  The upper end of every vent pipe that is not terminated in open air shall be connected to a venting system that is terminated in open air.

(2)  A vent pipe that serves an oil interceptor, a vent stack that is permitted by Sentence 7.5.3.2.(6), a vent stack and a stack vent shall each terminate in open air as set out in Sentence (3).

(3)  The terminal of a vent pipe shall be located

(a)	at least 900 mm above or 3.5 m in any other direction from air inlet, openable window or door,

(b)	at least 150 mm above the roof of the building where the vent is installed and, where storm water is intended to pond on the roof, at least 150 mm above the high water level, and

(c)	at least 2 000 mm above the roof of the building that the vent is installed in, where the roof is intended for human occupancy.

(4)  Clause (3)(a) does not apply to a fresh air inlet pipe.

(5)  Where a vent pipe is located 2 000 mm or more above a roof, it shall be so constructed as to be stable and secure.

(6)  Where a stack or vent pipe passes through a roof or a wall, the stack or vent pipe shall be equipped with a flashing so installed that no storm water can pass between the structure and the flashing or between the flashing and the pipe or stack.

(7)  Flashing shall be of material specified in Article 7.2.10.14. and on a shingled roof shall have a minimum dimension of 500 mm by 500 mm.

(8)  Where a sleeve flashing is installed on a flat roof, it shall extend at least 150 mm above the flood level and on a sloped roof shall be at least 150 mm high on the short side.

(9)  No bore of a vent stack or stack vent shall be reduced or obstructed by the installation of a flashing.

(10)  Where a vent pipe passes through a roof or an outside wall of a building, it shall be increased to a minimum size of 3 in. before penetrating the roof or wall.

7.5.6. Minimum Size of Vent Pipes

7.5.6.1.  General

(1)  Except as provided in Article 7.5.3.1. and 7.5.7.1, where a vent pipe vents one or more fixture traps, the pipe size of the vent pipe shall be in accordance with Table 7.5.6.1.

Table 7.5.6.1.

Minimum Permitted Size of Vent Pipe Based on Size of Trap

Forming Part of Sentence 7.5.6.1.(1)

| Size of Trap Served, in. | Minimum Size of Vent Pipe, in. |
| --- | --- |
| 1¼ | 1¼ |
| 1½ | 1¼ |
| 2 | 1½ |
| 2½ | 1½ |
| 3 | 1½ |
| 4 | 1½ |
| 5 | 2 |
| 6 | 2 |
| Column 1 | 2 |

(2)  Every relief vent or circuit vent shall be at least 2 in. size.

7.5.6.2.  Size Restriction

(1)  Except as provided in Sentence 7.5.3.2.(5), no branch vent, stack vent, vent stack or header shall be a size less than the size of the largest vent pipe connected to it.

(2)  Every sanitary building drain shall terminate at its upstream end in a stack of at least 3 in. size.

(3)  A stack referred to in Sentence (2) shall be a soil stack if one is available and may be a vent stack or waste stack that provides at least 3 in. stack vent and that goes to open air above the roof, either directly or through a header.

7.5.6.3.  Reserved

7.5.6.4.  Minimum Size of Yoke Vents

(1)  Where a yoke vent is required to be installed in accordance with Article 7.5.3.3., the yoke vent shall be at least 2 in. size.

7.5.6.5.  Vents for Sanitary Sewage Sumps

(1)  Where the diameter of an inlet pipe to a sanitary sewage tank is

(a)	5 in. or larger, the diameter of the vent pipe from the tank shall be at least 4 in., and

(b)	less than 5 in., the diameter of the vent pipe from the tank shall be the greater of

(i)	1-1/4 in., and

(ii)	one trade size smaller than the inlet pipe.

7.5.7. Sizing of Vent Pipes

7.5.7.1.  Sizes for Wet Vents

(1)  Where 2 or 3 fixtures are installed in a plumbing system, any one of the fixtures may be wet vented by one or both of the other fixtures if

(a)	all the fixtures are on the same floor level,

(b)	only the wet vented fixture is a water closet or other fixture using a siphonic trap,

(c)	where the wet vented trap is not a siphonic trap, it is a P-trap and the wet vent is connected to the horizontal waste pipe downstream from the weir of the P-trap at least 450 mm and not more than 1 500 mm, and

(d)	at least one of the wet venting fixtures is drained through a vertical continuous waste and vent and the waste pipe serving as a wet vent is at least

(i)	1¼ in. size, where the wet vented trap is of 1¼ or 1½ in. size,

(ii)	1½ in. size, where the wet vented trap is of 2 in. size, or

(iii)	2 in. size, where the wet vented trap is of 3, 4 or 6 in. size.

(2)  Where there are two wet venting fixtures in a plumbing system referred to in Sentence (1) and both connect to the same vertical continuous waste and vent, both wet venting fixtures shall, where they are connected at the same level, be vented by a double fitting in conformance to Table 7.2.4.5. or, where they are not connected at the same level, be separately vented.

7.5.7.2.  Branch Vent Sizing

(1)  No branch vent and its connecting branch shall be smaller in diameter than the diameter calculated in accordance with Table 7.5.7.2.A. and where Table 7.4.10.5.B. is not applicable to the vent, the maximum length of the vent shall be calculated in accordance with Table 7.5.7.2.B.

(2)  Where Table 7.4.10.5.B. is not applicable to a branch vent, header or circuit vent, no vent or header shall have branch connections in excess of the number that are permitted by the combinations in Table 7.5.7.2.A. and, where one vent pipe protects more than one trap, each trap shall be counted as one vent.

Table 7.5.7.2.A.

Branch Venting

Forming Part of Sentences 7.5.3.2.(3), 7.5.7.2.(1) and (2)

| Combination Number | Size of Receiving Vent, in. | Maximum Number Size and Nature of Connecting Vents |  |  |
| --- | --- | --- | --- | --- |
|  |  | 1¼ in. Other than Water Closet | 1½ in. Other than Water Closet | 1½ in. Water Closet |
| 1 | 1¼ | 4 | — | — |
| 2 | 1½ | 12 | — | — |
| 3 | 1½ | — | 6 | — |
| 4 | 1½ | — | — | 2 |
| 5 | 1½ | 4 | — | 1 |
| 6 | 1½ | 2 | 1 | 1 |
| 7 | 1½ | — | 2 | 1 |
| 8 | 2 | 50 | — | — |
| 9 | 2 | — | 25 | — |
| 10 | 2 | — | 12 | 6 |
| 11 | 2½ | — | 12 | 10 |
| 12 | 2½ | 25 | — | 10 |
| Column 1 | 2 | 3 | 4 | 5 |

Note to Table 7.5.7.2.A.:

(1) Vent pipes permitted in Columns 3 and 4 of combinations 2 to 12 may be exchanged on the basis of two 1¼ in. vent pipes equal to one 1½ in. vent pipe.

(3)  Reserved

(4)  For the purpose of Table 7.5.7.2.B.

(a)	the length of a circuit vent shall be the developed length from the horizontal soil or waste pipe to the vent stack, stack vent, header or open air, and

(b)	the length of a branch vent shall be the developed length of vent piping from the most distant soil or waste pipe connection to a vent stack, stack vent, header or open air.

Table 7.5.7.2.B.

Maximum Length of Vents

Forming Part of Articles 7.5.7.2. and 7.5.7.3.

| Pipe, Trade Size, in. | Maximum Length, metres |
| --- | --- |
| 1¼ | 15.2 |
| 1½ | 15.2 |
| 2 | 18.3 |
| 2½ | 24.4 |
| 3 | 30.5 |
| 4 | 45.7 |
| 5 | 61.0 |
| 6 | 76.2 |
| Column 1 | 2 |

(5)  Reserved

(6)  Reserved

(7)  For the purpose of Table 7.4.10.5.B. and Table 7.5.7.2.B., the length of a header shall be the developed length of vent piping from the vent stack or stack vent where the header terminates to the most distant vent or stack connected to it.

7.5.7.3.  Developed Length

(1)  For the purpose of Table 7.4.10.5.B. and Table 7.5.7.2.B., the length of a vent stack or stack vent shall be its developed length from its lower end where it connects to drainage piping to its upper end where it connects to a header or goes directly to open air.

Section 7.6. Potable Water Systems

7.6.1. Arrangement of Piping

7.6.1.1.  Design, Fabrication and Installation

(1)  Potable water systems shall be designed, fabricated and installed in accordance with good engineering practice.

(2)  Every fixture supplied with separate hot and cold water controls shall have the hot water control on the left and the cold on the right.

(3)  Where hot and cold water are mixed and the temperature is regulated by a single, unmarked, manual control, a movement to the left shall increase the temperature and a movement to the right shall decrease the temperature.

7.6.1.2.  Drainage

(1)  A water distribution system shall be installed so that the system can be drained or blown out with air and outlets for this purpose shall be provided.

7.6.1.3.  Control and Shut-off Valves

(1)  A building control valve shall be provided

(a)	on every water service pipe at the location where the water service pipe enters the building, or

(b)	on the water distribution system at a location immediately downstream of the point of entry treatment unit, where the building is served by a point of entry treatment unit located in the building.

(2)  Except as provided in Sentence (3), a drain port shall be provided on the water distribution system immediately downstream of the building control valve required by Sentence (1) and if there is a meter, the drain port shall be installed immediately downstream of the meter on the water distribution system.

(3)  Where the building control valve required by Sentence (1) is of one in. trade size or smaller, the drain port may be an integral part of the building control valve in the form of a stop and waste valve and the drain port shall be located on the water distribution system side of the stop and waste valve.

(4)  Every pipe that is supplied with water from a tank on the property that is a gravity water tank or a tank of a drinking-water system shall be provided with a shut-off valve located close to the tank.

(5)  Where the water supply is to be metered, the installation of the meter, including the piping that is part of the meter installation and the valving arrangement for the meter installation, shall be according to the water purveyor’s requirements.

(6)  For the purpose of identifying the pipe material where plastic (polybutylene, polyethylene or PVC) water pipe is used underground for a service pipe, the end of the pipe inside the building shall be brought above ground for a distance not less than 300 mm and not greater than 450 mm.

7.6.1.4.  Shut-off Valves

(1)  Except for a single-family dwelling, every riser shall be provided with a shut-off valve at the source of supply.

7.6.1.5.  Water Closets

(1)  Every water closet shall be provided with a shut-off valve on its water supply pipe.

7.6.1.6.  Suites

(1)  Shut-off valves shall be installed in every suite in a building of residential occupancy as may be necessary to ensure that when the supply to one suite is shut off the supply to the remainder of the building is not interrupted.

7.6.1.7.  Public Washroom

(1)  The water supply to each fixture in a washroom for public use shall be individually valved and each valve shall be accessible.

7.6.1.8.  Tanks

(1)  Every water pipe that supplies a hot water tank, pressure vessel, plumbing appliance or water using device shall be provided with a shut-off valve located close to the tank, pressure vessel, plumbing appliance or water using device.

7.6.1.9.  Protection for Exterior Water Supply

(1)  Every pipe that passes through an exterior wall to supply water to the exterior of the building shall be provided with a frost-proof hydrant or a stop-and-waste valve located inside the building and close to the wall.

(2)  Where a self draining frost proof hydrant is used, a stop valve may be used in lieu of a stop-and-waste valve.

7.6.1.10.  Check Valves

(1)  A check valve shall be installed at the building end of the water service pipe where the pipe is made of plastic that is suitable for cold water use only.

7.6.1.11.  Flushing Devices

(1)  Every flushing device that serves a water closet or one or more urinals shall have sufficient capacity and be adjusted to deliver at each operation a volume of water that will thoroughly flush the fixture or fixtures that it serves.

(2)  Where a manually operated flushing device is installed, it shall serve only one fixture.

7.6.1.12.  Relief Valves

(1)  Every pressure vessel that is part of a plumbing system or connected to a plumbing system shall be equipped with a pressure relief valve designed to open when the water pressure in the tank reaches the rated working pressure of the tank, and so located that the pressure in the tank shall not exceed 1100 kPa or 1/2 the maximum test pressure sustained by the tank whichever is the lesser.

(2)  Every hot water tank of a storage-type service water heater shall be equipped with

(a)	a temperature relief valve with a temperature sensing element located within the top 150 mm of the tank and designed to open and discharge sufficient water from the tank to keep the temperature of the water in the tank from exceeding 99°C under all operating conditions, or

(b)	a device that

(i)	is designed to shut off the supply of electricity or fuel to the heater,

(ii)	is not connected to and operates independently of the thermostatic control that determines the temperature of the water in the tank, and

(iii)	is located and maintained on or within the top 150 mm of the tank so that the maximum temperature of the water in the tank shall not exceed 99°C under all operating conditions.

(3)  Every tank equipped as specified in Clause 7.6.1.12.(2)(b) shall bear the information in a clearly visible location that it is so equipped.

(4)  A pressure relief valve and temperature relief valve may be combined where Sentences (1) and (2) are complied with.

(5)  Every indirect service water heater shall be equipped with

(a)	a pressure relief valve, and

(b)	a temperature relief valve on every storage tank that forms part of the system.

(6)  A temperature relief, pressure relief, or a combined temperature and pressure relief valve which is installed on a hot water tank shall have a pipe that

(a)	has a size at least equal to the size of the outlet of the valve,

(b)	is rigid, slopes downward from the valve, and

(i)	terminates with an indirect connection above a floor drain, sump or other safe location, with an air break of not more than 300 mm, or

(ii)	terminates at a distance not less than 150 mm and not more than 300 mm from a floor and discharges vertically down,

(c)	has no thread at its outlet, and

(d)	is capable of operating at a temperature of not less than 99°C.

(7)  The temperature relief valve required in Clause 7.6.1.12.(5)(b) shall have a temperature sensing element located within the top 150 mm of the tank and be designed to open and discharge sufficient water to keep the temperature of the water in the tank from exceeding 99°C under all operating conditions.

(8)  No shut-off valve shall be installed on the pipe between any tank and the relief valves or on the discharge lines from such relief valves.

7.6.1.13.  Water Hammer

(1)  Provision shall be made to protect the water distribution system from the adverse effects of water hammer.

7.6.1.14.  Mobile Home Water Service

(1)  A water service pipe intended to serve a mobile home shall

(a)	be not less than 3/4 in. size,

(b)	be terminated above ground, and

(c)	be provided with

(i)	a tamperproof terminal connection that is capable of being repeatedly connected, disconnected and sealed,

(ii)	a protective concrete pad,

(iii)	a means to protect it from frost heave, and

(iv)	a curb stop and a means of draining that part of the pipe located above the frost line when not in use.

7.6.1.15.  Solar Domestic Hot Water Systems

(1)  Except as provided in Sentence (2), a system for solar heating of potable water shall be installed in accordance with good engineering practice.

(2)  Packaged systems for solar heating of potable water in residential occupancies shall be installed in conformance with CAN/CSA-F383, “Installation Code for Solar Domestic Hot Water Systems”.

7.6.2. Protection from Contamination

7.6.2.1.  Connection of Systems

(1)  Connections to potable water systems shall be designed and installed so that non-potable water or substances that may render the water non-potable cannot enter the system.

(2)  No connection shall be made between a potable water system supplied with water from a drinking-water system and any other potable water system without the consent of the water purveyor.

7.6.2.2.  Cleaning of Systems

(1)  Every newly installed part of a potable water system shall be clean and free of any matter that may affect the health of a person before being put into service.

7.6.2.3.  Back Siphonage

(1)  Every potable water system that supplies a fixture or tank that is not subject to pressures above atmospheric shall be protected against back-siphonage by a backflow preventer.

(2)  Where a potable water supply is connected to a boiler, tank, cooling jacket, lawn sprinkler system or other device where a non-potable fluid may be under pressure that is above atmospheric or the water outlet may be submerged in the non-potable fluid, the water supply shall be protected against backflow by a backflow preventer.

(3)  Where a hose bibb is installed outside a building, inside a garage, or where there is an identifiable risk of contamination, the potable water system shall be protected against backflow by a backflow preventer.

(4)  Where a potable water system serves a fire protection system, the fire protection system shall be isolated from the potable water system in the following manner:

(a)	a wet sprinkler fire protection system containing water only shall be provided with a listed alarm check valve installed in conformance with NFPA 13, “Installation of Sprinkler Systems”,

(b)	a wet standpipe fire protection system containing water only shall be provided with a resilient seated check valve,

(c)	a wet sprinkler or wet standpipe fire protection system containing anti-freeze or chemicals shall be provided with a reduced pressure principle backflow preventer certified to CAN/CSA-B64.4 Series, “Backflow Preventers, Reduced Pressure Principle Type (RP)”,

(d)	a dry sprinkler or dry standpipe fire protection system does not require isolation,

(e)	a water storage tank fire protection system shall be provided with a backflow preventer certified to CAN/CSA-B64 Series, “Backflow Preventers and Vacuum Breakers”,

(f)	a fire hydrant fire protection system does not require isolation,

(g)	a fire service main shall be provided with a reduced pressure principle backflow preventer certified to CAN/CSA-B64.4, “Backflow Preventers, Reduced Pressure Principle Type (RP)” if it is connected to more than one of the following different sources of supply:

(i)	a drinking-water system, or

(ii)	a source of non-potable water.

(iii)	Revoked:  O. Reg. 304/03, s. 6.

(5)  Except as permitted in Sentences (4) and (8), backflow prevention devices to protect a potable water system from contamination shall be selected, installed and field tested in accordance with CAN/CSA-B64.10, “Backflow Prevention Devices — Selection, Installation, Maintenance and Field Testing”.

(6)  Backflow prevention devices shall be provided in conformance with Sentence 7.2.10.10.(1).

(7)  Tank type water closet valves shall be provided with a back-siphonage preventer in conformance with Sentence 7.2.10.10.(2).

(8)  Buildings of residential occupancy within the scope of Part 9 are not required to be isolated unless they have access to an auxiliary water supply.

7.6.2.4.  Air Gap

(1)  An air gap shall not be located in a noxious environment.

(2)  Every air gap shall be not less than 25 mm high and at least twice the diameter of the opening of the water supply outlet in height.

7.6.2.5.  Vacuum Breakers and Flood Levels

(1)  Where the critical level is not marked on an atmospheric vacuum breaker or pressure vacuum breaker, the critical level shall be taken as the lowest point on the device.

(2)  Where an atmospheric vacuum breaker is installed, it shall be located on the downstream side of the fixture control valve or faucet so that it will be subject to water supply pressure

(a)	only when the fixture control valve or faucet is open, and

(b)	for periods of use not to exceed 12 h continuous.

(3)  An atmospheric vacuum breaker shall be installed so that the critical level is at least the distance specified by the manufacturer at which the device will operate safely but not less than 25 mm above

(a)	the flood level rim of a fixture or tank, or

(b)	the highest point open to atmosphere in an irrigation system.

(4)  A pressure vacuum breaker shall be installed with its critical level at least 300 mm above

(a)	the flood level rim of a fixture or tank, or

(b)	the highest point open to atmosphere in an irrigation system.

7.6.3. Size and Capacity of Pipes

7.6.3.1.  Design

(1)  Except as provided in Sentence (2), the size of every pipe in a water distribution system that supplies water to a fixture or device shall comply with Table 7.6.3.1.

(2)  Where a pipe in a water distribution system is not directly connected to a fixture or a fixture faucet but is connected with a flexible tube of a diameter smaller than that specified by Table 7.6.3.1., the developed length of the connector shall not be more than 355 mm and, where 3/8 in. pipe of iron pipe size is used, the maximum length shall not exceed 914 mm.

Table 7.6.3.1.

Pipe Sizing for Water Supply to Fixture/Device

Forming Part of Sentences 7.6.3.1.(1) and (2)

| Fixture or Device | Minimum Size of Supply Pipe, in. |
| --- | --- |
| Bath tub | 1/2 |
| Combination sink and tray | 1/2 |
| Dishwasher, domestic | 1/2 |
| Drinking fountain | 3/8 |
| Hose bib | 1/2 |
| Laundry tray: 1, 2 or 3 compartments | 1/2 |
| Lavatory | 3/8 |
| Shower, single head | 1/2 |
| Sink |  |
| (a) kitchen, domestic | 1/2 |
| (b) kitchen, commercial | 1/2 |
| (c) service, slop | 1/2 |
| (d) service with direct flush valve | 3/4 |
| Urinal |  |
| (a) with flush tank | 1/2 |
| (b) with direct flush valve | 3/4 |
| (c) with self closing metering | 1/2 |
| Wall hydrant | 1/2 |
| Water closet |  |
| (a) with flush tank | 3/8 |
| (b) with direct flush valve | 1 |
| Column 1 | 2 |

7.6.3.2.  Peak Demand Flow

(1)  No water system shall have a capacity that is less than the peak demand flow.

(2)  No water system between the point of connection with the water service pipe or the water meter and the first branch that supplies a water heater, shall be less than 3/4 in. size.

(3)  Every pipe that supplies a fixture shall have a capacity that will produce a flow in the fixture that will flush the fixture and keep it in a sanitary condition.

7.6.3.3.  Static Pressure

(1)  Where the static pressure exceeds 550 kPa, a pressure reducing valve shall be installed to limit the maximum static pressure to not more than 550 kPa in areas that may be occupied.

7.6.3.4.  Size

(1)  Every water service pipe shall be not less than 3/4 in. trade size.

7.6.4. Water Efficiency

7.6.4.1.  Water Supply Fittings

(1)  The flow rates of fittings that supply water to a fixture shall not exceed the maximum flow rates at the test pressures listed for that fitting in Table 7.6.4.1.

(2)  Sentence (1) does not apply to a fixture located in a heritage building.

Table 7.6.4.1.

Maximum Flow Rates for Water Supply Fittings

Forming Part of Sentence 7.6.4.1.(1)

| Fitting | Maximum Flow, L/min | Test Pressure, kPa |
| --- | --- | --- |
| Lavatory Faucet | 8.35 | 413 |
| Kitchen Faucet | 8.35 | 413 |
| Shower Heads | 9.50 | 550 |
| Column 1 | 2 | 3 |

7.6.4.2.  Plumbing Fixtures

(1)  Water closets and urinals shall be certified to CAN/CSA-B45.0, “General Requirements for Plumbing Fixtures”.

(2)  The flush cycle for each fixture that is a water closet or urinal and that is installed as a replacement for a fixture in a building that existed before January1, 1996 shall not exceed the maximum flush cycle listed for that fixture in Table 7.6.4.2.A.

Table 7.6.4.2.A.

Maximum Flush Cycles for Sanitary Fixtures

Forming Part of Sentence 7.6.4.2.(2)

| Fixture | litres |
| --- | --- |
| Water Closet (Tank Type) | 13.25 |
| Water Closet (Direct Flush) | 13.25 |
| Urinal (Tank Type) | 5.68(1) |
| Urinal (Direct Flush) | 5.68(1) |
| Column 1 | 2 |

Note to Table 7.6.4.2.A.:

(1) Urinals equipped with automatic flushing devices shall be controlled to prevent unnecessary flush cycles during building down time.

(3)  Except as provided in Sentence (2), the flush cycle for each fixture that is a water closet or urinal shall not exceed the maximum flush cycle listed for that fixture in Table 7.6.4.2.B.

(4)  Sentences (2) and (3) do not apply to a fixture located in a heritage building, care or detention occupancy or passenger station.

Table 7.6.4.2.B.

Maximum Flush Cycles for Sanitary Fixtures

Forming Part of Sentence 7.6.4.2.(3)

| Fixture | litres |
| --- | --- |
| Water Closet (Tank Type) | 6.0 |
| Water Closet (Direct Flush) | 6.0 |
| Urinal (Tank Type) | 3.8(1) |
| Urinal (Direct Flush) | 3.8(1) |
| Column 1 | 2 |

Note to Table 7.6.4.2.B.:

(1) Urinals equipped with automatic flushing devices shall be controlled to prevent unnecessary flush cycles during building down time.

7.6.5.  Water Temperature Control

7.6.5.1.  Maximum Temperature of Hot Water

(1)  Except as provided in Sentences (2) and 7.6.5.3.(1), the maximum temperature of hot water supplied by fittings to fixtures in a residential occupancy shall not exceed 49C.

(2)  Sentence (1) does not apply to hot water supplied to installed dishwashers or clothes washers.

7.6.5.2.  Showers

(1)  Except as provided in Sentence (2), all shower valves shall be pressure-balanced or thermostatic-mixing valves, conforming to CAN/CSA-B125, “Plumbing Fittings”.

(2)  No pressure-balanced or thermostatic-mixing valve is required for a shower if the hot water supply for the shower is controlled by a master thermostatic-mixing valve conforming to CAN/CSA-B125, “Plumbing Fittings”.

(3)  Pressure-balanced or thermostatic-mixing valves shall be

(a)	designed so that the outlet temperature does not exceed 49C, or

(b)	equipped with high-limit stops and adjusted to a maximum hot water setting of 49C.

7.6.5.3.  Temperature Control Devices

(1)  A water distribution system supplying hot water to any bathtub, shower or hand basin that is accessible to a patient or resident in a Group B, Division 2 or 3 occupancy or a resident of a group home, home for special care or residence for developmentally-handicapped adults shall have one or more temperature gauges and control devices that are

(a)	accessible only to supervisory staff, and

(b)	capable of being adjusted to ensure that the temperature of the water supplied to the fixtures does not exceed 49C.

Section 7.7. Non-Potable Water Systems

7.7.1. Connection

7.7.1.1.  Non-Potable Connection

(1)  A non-potable water system shall not be connected to a potable water system.

7.7.2. Identification

7.7.2.1.  Markings

(1)  Non-potable water piping shall be identified by markings that are permanent, distinct and easily recognized.

7.7.3. Location

7.7.3.1.  Pipes

(1)  Non-potable water piping shall not be located

(a)	where food is prepared in a food processing plant,

(b)	above food-handling equipment,

(c)	above a non-pressurized potable water tank, or

(d)	above a cover of a pressurized potable water tank.

7.7.3.2.  Outlets

(1)  An outlet from a non-potable water system shall not be located where it can discharge into

(a)	a sink or lavatory,

(b)	a fixture into which an outlet from a potable water system is discharged, or

(c)	a fixture that is used for a purpose related to the preparation, handling or dispensing of food, drink or products that are intended for human consumption.

O. Reg. 403/97, Part 7; O. Reg. 22/98, s. 17; O. Reg. 122/98, s. 1; O. Reg. 304/03, ss. 2-6; O. Reg. 23/04, ss. 3, 4; O. Reg. 349/06, ss. 15-21.

Part 8
Sewage Systems

| Section | 8.1. | General |
| --- | --- | --- |
|  | 8.1.1. | Scope |
|  | 8.1.2. | Application |
|  | 8.1.3. | Limitations |
| Section | 8.2. | Design Standards |
|  | 8.2.1. | General Requirements |
|  | 8.2.2. | Treatment and Holding Tanks |
| Section | 8.3. | Class 1 Sewage Systems |
|  | 8.3.1. | General Requirements |
|  | 8.3.2. | Superstructure Requirements |
|  | 8.3.3. | Earth Pit Privy |
|  | 8.3.4. | Privy Vaults and Pail Privy |
|  | 8.3.5 | Portable Privy |
| Section | 8.4. | Class 2 Sewage Systems |
|  | 8.4.1. | General Requirements |
|  | 8.4.2. | Design and Construction Requirements |
| Section | 8.5. | Class 3 Sewage Systems |
|  | 8.5.1. | General Requirements |
|  | 8.5.2. | Design and Construction Requirements |
| Section | 8.6. | Class 4 Sewage Systems |
|  | 8.6.1. | General Requirements |
|  | 8.6.2. | Treatment Units |
| Section | 8.7. | Leaching Beds |
|  | 8.7.1. | General Requirements |
|  | 8.7.2. | Construction Requirements |
|  | 8.7.3. | Absorption Trench Construction |
|  | 8.7.4 | Fill Based Absorption Trenches |
|  | 8.7.5. | Filter Beds |
|  | 8.7.6. | Shallow Buried Trenches |
| Section | 8.8. | Class 5 Sewage Systems |
|  | 8.8.1. | Application |
|  | 8.8.2. | General Requirements |
| Section | 8.9. | Operation and Maintenance |
|  | 8.9.1. | General |
|  | 8.9.2. | Operation |
|  | 8.9.3. | Maintenance |

Part 8
Sewage Systems

Section 8.1. General

8.1.1. Scope

8.1.1.1. Scope

(1)  The scope of this Part shall be as described in Section 2.1. and applies to the design, construction, operation, and maintenance of sewage systems.

8.1.1.2.  Definitions

(1)  In this Part

Soil means in-situ, naturally occurring, unconsolidated mineral or organic material, at the earth’s surface which is at least 100 mm thick and capable of supporting plant growth, and includes material compacted or cemented by soil forming processes, but does not include displaced materials such as gravel dumps, mine spoils, or like deposits.

8.1.2. Application

8.1.2.1.  Classification of Systems

(1)  All sewage systems shall be classed as one of the following:

(a)	Class 1 — a chemical toilet, an incinerating toilet, a recirculating toilet, a self-contained portable toilet and all forms of privy including a portable privy, an earth pit privy, a pail privy, a privy vault and a composting toilet system,

(b)	Class 2 — a greywater system,

(c)	Class 3 — a cesspool,

(d)	Class 4 — a leaching bed system,

(e)	Class 5 — a system which requires or uses a holding tank for the retention of hauled sewage at the site where it is produced prior to its collection by a hauled sewage system.

8.1.2.2.  Operation and Maintenance

(1)  Operation and maintenance of sewage systems shall comply with Section 8.9.

8.1.3. Limitations

8.1.3.1.  Discharge

(1)  Except as provided in Sentences (2) to (5), the sewage system shall be designed and constructed to receive only sanitary sewage of domestic origin.

(2)  Where laundry waste is not more than 20% of the total daily design sanitary sewage flow, it may discharge to a sewage system.

(3)  Where industrial process waste water is treated to the contaminant levels found in domestic sanitary sewage, it may discharge to a leaching bed provided the treatment unit and sewage system are designed in accordance with good engineering practice.

(4)  Where all kitchen waste water from a restaurant has passed through an operating grease interceptor, it may discharge to a leaching bed system provided the sewage system has been designed in accordance with good engineering practice.

(4.1)  Waste water from a kitchen equipped with a garbage grinder may be directed to the sewage system provided the system has been designed to accept such waste water.

(5)  Water softener and iron filter discharge may be directed to the sewage system provided the system has been designed to accept such discharges.

(6)  Storm sewage shall not be discharged into a sewage system.

(7)  The interceptor required in Sentence (4) shall have a minimum flow rate as required by Sentence 7.4.4.3.(8) using a 60 second drain down time.

8.2. Design Standards

8.2.1.  General Requirements

8.2.1.1.  Scope

(1)  This Subsection applies to the design of sewage systems.

8.2.1.2.  Site Evaluation

(1)  A site evaluation shall be conducted on every site where a new or replacement sewage system is to be installed.

(2)  The percolation time shall be determined by either percolation tests or by classifying the soil according to the Unified Soil Classification System as described in the Supplementary Guidelines to the 1997 OBC.

(3)  Where the percolation time is determined by a percolation test, there shall be a minimum of 3 locations selected, suitably spaced to accurately evaluate the leaching bed area, with the highest percolation time of the tests being used.

8.2.1.3.  Sewage System Design Flows

(1)  For residential occupancies, the total daily design sanitary sewage flow shall be at least the value in Column 2 as determined from Table 8.2.1.3.A.

(2)  For all other occupancies, the total daily design sanitary sewage flow shall be at least the value in Column 2 as determined from Table 8.2.1.3.B.

(3)  Where a building contains more than one establishment, the total daily design sanitary sewage flow shall be the sum of the total daily design sanitary sewage flow for each establishment.

(4)  Where an occupancy is not listed in Table 8.2.1.3.B., the highest of metered flow data from at least 3 similar establishments shall be acceptable for determining total daily design sanitary sewage flow.

Table 8.2.1.3.A.

Forming Part of Sentence 8.2.1.3.(1)

| Residential Occupancy | Volume(Litres) |
| --- | --- |
| Apartments, Condominiums, Other Multi-family Dwellings — per person(1) | 275 |
| Boarding Houses |  |
| (a) Per person, |  |
| (i) with meals and laundry facilities, or | 200 |
| (ii) without meal or laundry facilities, and | 150 |
| (b) Per non-resident staff per 8 hour shift | 40 |
| Boarding School — per person | 300 |
| Dwellings |  |
| (a) 1 Bedroom Dwelling | 750 |
| (b) 2 Bedroom Dwelling | 1100 |
| (c) 3 Bedroom Dwelling | 1600 |
| (d) 4 Bedroom Dwelling | 2000 |
| (e) 5 Bedroom Dwelling | 2500 |
| (f) Additional flow for (2) |  |
| (i) each bedroom over 5 | 500 |
| (ii) |  |
| (A) each 10 m2 (or part thereof) over 200 m2 up to 400 m2 (3) | 100 |
| (B) each 10 m2 (or part thereof) over 400 m2 up to 600 m2 (3), and | 75 |
| (C) each 10 m2 (or part thereof) over 600 m2 (3), | 50 |
| or |  |
| (iii) each fixture unit over 20 fixture units | 50 |
| Hotels and Motels (excluding bars and restaurants) |  |
| (a) Regular, per room | 250 |
| (b) Resort hotel, cottage, per person | 500 |
| (c) Self service laundry, add per machine | 2500 |
| Work Camp/Construction Camp, semi-permanent per worker | 250 |
| Column 1 | 2 |

Notes for Table 8.2.1.3.A.:

(1) The occupant load shall be calculated using Subsection 3.1.16.

(2) Where multiple calculations of sewage volume is permitted the calculation resulting the highest flow shall be used in determining the design daily sanitary sewage flow.

(3) Total finished area, excluding the area of the finished basement.

Table 8.2.1.3.B.

Forming Part of Sentence 8.2.1.3.(2) Other Occupancies

| Establishments(1) | Volume (Litres) |
| --- | --- |
| Airports, Bus Terminals, Train Stations, Dock/Port Facilities (Food Services excluded) |  |
| (a) Per passenger, and | 20 |
| (b) Per employee per 8 hour shift | 40 |
| Assembly Hall per seat |  |
| (a) No food service, or | 8 |
| (b) Food service provided | 36 |
| Barber Shop/Beauty Salon per service chair | 650 |
| Bowling Alleys (Food Service not included) per lane | 400 |
| Churches per seat |  |
| (a) No kitchen facilities, or | 8 |
| (b) Kitchen facilities provided | 36 |
| Country Club (excluding Food Service) |  |
| (a) Per resident, | 375 |
| (b) Per employee per 8 hour shift, | 50 |
| and |  |
| (c) Per member or patron | 40 |
| Day Care Facility per person (staff and children) | 75 |
| Dentist Office |  |
| (a) Per wet service chair, and | 275 |
| (b) Per dry service chair | 190 |
| Doctors Office |  |
| (a) Per practitioner, and | 275 |
| (b) Per employee per 8 hour shift | 75 |
| Factory (excluding process or cleaning waters) per employee per 8 hour shift |  |
| (a) No showers, or | 75 |
| (b) Including showers | 125 |
| Flea Markets(3) (open 3 or less days per week) |  |
| (a) Per non-food service vendor space, | 60 |
| (b) Per food service establishment 9.25 m2 of floor space, and | 190 |
| (c) Per limited food service outlet | 95 |
| Food Service Operations |  |
| (a) Restaurant (not 24 hour), per seat | 125 |
| (b) Restaurant (24 hour), per seat | 200 |
| (c) Restaurant on controlled access highway, per seat | 400 |
| (d) Paper Service Restaurant, per seat | 60 |
| (e) Donut Shop, per seat | 400 |
| (f) Bar and Cocktail Lounge, per seat | 125 |
| (g) Drive-in Restaurant, per parking space | 60 |
| (h) Take-out Restaurant (no seating area) |  |
| (i) Per 9.25 m2 of floor area, and | 190 |
| (ii) Per employee per 8 hour shift | 75 |
| (i) Cafeteria, per meal | 12 |
| (j) Food outlet |  |
| (i) excluding delicatessen, bakery and meat department, per 9.25 m2 of floor space | 40 |
| (ii) Per 9.25 m2 of delicatessen floor space | 190 |
| (iii) Per 9.25 m2 of bakery floor space | 190 |
| (iv) Per 9.25 m2 of meat department floor space, and | 380 |
| (v) Per water closet | 950 |
| Hospitals per bed |  |
| (a) Including laundry facilities, or | 750 |
| (b) Excluding laundry facilities | 550 |
| Nursing Homes, Rest Homes, etc., per bed | 450 |
| Office Building(4) |  |
| (a) Per employee per 8 hour shift, or | 75 |
| (b) Per each 9.3 m2 of floor space | 75 |
| Public Parks |  |
| (a) With toilets only per person, or | 20 |
| (b) With bathhouse, showers, and toilets per person | 50 |
| Recreational Vehicle or Campground Park |  |
| (a) Per site without water or sewer hook-up, or | 275 |
| (b) Per site with water and sewer hook-up | 425 |
| Schools per student |  |
| (a) Day school | 30 |
| (b) With showers | 50 |
| (c) With cafeteria, and | 30 |
| (d) Per non-teaching employee per 8 hour shift | 50 |
| Service Stations (No vehicle washing)(4) |  |
| (a) Per water closet, and | 950 |
| (i) Per fuel outlet, or | 560 |
| (ii) Per vehicle served | 20 |
| Shopping Centre (Excluding Food and Laundry) per 1.0 m2 of floor space | 5 |
| Stadiums, Race Tracks, Ball Parks per seat | 20 |
| Stores(4) |  |
| (a) Per 1.0 m2 of floor area, or | 5 |
| (b) Per water closet | 1230 |
| Swimming and Bathing Facilities (Public) per person | 40 |
| Theatres |  |
| (a) Indoor, auditoriums per seat, | 20 |
| (b) Outdoor, drive-ins per space, or | 40 |
| (c) Movie theatres per seat | 15 |
| Veterinary Clinics |  |
| (a) Per practitioner, | 275 |
| (b) Per employee per 8 hour shift, and | 75 |
| (c) Per stall, kennel, or cage if floor drain connected | 75 |
| Warehouse |  |
| (a) Per water closet, and | 950 |
| (b) Per loading bay | 150 |
| Column 1 | 2 |

Notes for Table 8.2.1.3.B:

(1) The occupant load shall be calculated using Subsection 3.1.16.

(2) Reserved.

(3) Flea Markets open more than 3 days per week shall be assessed using the volumes stated under the heading “Stores”.

(4) Where multiple calculations of sanitary sewage volume is permitted the calculation resulting in the highest flow shall be used in determining the design daily sanitary sewage flow.

8.2.1.4.  Clearances

(1)  Unless it can be shown to be unnecessary, where the percolation time is 10 minutes or greater, the location of all components within a sewage system shall be in conformance with the clearances listed in Articles 8.2.1.5. or 8.2.1.6.

(2)  Unless it can be shown to be unnecessary, where the percolation time is less than 10 minutes, the clearances listed in Articles 8.2.1.5. and 8.2.1.6. for wells, lakes, ponds, reservoirs, rivers, springs or streams shall be increased to compensate for the lower percolation time.

(3)  No building shall be constructed closer to any part of a sewage system than the clearances listed in Articles 8.2.1.5. or 8.2.1.6.

(4)  If more than one sewage system is located on a lot or parcel of land, there shall be no overlap of any part of the systems.

8.2.1.5.  Clearance Distances for Class 1, 2 and 3 Sewage Systems

(1)  Except as provided in Sentences 8.2.1.4.(1) and (2), no Class 1, 2, or 3 sewage system shall have a horizontal distance of less than that permitted by Table 8.2.1.5.

Table 8.2.1.5.

Forming Part of Sentence 8.2.1.5.(1)

| Clearance Distances for Class 1, 2 and 3 Sewage Systems |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Minimum horizontal distance in metres from a well with watertight casing to a depth of at least 6 m | Minimum horizontal distance in metres from a spring used as a source of potable water or well other than a well with a water tight casing to a depth of at least 6 metres | Minimum horizontal distance in metres from a lake, river, pond, stream, reservoir, or a spring not used as a source of potable water | Minimum horizontal distance in metres from a Property Line |
| Earth Pit Privy | 15 | 30 | 15 | 3 |
| Privy Vault Pail Privy | 10 | 15 | 10 | 3 |
| Greywater System | 10 | 15 | 15 | 3 |
| Cesspool | 30 | 60 | 15 | 3 |
| Column 1 | 2 | 3 | 4 | 5 |

8.2.1.6.  Clearances for a Class 4 or 5 Sewage System

(1)  Except as provided in Sentences 8.2.1.4.(1) and (2), a treatment unit shall not be located closer than the minimum horizontal distances as set out in Table 8.2.1.6.A.

(2)  Except as provided in Sentences 8.2.1.4.(1) and (2), a distribution pipe shall not be located closer than the minimum horizontal distances set out in Table 8.2.1.6.B. and these distances shall be increased when required by Sentence 8.7.4.2.(9).

(3)  Except as provided in Sentences 8.2.1.4.(1) and (2), a holding tank shall not be located closer than the minimum horizontal distances set out in Table 8.2.1.6.C.

Table 8.2.1.6.A.

Forming Part of Sentence 8.2.1.6.(1)

| Minimum Clearances for Treatment Units |  |
| --- | --- |
| Structure | 1.5 m |
| Well | 15 m |
| Lake | 15 m |
| Pond | 15 m |
| Reservoir | 15 m |
| River | 15 m |
| Spring | 15 m |
| Stream | 15 m |
| Property Line | 3 m |
| Column 1 | 2 |

Table 8.2.1.6.B.

Forming Part of Sentence 8.2.1.6.(2)

| Minimum Clearances for Distribution Piping |  |
| --- | --- |
| Structure | 5 m |
| Well with a watertight casing to a depth of 6 m | 15 m |
| Any other well | 30 m |
| Lake | 15 m |
| Pond | 15 m |
| Reservoir | 15 m |
| River | 15 m |
| A spring not used as a source of potable water | 15 m |
| Stream | 15 m |
| Property Line | 3 m |
| Column 1 | 2 |

Table 8.2.1.6.C.

Forming Part of Sentence 8.2.1.6.(3)

| Minimum Clearances for Holding Tanks |  |
| --- | --- |
| Structure | 1.5 m |
| Well with a watertight casing to a depth of at least 6 m | 15 m |
| Any other well | 15 m |
| A spring | 15 m |
| Property Line | 3 m |
| Column 1 | 2 |

8.2.2. Treatment and Holding Tanks

8.2.2.1.  Application

(1)  This Subsection applies to any tank used in a sewage system for collecting, treating, holding or storing sanitary sewage.

8.2.2.2.  Tanks

(1)  Subject to Sentence 8.2.2.2.(2.1), a tank that is used as a treatment unit in a Class 4 sewage system or a holding tank in a Class 5 sewage system shall conform to the requirements of CSA B66 “Prefabricated Septic Tanks and Sewage Holding Tanks”.

(2)  Subject to Sentence 8.2.2.2.(2.1), material standards, access and construction methods and practices for a tank used for other Classes of sewage systems shall conform to the requirements of CSA B66 “Prefabricated Septic Tanks and Sewage Holding Tanks”.

(2.1)  Tanks referred to in Sentences 8.2.2.2.(1) and (2) are not required to conform to the requirements of Clause 9.2(j) of CSA B66 “Prefabricated Septic Tanks and Sewage Holding Tanks”.

(3)  Sentence (2) does not apply to a tank that is an integral part of a prefabricated Class 1 sewage system.

(4)  Access openings shall be located to facilitate the pumping of all compartments and the servicing of the inlet and outlet of each compartment not accessible by removal of the tank top or part thereof.

(5)  A tank shall not be covered by soil or leaching bed fill having a depth greater than the maximum depth of burial that the tank is designed to withstand.

(6)  A tank shall be securely anchored when located in an area subject to flooding or where ground water levels may cause hydrostatic pressures.

8.2.2.3.  Septic Tanks

(1)  The minimum working capacity of a septic tank shall be the greater of 3 600 L and

(a)	in residential occupancies, twice the daily design sanitary sewage flow, or

(b)	in non-residential occupancies, three times the daily design sanitary sewage flow.

(2)  Every septic tank shall be constructed in such a manner that any sanitary sewage flowing through the tank will pass through at least 2 compartments.

(3)  The working capacity of the compartments required in Sentence (2) shall be sized such that

(a)	the first compartment is at least 1.3 times the daily design sanitary sewage flow but in no case less than 2 400 L, and

(b)	each subsequent compartment shall be at least 50% of the first compartment.

(4)  Where multiple tanks are to be used to meet the requirements of Sentences (2) and (3), the tanks shall be connected in series such that

(a)	the first tank in the series shall have at least a capacity as calculated in Clause (3)(a), however at no time shall a tank having a working capacity of less than 3 600 L be used,

(b)	all additional tanks after the first tank, excluding pump or dosing tanks shall have at least a working capacity equal to Clause (3)(b),

(c)	the pipe between the outlet of one tank and the inlet of the next tank in the series shall have a minimum slope of 2 per cent,

(d)	there shall be no partitions in the tank except where a partition is required to maintain the structural integrity of the tank, in which case openings within the partition shall be provided to allow the free movement of sanitary sewage throughout the tank,

(e)	Reserved, and

(f)	all piping between tanks shall be continuous and shall be connected to the tank through the use of flexible watertight seals which will permit differential movement between the tanks.

(5)  Partitions separating the septic tank into compartments shall extend at least 150 mm above the liquid level at the outlet, and there shall be one or more openings through or above the partition.

(6)  The openings required between compartments referred to in Sentence (2) shall have a total cross-sectional area of at least three times the area of the inlet pipe and be located between the top and a level 150 mm above the liquid level at the outlet to provide for the free flow or air between compartments.

(7)  Sanitary sewage shall pass from one compartment to another of the septic tank by means of either

(a)	a device similar to that described in CSA B66 “Prefabricated Septic Tanks and Sewage Holding Tanks” for outlet devices, or

(b)	through two or more openings through the partition located in a horizontal line, and evenly spaced across the width of the partition, centred at approximately 40% of the liquid depth below the surface of the liquid, and having a total area of between three and five times that of the cross-sectional area of the inlet pipe.

(8)  A septic tank shall be of such design and construction as will permit the collection and holding of sanitary sewage therein to a depth of not less than 1 200 mm except that a depth of not less than 900 mm is permitted where the excavation is in rock, or to avoid rupture or displacement of the tank due to ground water pressure.

8.2.2.4.  Holding Tanks

(1)  All holding tanks shall be of such design and construction as will allow the complete removal of solid matter that can be expected to settle in the holding tank through an apparatus or device suitable for allowing the contents of the holding tank to be removed from the holding tank.

(2)  A holding tank shall have a working capacity of not less than 9 000 L.

(3)  Where two or more tanks are used to meet the requirement of Sentence (2), they shall be deemed to be one holding tank provided they are connected in such a manner as will allow the sanitary sewage contained therein to flow between the tanks.

(4)  The working capacity of the tanks described in Sentence (3) shall not include any portion of any tank that cannot be completely drained due to the manner in which the connections are made.

Section 8.3. Class 1 Sewage Systems

8.3.1.  General Requirements

8.3.1.1.  Scope

(1)  This Section applies to the construction of a Class 1 sewage system.

8.3.1.2.  Application

(1)  Except as provided in Sentence (2), a Class 1 sewage system shall be designed only to receive human body waste for disposal.

(2)  Where the sewage system is specifically designed for the biological decomposition of non-waterborne biodegradable kitchen wastes or requires the addition of small quantities of plant matter to improve the decomposition of human body waste, it may receive such wastes in addition to human body waste.

(3)  Where the sewage system is designed with a drain for the removal of excess liquid, then the sewage system shall drain to a Class 3, 4, or 5 sewage system.

8.3.2. Superstructure Requirements

8.3.2.1.  Construction Requirements

(1)  A privy as described in Subsections 8.3.3., 8.3.4. and 8.3.5. shall be enclosed with a superstructure that

(a)	is constructed of strong durable weatherproof materials,

(b)	has a solid floor supported by a sill constructed of treated timber, masonry or other material of at least equal strength and durability,

(c)	is easily sanitized,

(d)	unless it is equipped solely as a urinal, is equipped with one or more seats each having a cover and being supported by an enclosed bench or riser which is lined with an impervious material on all interior vertical surfaces,

(e)	is equipped with a self-closing door,

(f)	has one or more openings for purposes of ventilation, all of which are screened,

(g)	has a ventilation duct that is screened at the top end and that extends from the underside of the bench or riser to a point above the roof of the superstructure, and

(h)	shall not have any openings for the reception of human body waste, other than urinals and those constructed in accordance with Clause (1)(d).

8.3.3. Earth Pit Privy

8.3.3.1.  Construction Requirements

(1)  An earth pit privy shall be constructed in the following manner:

(a)	the bottom of the pit shall be at least 900 mm above the high ground water table,

(b)	the sides of the pit shall be reinforced so as to prevent collapse thereof,

(c)	the pit shall be surrounded on all sides and on its bottom by not less than 600 mm of soil or leaching bed fill, and

(d)	the soil or leaching bed fill around the base of the sides of the superstructure of the earth pit privy shall be raised or mounded to a height of at least 150 mm above ground level.

8.3.4. Privy Vaults and Pail Privy

8.3.4.1.  Construction Requirements

(1)  A privy-vault or a pail privy shall be constructed in the following manner:

(a)	the container or structure which is to be used for the holding or storage of sanitary sewage shall be watertight and made of a material which can be easily cleaned,

(b)	the soil or leaching bed fill around the base of the sides of the superstructure shall be raised or mounded to a height of at least 150 mm above ground level, and

(c)	the surface of the ground in the area of the privy-vault or pail privy shall be so graded that surface drainage will be diverted away from the privy.

8.3.5. Portable Privy

8.3.5.1.  Construction Requirements

(1)  A portable privy shall be constructed in the following manner:

(a)	the portable privy shall have a watertight receptacle which shall be suitable for the holding and storage of any sanitary sewage deposited therein,

(b)	the receptacle for the holding and storage of sewage shall be designed and constructed in such a manner as to allow it to be easily emptied and cleaned, and

(c)	the portable privy shall be constructed of such material and in such a manner that it can withstand the stresses to which it will be subjected during its transportation to and from sites where it is to be used and during loading and unloading from vehicles used for the transportation of the portable privy to and from sites where it is to be used.

Section 8.4. Class 2 Sewage Systems

8.4.1. General Requirements

8.4.1.1.  Scope

(1)  This Section applies to the construction of a Class 2 sewage system.

8.4.1.2.  Application

(1)  A Class 2 sewage system shall be designed only for the treatment and disposal of greywater.

(2)  The total daily design flow for a Class 2 sewage system shall be calculated based on the fixtures discharging to the system as follows:

(a)	200 L per fixture unit where there is a supply of pressurized water, and

(b)	125 L per fixture unit where there is no supply of pressurized water.

8.4.2. Design and Construction Requirements

8.4.2.1.  Construction Requirements

(1)  The bottom of the pit shall be at least 900 mm above the high ground water table.

(2)  The pit shall be constructed in such a manner as to prevent the collapse of its sidewalls.

(3)  Any material used to support or form the sidewalls of the pit shall be an open jointed material of a type that will permit leaching from the pit.

(4)  The pit shall be provided with a tight, strong cover that shall remain over the pit except when it is necessary to remove it for purposes of adding greywater to or removing greywater from the pit or for purposes of maintenance of the pit.

(5)  The earth around the perimeter of the pit shall be raised or mounded to a height of at least 150 mm above ground level.

(6)  The surface of the ground in the area of the pit shall be so graded that surface drainage in the area will be diverted away from the pit.

(7)  The pit shall be surrounded on all sides and on its bottom by at least 600 mm of soil having a percolation time of less than 50 minutes.

8.4.2.2.  Maximum Sewage Flow

(1)  A Class 2 sewage system shall not be constructed where the daily design greywater flow to the system exceeds 1 000 L/day.

8.4.2.3.  Sizing

(1)  A Class 2 sewage system shall be designed and constructed so that the loading rate to the side walls shall be not more than the value calculated using

LR=400T

| where | LR | = | Loading rate of the sidewalls in litres per day/m2 |
| --- | --- | --- | --- |
|  | T | = | Percolation time |

Section 8.5. Class 3 Sewage Systems

8.5.1. General Requirements

8.5.1.1.  Scope

(1)  This Section applies to the construction of a Class 3 sewage system.

8.5.1.2.  Application

(1)  A Class 3 sewage system shall not be constructed where the daily design sanitary sewage flow to the system exceeds 1 000 L/day.

(2)  A Class 3 sewage system shall be designed to receive only the contents of a Class 1 sewage system or effluent from a Class 1 sewage system for disposal.

8.5.2. Design and Construction Requirements

8.5.2.1.  Construction Requirements

(1)  The bottom of the cesspool shall be at least 900 mm above the high ground water table.

(2)  The cesspool shall be constructed in such a manner as to prevent the collapse of its sidewalls.

(3)  Any material used to support or form the sidewalls of the cesspool shall be an open jointed material of a type that will permit leaching from the cesspool.

(4)  The cesspool shall be provided with a tight strong cover that shall remain over the cesspool except when it is necessary to remove it for the purposes of adding sanitary sewage to or removing sanitary sewage from the cesspool or for purposes of maintenance of the cesspool.

(5)  Where the cesspool extends to the ground surface, the cover required in Sentence (4) shall be lockable.

(6)  The soil or leaching bed fill around the perimeter of the cesspool shall be raised or mounded to a height of at least 150 mm above ground level.

(7)  The surface of the ground in the area of the cesspool shall be so graded that surface drainage in the area will be diverted away from the cesspool.

(8)  The cesspool shall be surrounded on all sides and on its bottom by at least 600 mm of soil or leaching bed fill, except the top where the cesspool extends to the surface of the ground.

Section 8.6. Class 4 Sewage Systems

8.6.1. General Requirements

8.6.1.1.  Scope

(1)  This section applies to the construction of a Class 4 sewage system.

8.6.1.2.  General Requirements

(1)  The treatment unit shall be connected to a leaching bed constructed in accordance with the requirements of Section 8.7.

8.6.1.3.  Pumps and Siphons

(1)  Where the total length of distribution pipe required is 150 m or more, the sewage system shall have at least one pump or a siphon contained in a dosing tank that may be a separate compartment within the tank structure, for distribution of the effluent.

(2)  Alternating siphons shall not be installed in a sewage system.

(3)  Where 2 or more pumps are employed within a dosing tank, the pumps shall be designed such that the pumps alternate dosing, and dosing shall continue in the event that one pump fails.

(4)  Where a pump or siphon is required, the pump or siphon shall be designed to discharge a dose of at least 75% of the internal volume of the distribution pipe within a time period not exceeding fifteen minutes.

8.6.2. Treatment Units

8.6.2.1.  Septic Tank Systems

(1)  Where a septic tank system has been designed to incorporate an effluent filter, the effluent filter shall form an integral part of the outlet device or be contained within a separate tank or compartment which may form an integral part of the septic tank structure.

(2)  All effluent filters shall be sized and installed in accordance with the manufacturer’s recommendations.

8.6.2.2.  Other Treatment Units

(1)  A treatment unit other than those described in Article 8.6.2.1. and Sentence (2) shall be designed such that effluent does not exceed the maximum concentrations stipulated in Column 2 of Table 8.6.2.2.A.

(2)  A treatment unit that is used in conjunction with a leaching bed constructed as shallow buried trenches shall be designed such that the effluent does not exceed the maximum concentrations stipulated in Column 3 of Table 8.6.2.2.A.

(3)  All treatment units referred to in Sentences (1) and (2) that contain mechanical components shall be equipped with an audible and visual warning alarm so located to warn the occupants of the building served or the operator of the treatment unit of a malfunction in the operation of the treatment unit.

(4)  All treatment units referred to in Sentences (1) and (2) shall permit the sampling of the effluent.

(5)  A treatment unit described in the Supplementary Guidelines to the 1997 OBC is deemed to comply with the requirements of Table 8.6.2.2.A. as set out in the Guideline.

(6)  Every manufacturer or distributor of a treatment unit shall provide, for each model sold, printed literature that describes the unit in detail and provides complete instructions regarding the operation, servicing, and maintenance requirements of the unit and its related components necessary to ensure the continued proper operation in accordance with the original design and specifications.

Table 8.6.2.2.A.

Forming Part of Sentences 8.6.2.2.(1), (2) and (5)

| Other Treatment Unit Effluent Quality Criteria |  |  |
| --- | --- | --- |
| Parameter | Secondary Effluent(1) | Tertiary Effluent(1) |
| BOD5 | 40 | 15 |
| CBOD5 | 30 | 10 |
| Suspended Solids | 30 | 10 |
| Column 1 | 2 | 3 |

(1) Maximum concentration based on 30 day averages in milligrams per Litre (mg/L)

Section 8.7. Leaching Beds

8.7.1. General Requirements

8.7.1.1.  Application

(1)  This Section is applicable to the construction of leaching beds.

8.7.2. Construction Requirements

8.7.2.1.  General Requirements

(1)  A leaching bed shall not be located

(a)	in an area that has an average slope that exceeds one unit vertically to four units horizontally,

(b)	in soil or leaching bed fill having a percolation time

(i)	less than one minute, or greater than 125 minutes if constructed as a shallow buried trench, or

(ii)	less than one minute, or greater than 50 minutes for all other leaching beds, or

(c)	in or on an area that is subject to flooding that may be expected to cause damage to the leaching bed or impair the operation of the leaching bed.

(2)  A leaching bed shall not be covered with any material having a hydraulic conductivity less than 0.01 m/day.

(3)  The surface of the leaching bed shall be shaped to shed water and together with the side slopes of any raised portion, shall be protected against erosion in such a manner as to not inhibit the evaporation and transpiration of waters from the soil or leaching bed fill, and to not cause plugging of the distribution pipe.

(4)  No part of a leaching bed shall be sloped steeper than one unit vertically to four units horizontally.

(5)  A leaching bed shall be designed to be protected from compaction or any stress or pressure that

(a)	may result in the impairment or destruction of any pipe in the leaching bed, or

(b)	may result in the smearing of the soil or leaching bed fill.

8.7.3. Absorption Trench Construction

8.7.3.1.  Length of Distribution Pipe

(1)  The total length of distribution piping shall

(a)	not be less than 30 m when constructed as a shallow buried trench, or

(b)	not be less than 40 m for any other absorption trench.

(2)  Except as provided in Sentences (1), (3), and (4), every leaching bed constructed by means of absorption trenches shall have a total length of distribution pipe not less than the value determined by the formula

L=QT200

where

| L Q T | = = = | total length of distribution pipe in metres the total daily design sanitary sewage flow in litres the design percolation time |
| --- | --- | --- |

(3)  Except as provided in Sentence (1), where the treatment unit is described in Article 8.6.2.2., the leaching bed may have a total length of distribution pipe not less than the value determined by the formula

L=QT300

where

| L Q T | = = = | total length of distribution pipe in metres the total daily design sanitary sewage flow in litres the design percolation time |
| --- | --- | --- |

(4)  Except as provided in Sentence (1), where the leaching bed is constructed as a shallow buried trench

(a)	the total length of distribution pipe when located in or on soil or leaching bed fill of 50 minutes or less, shall not be less than the value determined by the formula

L=Q75

where

| L Q | = = | total length of distribution pipe in metres the total daily design sanitary sewage flow in litres |
| --- | --- | --- |

(b)	the total length of distribution pipe when located in or on soil or leaching bed fill of more than 50 minutes, shall not be less than the value determined by the formula

L=Q40

where

| L Q | = = | total length of distribution pipe in metres the total daily design sanitary sewage flow in litres |
| --- | --- | --- |

8.7.3.2.  Absorption Trenches

(1)  Except as provided in Sentence (2), absorption trenches shall be

(a)	approximately the same length and not more than 30 m in length,

(b)	at least 500 mm and not more than 1 000 mm in width,

(c)	at least 600 mm and not more than 900 mm in depth,

(d)	centred at least 1 600 mm apart,

(e)	at least 900 mm at all points on the bottom of the absorption trench, or 900 mm from the surface of a filter bed above the high ground water table, rock or soil with a percolation time greater than 50 minutes, and

(f)	backfilled, after the installation of the distribution pipe with leaching bed fill, so as to ensure that after the leaching bed fill settles, the surface of the leaching bed will not form any depressions.

(2)  Absorption trenches constructed as shallow buried trenches shall be

(a)	approximately the same length and not more than 30 m in length,

(b)	at least 300 mm and not more than 600 mm in width,

(c)	at least 300 mm and not more than 600 mm in depth,

(d)	centred at least 1 600 mm apart,

(e)	at least 900 mm at all points on the bottom of the absorption trench above the high ground water table or rock, and

(f)	backfilled, after the installation of the distribution pipe with leaching bed fill, so as to ensure that after the leaching bed fill settles, the surface of the leaching bed will not form any depressions.

8.7.3.3.  Distribution Pipe

(1)  The distribution pipe used in the construction of a leaching bed shall be

(a)	of not less than 3 in. trade size for gravity flow systems, or 1 in. trade size for pressurized systems,

(b)	installed on a layer or covering at least 150 mm in depth and 500 mm in width comprised of stone that is either

(i)	19 mm clear aggregate washed to be free of fine material, or

(ii)	clean gravel screened to between 19 mm and 53 mm in size,

(c)	installed with a uniform downward slope from the inlet with a drop of not less than 30 mm and not more than 50 mm for each 10 m of distribution pipe, and

(d)	covered with stone of the type used below the distribution pipe to a height of at least 50 mm above the top of the distribution pipe.

(2)  Prior to backfilling, the stone layer required in Clause (1)(d) shall be protected in such a manner so as to prevent soil, or leaching bed fill from entering the stone by completely covering with

(a)	untreated building paper, or

(b)	a permeable geo-textile fabric.

(3)  Every pressurized distribution pipe shall be self-draining so as to prevent freezing of its contents.

(4)  Every pressurized distribution pipe shall have orifices of at least 3 mm in diameter, spaced equally along the length of the pipe.

8.7.4. Fill Based Absorption Trenches

8.7.4.1.  Loading Requirements

(1)  The area described in Sentence 8.7.4.2.(1) shall be designed such that the loading rate does not exceed, for soil having a percolation time set out in Column 1 of Table 8.7.4.1.A., the maximum value set out opposite thereto in Column 2 of Table 8.7.4.1.A.

Table 8.7.4.1.A.

Loading Rates for Fill Based Absorption Trenches and Filter Beds Forming Part of Sentences 8.7.4.1.(1) and 8.7.5.2.(2)

| Percolation Time (T) of Soil (min/cm) | Loading Rates (L/m2/day) |
| --- | --- |
| 1<T<20 | 10 |
| 20<T<35 | 8 |
| 35<T<50 | 6 |
| T>50 | 4 |
| Column 1 | Column 2 |

8.7.4.2.  Construction Requirements

(1)  A leaching bed comprised of absorption trenches may be constructed in leaching bed fill if unsaturated soil or leaching bed fill complying with Clause 8.7.2.1.(1)(b) extends

(a)	to a depth of at least 250 mm over the area covered by the leaching bed fill, and

(b)	for at least 15 m beyond the outer distribution pipes in any direction in which the effluent entering the soil or leaching bed fill will move horizontally.

(2)  If the unsaturated soil or leaching bed fill described in Sentence (1) has a percolation time greater than 15 minutes, any leaching bed fill added to form the leaching bed shall have a percolation time not less than 75% of the percolation time of the unsaturated soil or leaching bed fill.

(2.1)  Leaching bed fill that does not meet the requirements of Sentence (2) may be used to form the leaching bed if

(a)	the distance from the bottom of the absorption trench to native soil is not less than 900 mm, or

(b)	where the distance from the bottom of the absorption trench to native soil is less than 900 mm, the percolation time of the least permeable soil or leaching bed fill within 900 mm from the bottom of the absorption trench is used to calculate the length of the distribution pipe under Article 8.7.3.1.

(3)  Sentence (2) does not apply to any leaching bed fill added as backfill above the stone layer in which the distribution pipe is located.

(4)  All leaching bed fill added shall be stabilized against erosion.

(5)  The site to which the leaching bed fill is added shall be generally clear of vegetation.

(6)  The leaching bed fill that is added shall be compacted in layers in such a manner as to avoid uneven settlement of the distribution pipes.

(7)  Any distribution boxes, header lines, absorption trenches or distribution pipes shall be installed only after the leaching bed fill has been compacted in accordance with Sentence (6).

(8)  Except as provided in Sentence (8.1), the sides of the added leaching bed fill shall be sloped to ensure stability, but shall not be steeper than one unit vertically to four units horizontally.

(8.1)  The side slope of the leaching bed fill may be increased up to one unit vertically to three units horizontally if measures are taken to prevent erosion and ensure stability of the leaching bed fill.

(9)  The distances as set out in Column 2 of Table 8.2.1.6.B shall be increased by twice the height that the leaching bed is raised above the original grade.

8.7.5. Filter Beds

8.7.5.1.  Application

(1)  The total daily design sanitary sewage flow shall not exceed 5 000 L where the treatment unit is a septic tank, or 10 000 L where the treatment unit is described in Article 8.6.2.2.

8.7.5.2.  Loading Requirements

(1)  The effective area of the surface of the filter medium in each filter bed shall be at least 10 m2 and not more than 50 m2.

(2)  The area described in Sentence 8.7.4.2.(1) shall be designed such that the loading rate does not exceed, for soil having a percolation time set out in Column 1 of Table 8.7.4.1.A., the maximum value set out opposite thereto in Column 2 of Table 8.7.4.1.A.

(3)  Where the total daily design sanitary sewage flow does not exceed 3 000 L, the effective area shall be such that the loading on the surface of the filter medium does not exceed 75 L/m2 per day.

(4)  Where the total daily design sanitary sewage flow exceeds 3 000 L,

(a)	the effective area shall be such that the loading on the surface of the filter medium does not exceed 50 L/m2 per day, and

(b)	the leaching bed shall be comprised of more than one filter bed, each of similar size and adjacent to each other.

(5)  Where a treatment unit designed to produce effluent not exceeding the maximum concentrations stipulated in Column 2 of Table 8.6.2.2.A is used in conjunction with a filter bed, the effective area shall be such that the loading on the surface of the filter medium does not exceed 100 L/m2 per day.

8.7.5.3.  Construction Requirements

(1)  Sentences 8.7.4.2.(1) to (7) and (9) apply to the construction of a filter bed.

(2)  The lines of distribution pipe shall be evenly spaced over the surface of the filter medium to which the sanitary sewage is applied.

(3)  The filter medium shall have a minimum depth of 750 mm below the stone layer and shall be clean sand comprised of particles ranging in size between the limits of

(a)	an effective size of .25 mm with a uniformity coefficient not less than 3.5,

(b)	an effective size of 2.5 mm with a uniformity coefficient not greater than 1.5, and

(c)	having a uniformity coefficient not greater than 4.5.

(4)  The filter medium shall be unsaturated for its entire depth.

(5)  Where there is more than one filter bed in a leaching bed, the filter beds shall be separated by at least 5 m between the distribution pipes of the filter beds.

(6)  The base of the filter medium shall extend to a thickness of at least 250 mm over an area meeting the requirements of the following:

where

| A | = | the area of contact in square metres between the base of the filter medium and the underlying soil |
| --- | --- | --- |
| Q | = | the total daily design sanitary sewage flow in litres |
| T | = | the lesser of 50 and the percolation time of the underlying soil |

8.7.6. Shallow Buried Trenches

8.7.6.1.  Design Requirements

(1)  The design and installation of a shallow buried trench shall be carried out by a person competent in this field of work.

8.7.6.2.  Construction Requirements

(1)  The treatment unit shall provide an effluent quality as required in Sentence 8.6.2.2.(2).

(2)  The effluent shall be distributed through a pressurized distribution system having a pressure head of not less than 600 mm when measured to the most distant point from the pump.

(3)  A shallow buried trench shall not be constructed unless the soil or leaching bed fill is sufficiently dry to resist the compaction and smearing during excavation.

(4)  Every chamber shall be as wide as the shallow buried trench in which it is contained, and the cross-sectional height of the chamber at its centre point shall not be less than half the width of the trench.

(5)  Every chamber shall contain only one pressurized distribution pipe.

Section 8.8. Class 5 Sewage Systems

8.8.1. Application

8.8.1.1.  Prohibited Installation

(1)  Except as provided in Article 8.8.1.2., a Class 5 sewage system shall not be installed.

8.8.1.2.  Acceptable Installation

(1)  A Class 5 sewage system may be installed in the following circumstances:

(a)	where the proposed use of the sewage system is for a temporary operation, excluding seasonal recreational use, not exceeding 12 months in duration,

(b)	to permit the extension of an existing single-family dwelling provided that

(i)	the extension will not increase the wastewater load, and

(ii)	the building is already served by a Class 5 sewage system,

(c)	to remedy an unsafe sewage system where the remediation of the unsafe condition by the installation of a Class 4 sewage system is impracticable,

(d)	to upgrade a sewage system serving an existing building, where upgrading through the use of a Class 4 sewage system is not possible due to lot size, site slope or clearance limitations, or

(e)	as an interim measure for a lot or parcel of land until municipal sewers are available, provided that the municipality undertakes to ensure the continued operation of an approved hauled sewage system until the municipal sewers are available.

(2)  Where a Class 5 sewage system is installed, a written agreement for the disposal of sanitary sewage from the sewage system shall be entered into with a hauled sewage system operator.

8.8.2. General Requirements

8.8.2.1.  Construction Requirements

(1)  All Class 5 sewage systems shall be equipped with a device that shall produce an audible and visual warning alarm so located to warn that the sewage system is nearing capacity.

(2)  The device required in Sentence (1) shall be designed to provide suitable advance warning to the building occupants considering

(a)	the total daily design sanitary sewage flow,

(b)	the location of the Class 5 sewage system, and

(c)	the response time of the hauled sewage system contractor.

(3)  Except as provided in Sentence (4), all holding tanks shall be provided with a vent that

(a)	is not less than 3 in. trade size,

(b)	terminates at least

(i)	300 mm above finished grade with a vent cap, or

(ii)	600 mm above finished grade with a vent cap when the holding tank is located in an area subject to flooding, and

(c)	terminates at least 3.5 m away from any air inlet, window, or door.

(4)  A vent from a holding tank may connect into the venting system of the building served by the holding tank provided that

(a)	the vent is not less than 3 in. trade size, and

(b)	the installation of the vent shall conform to the requirements in Part 7.

8.8.2.2.  Sizing of Holding Tanks

(1)  All holding tanks used in residential dwellings shall have a minimum 7 day holding capacity based on the total daily design sanitary sewage flow.

Section 8.9. Operation and Maintenance

8.9.1. General

8.9.1.1.  Scope

(1)  This Section applies to the operation and maintenance of all sewage systems.

8.9.1.2.  General Requirements for Operation and Maintenance

(1)  Every sewage system shall be operated and maintained so that

(a)	the sewage system or any part thereof shall not emit, discharge or deposit sanitary sewage or effluent onto the surface of the ground,

(b)	sanitary sewage or effluent shall not emit, discharge, seep, leak or otherwise escape from the sewage system or any part thereof other than from a place or part of the sewage system where the system is designed or intended to discharge the sanitary sewage or effluent, and

(c)	except as provided in Sentence (2), sanitary sewage or effluent shall not emit, discharge, seep, leak or otherwise escape from the sewage system or any part thereof into a piped water supply, well water supply, a watercourse, ground water or surface water.

(2)  Clause (1)(c) does not apply to the use of a sewage system designed and operated such that properly treated effluent is discharged into soil.

8.9.2. Operation

8.9.2.1.  Scope

(1)  The requirement of this Subsection are in addition to the requirements of Subsection 8.9.1.

8.9.2.2.  General

(1)  Every sewage system shall be operated in accordance with

(a)	the basis on which the construction and use of the sewage system was approved or required under this Act or predecessor legislation, as the case may be, and

(b)	the requirements of the manufacturer of the sewage system.

8.9.2.3.  Class 4 Sewage Systems

(1)  Every Class 4 sewage system shall be operated in accordance with the literature required in Sentence 8.6.2.2.(6).

(2)  No person shall operate a treatment unit other than a septic system unless the person has entered into an agreement whereby servicing and maintenance of the treatment unit and its related components will be carried out by a person who

(a)	possesses a copy of the literature required by Sentence 8.6.2.2.(6), and

(b)	is authorized by the manufacturer to service and maintain that type of treatment unit.

(3)  The person authorized by the manufacturer to service and maintain the treatment unit and who has entered into the agreement referred to in Sentence (2) with the person operating the treatment unit shall notify the chief building official if

(a)	the agreement is terminated, or

(b)	access for service and maintenance of the treatment unit is denied by the person operating the treatment unit.

8.9.2.4.  Shallow Buried Trenches

(1)  Every person operating a treatment unit that is designed and constructed to produce effluent described in Column 3 of Table 8.6.2.2.A. shall, at the intervals described in Sentence (2)

(a)	take a grab sample of the effluent to determine whether it complies with the levels contained in Column 3 of Table 8.6.2.2.A. for BOD5 and suspended solids,

(b)	carry out the sampling required by Clause (1)(a) in accordance with the methods described in the “Standard Methods for the Examination of Water and Wastewater”, and

(c)	promptly submit the results of the sampling required by Clause (1)(a) to the chief building official.

(2)  The sampling required by Clause (1)(a) shall be conducted

(a)	initially, once during the first 12 months after the sewage system was put into use, and

(b)	thereafter, once during every 12 month period, at least 10 months and not more than 18 months after the previous sampling has been completed.

8.9.2.5.  Class 5 Sewage Systems

(1)  Every Class 5 sewage system shall be operated in accordance with the agreement referred to in Sentence 8.8.1.2.(2).

(2)  No Class 5 sewage system shall be operated once it is filled with sanitary sewage until such time as the sanitary sewage is removed from the sewage system.

8.9.3. Maintenance

8.9.3.1.  Scope

(1)  The requirement of this Subsection are in addition to the requirements of Subsection 8.9.1.

8.9.3.2.  General

(1)  Every sewage system shall be maintained so that

(a)	the construction of the sewage system remains in accordance with

(i)	the basis on which the construction and use of the sewage system was approved or required under this Act or predecessor legislation, as the case may be, and

(ii)	the requirements of the manufacturer of the sewage system, and

(b)	all components of the sewage system function in their intended manner.

(2)  The land in the vicinity of a sewage system shall be maintained in a condition that will not cause damage to, or impair the functioning of, the sewage system.

8.9.3.3.  Interceptors

(1)  Every grease interceptor referred to in Article 8.1.3.1. shall be maintained so that the grease retained is below the rated capacity of the interceptor.

8.9.3.4.  Class 4 Sewage Systems

(1)  Septic tanks and other treatment units shall be cleaned whenever sludge and scum occupy one-third of the working capacity of the tank.

8.9.3.5.  Shallow Buried Trenches

(1)  The pressure head at the furthest point from the pump in all distribution pipes shall be checked for compliance with Article 8.7.6.2. and the design specification at least every 36 months.

O. Reg. 22/98, s. 18; O. Reg. 122/98, ss. 2-6; O. Reg. 278/99, ss. 5-18; O. Reg. 220/02, ss. 10, 11.

Part 9
Housing and Small Buildings

| Section | 9.1. | General |
| --- | --- | --- |
|  | 9.1.1. | Scope |
| Section | 9.2. | Definitions |
|  | 9.2.1. | General |
| Section | 9.3 | Materials, Systems and Equipment |
|  | 9.3.1. | Concrete |
|  | 9.3.2. | Lumber and Wood Products |
|  | 9.3.3. | Metal |
| Section | 9.4. | Structural Requirements |
|  | 9.4.1. | General |
|  | 9.4.2. | Specified Loads |
|  | 9.4.3. | Deflections |
|  | 9.4.4. | Foundation Conditions |
| Section | 9.5. | Design of Areas and Spaces |
|  | 9.5.1. | General |
|  | 9.5.2. | Barrier-Free Design |
|  | 9.5.3. | Ceiling Heights |
|  | 9.5.4. | Living Rooms or Spaces Within Dwelling Units |
|  | 9.5.5. | Dining Rooms or Spaces Within Dwelling Units |
|  | 9.5.6. | Kitchens Within Dwelling Units |
|  | 9.5.7. | Bedrooms or Spaces in Dwelling Units and Dormitories |
|  | 9.5.7A. | Combined Spaces |
|  | 9.5.8. | Bathrooms and Water-Closet Rooms |
|  | 9.5.9. | Hallways |
| Section | 9.6. | Doors |
|  | 9.6.1. | General |
|  | 9.6.2. | Required Doors |
|  | 9.6.3. | Doorway Sizes |
|  | 9.6.4. | Door Sill Height |
|  | 9.6.5. | Exterior Doors |
|  | 9.6.6. | Glass |
|  | 9.6.7. | Thermal Breaks |
|  | 9.6.8. | Resistance to Forced Entry |
| Section | 9.7. | Windows and Skylights |
|  | 9.7.1. | General |
|  | 9.7.2. | Window Standards |
|  | 9.7.3. | Glass |
|  | 9.7.4. | Caulking and Glazing |
|  | 9.7.5. | Protection of Windows in Public Areas |
|  | 9.7.6. | Resistance to Forced Entry |
|  | 9.7.7. | Skylights |
| Section | 9.8. | Stairs, Ramps, Handrails and Guards |
|  | 9.8.1. | Scope |
|  | 9.8.2. | General |
|  | 9.8.3. | Stair Dimensions |
|  | 9.8.4. | Landings |
|  | 9.8.5. | Curved Stairs and Winders |
|  | 9.8.6. | Pedestrian Ramps |
|  | 9.8.7. | Handrails |
|  | 9.8.8. | Guards |
|  | 9.8.9. | Construction |
|  | 9.8.10. | Cantilevered Precast Concrete Steps |
| Section | 9.9. | Means of Egress |
|  | 9.9.1. | Scope |
|  | 9.9.2. | General |
|  | 9.9.3. | Dimensions of Means of Egress |
|  | 9.9.4. | Fire Protection of Exits |
|  | 9.9.5. | Obstructions and Hazards in Means of Egress |
|  | 9.9.6. | Doors in a Means of Egress |
|  | 9.9.7. | Access to Exits |
|  | 9.9.8. | Exits from Floor Areas |
|  | 9.9.9. | Egress from Dwelling Units |
|  | 9.9.10. | Signage |
|  | 9.9.11. | Lighting |
| Section | 9.10. | Fire Protection |
|  | 9.10.1. | General |
|  | 9.10.2. | Occupancy Classification |
|  | 9.10.3. | Ratings |
|  | 9.10.4. | Building Size Determination |
|  | 9.10.5. | Permitted Openings in Wall and Ceiling Membranes |
|  | 9.10.6. | Construction Types |
|  | 9.10.7. | Steel Members |
|  | 9.10.8. | Fire Resistance in Relation to Occupancy and Height |
|  | 9.10.9. | Fire Separations Between Rooms and Spaces Within Buildings |
|  | 9.10.10. | Service Rooms |
|  | 9.10.11. | Firewalls |
|  | 9.10.12. | Prevention of Fire Spread at Exterior Walls and between Storeys |
|  | 9.10.13. | Doors, Dampers and Other Closures in Fire Separations |
|  | 9.10.14. | Spatial Separations between Buildings |
|  | 9.10.15. | Fire Stops |
|  | 9.10.16. | Flame Spread Limits |
|  | 9.10.17. | Alarm and Detection Systems |
|  | 9.10.18. | Smoke Alarms |
|  | 9.10.19. | Fire-fighting |
|  | 9.10.20. | Fire Protection for Construction Camps |
|  | 9.10.21. | Fire Protection for Gas and Electric Ranges |
| Section | 9.11. | Sound Control |
|  | 9.11.1. | Sound Transmission Class Rating (Airborne Sound) |
|  | 9.11.2. | Required Sound Control Locations (Airborne Sound) |
| Section | 9.12. | Excavation |
|  | 9.12.1. | General |
|  | 9.12.2. | Depth |
|  | 9.12.3. | Backfill |
|  | 9.12.4. | Trenches Beneath Footings |
| Section | 9.13. | Dampproofing, Waterproofing and Soil Gas Control |
|  | 9.13.1. | General |
|  | 9.13.2. | Material |
|  | 9.13.3. | Dampproofing of Walls |
|  | 9.13.4. | Dampproofing of Floors-on-Ground |
|  | 9.13.5. | Waterproofing of Walls |
|  | 9.13.6. | Waterproofing of Floors-on-Ground |
|  | 9.13.7. | Soil Gas |
| Section | 9.14. | Drainage |
|  | 9.14.1. | Scope |
|  | 9.14.2. | Foundation Drainage |
|  | 9.14.3. | Drainage Tile and Pipe |
|  | 9.14.4. | Granular Drainage Layer |
|  | 9.14.5. | Drainage Disposal |
|  | 9.14.6. | Surface Drainage |
| Section | 9.15. | Footings and Foundations |
|  | 9.15.1. | Scope |
|  | 9.15.2. | General |
|  | 9.15.3. | Footings |
|  | 9.15.4. | Foundation Walls |
|  | 9.15.5. | Joist and Beam Support |
|  | 9.15.6. | Parging and Finishing |
| Section | 9.16. | Slabs-on-Ground |
|  | 9.16.1. | Scope |
|  | 9.16.2. | Granular Material beneath Floors |
|  | 9.16.3. | Drainage |
|  | 9.16.4. | Concrete |
|  | 9.16.5. | Wood |
| Section | 9.17. | Columns |
|  | 9.17.1. | Scope |
|  | 9.17.2. | General |
|  | 9.17.3. | Steel Columns |
|  | 9.17.4. | Wood Columns |
|  | 9.17.5. | Unit Masonry Columns |
|  | 9.17.6. | Solid Concrete Columns |
| Section | 9.18. | Crawl Spaces |
|  | 9.18.1. | General |
|  | 9.18.2. | Access |
|  | 9.18.3. | Ventilation |
|  | 9.18.4. | Clearance |
|  | 9.18.5. | Drainage |
|  | 9.18.6. | Ground Cover |
|  | 9.18.7. | Fire Protection |
| Section | 9.19. | Roof Spaces |
|  | 9.19.1. | Venting |
|  | 9.19.2. | Access |
| Section | 9.20. | Above-Grade Masonry |
|  | 9.20.1. | Scope |
|  | 9.20.2. | Masonry Units |
|  | 9.20.3. | Mortar |
|  | 9.20.4. | Masonry Joints |
|  | 9.20.5. | Masonry Support |
|  | 9.20.6. | Thickness and Height |
|  | 9.20.7. | Chases and Recesses |
|  | 9.20.8. | Support of Loads |
|  | 9.20.9. | Bonding and Tying |
|  | 9.20.10. | Lateral Support |
|  | 9.20.11. | Anchorage of Roofs, Floors and Intersecting Walls |
|  | 9.20.12. | Corbelling |
|  | 9.20.13. | Control of Rain Water Penetration |
|  | 9.20.14. | Protection during Work |
|  | 9.20.15. | Reinforcement for Earthquake Resistance |
|  | 9.20.16. | Corrosion Resistance |
| Section | 9.21. | Chimneys and Flues |
|  | 9.21.1. | General |
|  | 9.21.2. | Chimney Flues |
|  | 9.21.3. | Chimney lining |
|  | 9.21.4. | Masonry and Concrete Chimney Construction |
|  | 9.21.5. | Clearance from Combustible Construction |
| Section | 9.22. | Fireplaces |
|  | 9.22.1. | General |
|  | 9.22.2. | Fireplace Liners |
|  | 9.22.3. | Fireplace Walls |
|  | 9.22.4. | Fire Chamber |
|  | 9.22.5. | Hearth |
|  | 9.22.6. | Damper |
|  | 9.22.7. | Smoke Chamber |
|  | 9.22.8. | Factory-Built Fireplaces |
|  | 9.22.9. | Clearance of Combustible Material |
|  | 9.22.10. | Fireplace Inserts |
| Section | 9.23. | Wood-Frame Construction |
|  | 9.23.1. | Scope |
|  | 9.23.2. | General |
|  | 9.23.3. | Fasteners |
|  | 9.23.4. | Maximum Spans |
|  | 9.23.5. | Notching and Drilling |
|  | 9.23.6. | Anchorage |
|  | 9.23.7. | Sill Plates |
|  | 9.23.8. | Beams to Support Floors |
|  | 9.23.9. | Floor Joists |
|  | 9.23.10. | Wall Studs |
|  | 9.23.11. | Wall Plates |
|  | 9.23.12. | Framing Over Openings |
|  | 9.23.13. | Roof and Ceiling Framing |
|  | 9.23.14. | Subflooring |
|  | 9.23.15. | Roof Sheathing |
|  | 9.23.16. | Wall Sheathing |
|  | 9.23.17. | Wall Sheathing Paper |
| Section | 9.24. | Sheet Steel Stud Wall Framing |
|  | 9.24.1. | General |
|  | 9.24.2. | Size of Framing |
|  | 9.24.3. | Installation |
| Section | 9.25. | Heat Transfer, Air Leakage and Condensation Control |
|  | 9.25.1. | Scope |
|  | 9.25.2. | Thermal Insulation |
|  | 9.25.3. | Air Barrier Systems |
|  | 9.25.4. | Vapour Barriers |
| Section | 9.26. | Roofing |
|  | 9.26.1. | General |
|  | 9.26.2. | Roofing Materials |
|  | 9.26.3. | Roof Slope |
|  | 9.26.4. | Flashing at Intersections |
|  | 9.26.5. | Eave Protection for Shingles and Shakes |
|  | 9.26.6. | Underlay beneath Shingles |
|  | 9.26.7. | Asphalt Shingles on Slopes of 1 in 3 and Greater |
|  | 9.26.8. | Asphalt Shingles on Slopes of Less than 1 in 3 |
|  | 9.26.9. | Wood Roof Shingles |
|  | 9.26.10. | Handsplit Roof Shakes |
|  | 9.26.11. | Built-Up Roofs |
|  | 9.26.12. | Selvage Roofing |
|  | 9.26.13. | Sheet Metal Roofing |
|  | 9.26.14. | Glass Reinforced Polyester Roofing |
|  | 9.26.15. | Hot Applied Rubberized Asphalt Roofing |
|  | 9.26.16. | Polyvinyl Chloride Sheet Roofing |
|  | 9.26.17. | Concrete Roof Tiles |
|  | 9.26.18. | Downspouts and Roof Drains |
| Section | 9.27. | Cladding |
|  | 9.27.1. | Scope |
|  | 9.27.2. | General |
|  | 9.27.3. | Flashing |
|  | 9.27.4. | Caulking |
|  | 9.27.5. | Attachment of Cladding |
|  | 9.27.6. | Lumber Siding |
|  | 9.27.7. | Wood Shingles and Machine Grooved Shakes |
|  | 9.27.8. | Asbestos-Cement Shingles and Sheets |
|  | 9.27.9. | Plywood |
|  | 9.27.10. | Hardboard |
|  | 9.27.11. | OSB and Waferboard |
|  | 9.27.12. | Metal Siding |
|  | 9.27.13. | Vinyl Siding |
| Section | 9.28. | Stucco |
|  | 9.28.1. | General |
|  | 9.28.2. | Stucco Materials |
|  | 9.28.3. | Fasteners |
|  | 9.28.4. | Stucco Lath |
|  | 9.28.5. | Stucco Mixes |
|  | 9.28.6. | Stucco Application |
| Section | 9.29. | Interior Wall and Ceiling Finishes |
|  | 9.29.1. | General |
|  | 9.29.2. | Waterproof Wall Finish |
|  | 9.29.3. | Wood Furring |
|  | 9.29.4. | Plastering |
|  | 9.29.5. | Gypsum Board Finish (Taped Joints) |
|  | 9.29.6. | Plywood Finish |
|  | 9.29.7. | Hardboard Finish |
|  | 9.29.8. | Insulating Fibreboard Finish |
|  | 9.29.9. | Particleboard, OSB or Waferboard Finish |
|  | 9.29.10. | Wall Tile Finish |
| Section | 9.30. | Flooring |
|  | 9.30.1. | General |
|  | 9.30.2. | Panel-Type Underlay |
|  | 9.30.3. | Wood Strip Flooring |
|  | 9.30.4. | Parquet Flooring |
|  | 9.30.5. | Resilient Flooring |
|  | 9.30.6. | Ceramic Tile |
| Section | 9.31. | Plumbing Facilities |
|  | 9.31.1. | Scope |
|  | 9.31.2. | General |
|  | 9.31.3. | Water Supply and Distribution |
|  | 9.31.4. | Required Facilities |
|  | 9.31.5. | Reserved |
|  | 9.31.6. | Service Water Heating Facilities |
| Section | 9.32. | Ventilation |
|  | 9.32.1. | General |
|  | 9.32.2. | Natural Ventilation |
|  | 9.32.3. | Mechanical Ventilation |
| Section | 9.33. | Heating and Air-Conditioning |
|  | 9.33.1. | General |
|  | 9.33.2. | Required Heating Systems |
|  | 9.33.3. | Design Temperatures |
|  | 9.33.4. | Carbon Monoxide Detectors |
| Section | 9.34. | Electrical Facilities |
|  | 9.34.1. | General |
|  | 9.34.2. | Lighting Outlets |
|  | 9.34.3. | Emergency Lighting |
|  | 9.34.4. | Service Entrance Requirements |
| Section | 9.35. | Garages and Carports |
|  | 9.35.1. | Scope |
|  | 9.35.2. | General |
|  | 9.35.3. | Foundations |
|  | 9.35.4. | Walls and Columns |
| Section | 9.36. | Cottages |
|  | 9.36.1. | Scope |
|  | 9.36.2. | General |
|  | 9.36.3. | Tourist Accommodation |
| Section | 9.37. | Log Construction |
|  | 9.37.1. | General |
|  | 9.37.2. | Walls |
|  | 9.37.3. | Lintels |
| Section | 9.38. | Thermal design |
|  | 9.38.1. | Scope |
|  | 9.38.2. | General |
|  | 9.38.3. | Thermal Resistance of Assemblies |
|  | 9.38.4. | Glazing |
|  | 9.38.5. | Doors and Windows |
|  | 9.38.6. | Infiltration |
|  | 9.38.7. | Ventilation |
| Section | 9.39 | Park Model Trailers |
|  | 9.39.1. | Scope |
|  | 9.39.2. | General |
|  | 9.39.3. | Requirements |
| Section | 9.40 | Construction of Farm Buildings |
|  | 9.40.1. | Scope |
|  | 9.40.2. | Lumber |
|  | 9.40.3. | Structural Requirements |
| Section | 9.41 | Additional Requirements for Change of Use |
|  | 9.41.1. | Scope |
|  | 9.41.2. | Requirements |

Part 9
Housing and Small Buildings

Section 9.1. General

9.1.1. Scope

9.1.1.1.  Scope

(1)  The scope of this Part shall be as described in Section 2.1.

9.1.1.2.  Signs

(1)  Signs shall conform to the requirements in Section 3.14.

9.1.1.3.  Self-Service Storage Buildings

(1)  Self-service storage buildings shall conform to the requirements in Section 3.10.

9.1.1.4.  Tents and Air-Supported Structures

(1)  Tents shall conform to the requirements in Subsection 3.13.1.

(2)  Air-supported structures shall conform to the requirements in Subsection 3.13.2.

9.1.1.5.  Proximity to Existing Above Ground Electrical Conductors

(1)  Where a building is constructed in close proximity to existing above ground electrical conductors the requirements of Subsection 3.1.18. shall apply.

9.1.1.6.  Food Premises

(1)  The requirements of Subsection 3.7.6. apply to all food premises.

Section 9.2. Definitions

9.2.1. General

9.2.1.1.  Defined Words

(1)  Words in italics are defined in Part 1.

Section 9.3. Materials, Systems and Equipment

9.3.1. Concrete

9.3.1.1.  Concrete

(1)  Concrete shall be designed, mixed, placed, cured and tested in accordance with CAN3-A438-M, “Concrete Construction for Housing and Small Buildings.”

9.3.1.2.  Cement

(1)  Cement shall meet the requirements of CAN/CSA-A5, “Portland Cements.”

9.3.1.3.  Concrete in Contact with Sulfate Soil

(1)  Concrete in contact with sulfate soil deleterious to normal cement shall conform to the requirements in Clause 15.5 of CAN/CSA-A23.1, “Concrete Materials and Methods of Concrete Construction.”

9.3.1.4.  Aggregates

(1)  Aggregates shall

(a)	consist of sand, gravel, crushed rock, crushed air-cooled blast furnace slag, expanded shale or expanded clay conforming to CAN/CSA-A23.1, “Concrete Materials and Methods of Concrete Construction”, and

(b)	be clean, well-graded and free of injurious amounts of organic and other deleterious material.

9.3.1.5.  Water

(1)  Water shall be clean and free of injurious amounts of oil, organic matter, sediment or any other deleterious material.

9.3.1.6.  Compressive Strength

(1)  Except as provided elsewhere in this Part, the compressive strength of unreinforced concrete after 28 days shall be not less than

(a)	32 MPa for garage and carport floors and all exterior flatwork, and

(b)	15 MPa for all other applications.

(2)  Concrete used for garage and carport floors and exterior steps shall have air entrainment of 5 to 8%.

9.3.1.7.  Site Mixed Concrete

(1)  The concrete mixes described in Table 9.3.1.7. shall be considered acceptable if, when measured according to the slump test described in Appendix A of CAN3-A438-M, “Concrete Construction for Housing and Small Buildings,” the slump does not exceed

(a)	150 mm for footings for walls, columns, fireplaces and chimneys, foundation walls, grade beams and piers, or

(b)	100 mm for garage and carport floors and all exterior flatwork.

Table 9.3.1.7.

Site Mixed Concrete Proportions(1)

Forming Part of Sentence 9.3.1.7.(1)

| Maximum Size of Course Aggregate mm | Materials, volume |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Cement |  | Fine Aggregate (damp average course sand) |  | Course Aggregate (gravel or crushed stone) |  |
|  | Parts | L(2) | Parts | L | Parts | L |
| 14 | 1 | 28 | 1.75 | 49 | 2 | 56 |
| 20 | 1 | 28 | 1.75 | 49 | 2.5 | 70 |
| 28 | 1 | 28 | 2 | 56 | 3 | 84 |
| 40 | 1 | 28 | 2 | 56 | 3.5 | 98 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 |

Notes to Table 9.3.1.7.:

(1)	 The concrete strength obtained from these proportions will be in excess of the minimum strengths required in Sentence 9.3.1.6.(1).

(2)	 A 40 kg bag of cement contains 28 L.

(2)  Aggregate for unreinforced concrete mixes referred to in Sentence (1) shall not exceed in size

(a)	1/5 the distance between the sides of vertical forms, or

(b)	1/3 the thickness of flatwork.

9.3.1.8.  Admixtures

(1)  Admixtures shall conform to CAN3-A266.1-M, “Air Entraining Admixtures for Concrete” or CAN3-A266.2-M, “Chemical Admixtures for Concrete,” as applicable.

9.3.1.9.  Reinforced Concrete

(1)  Reinforced concrete shall be designed to conform to the requirements of Part 4.

9.3.1.10.  Cold Weather Requirements

(1)  When the air temperature is below 5oC, concrete shall be

(a)	kept at a temperature of not less than 10oC or more than 25oC while being placed, and

(b)	maintained at a temperature of not less than 10oC for 72 h after placing.

(2)  No frozen material or ice shall be used in concrete described in Sentence (1).

9.3.2. Lumber and Wood Products

9.3.2.1.  Grade Marking

(1)  Lumber for joists, rafters, trusses and beams and for the uses listed in Table 9.3.2.1. shall be identified by a grade stamp to indicate its grade as determined by the NLGA “Standard Grading Rules for Canadian Lumber.”

Table 9.3.2.1.

Minimum Lumber Grades for Specific End Uses

Forming Part of Sentence 9.3.2.1.(1)

| Use | Boards |  |  | Framing |
| --- | --- | --- | --- | --- |
|  | Paragraph in the NLGA grading rules under which boards are graded |  |  |  |
|  | All Species |  | Eastern White Pine & Red Pine | All Species |
|  | Para 113 | Para 114 | Para 118 |  |
| Stud wall framing (loadbearing members) | — | — | — | Stud, Standard No. 2 |
| Stud wall framing (non-loadbearing members) | — | — | — | Stud, Utility No. 3 |
| Plank frame construction (loadbearing members) | No. 3 Common | — | No. 3 Common | No. 2 |
| Plank frame construction (non-loadbearing members) | No. 5 Common | — | No. 5 Common | Economy, No 3 |
| Post and beams less than 114 mm thickness | — | — | — | Standard, No.2 |
| Post and beams not less than 114 mm thickness | — | — | — | Standard |
| Roof sheathing | No. 3 Common | Standard | No. 4 Common | — |
| Subflooring | No. 3 common | Standard | No. 3 Common | — |
| Wall sheathing when required as a nailing base | No. 4 Common | Utility | No. 4 Common | — |
| Wall sheathing not required as a nailing base | No. 5 Common | Common | No. 5 Common | — |
| Column 1 | 2 | 3 | 4 | 5 |

9.3.2.2. Lumber Grades

(1)  Except for joists, rafters, trusses and beams, visually graded lumber shall conform to the grades in Table 9.3.2.1.

9.3.2.3.  Machine Stress Rated Lumber

(1)  Machine stress rated lumber shall conform to the requirements of Subsection 4.3.1.

9.3.2.4.  OSB, Waferboard and Plywood Marking

(1)  OSB, waferboard and plywood used for roof sheathing, wall sheathing and subflooring shall be legibly identified on the face of the material indicating

(a)	the manufacturer of the material,

(b)	the standard to which it is produced, and

(c)	that the material is of an exterior type.

9.3.2.5.  Moisture Content

(1)  Moisture content of lumber shall be not more than 19% at the time of installation.

9.3.2.6.  Lumber Dimensions

(1)  Lumber dimensions referred to in this Part are actual dimensions determined in conformance with CAN/CSA-O141, “Softwood Lumber”.

9.3.2.7.  Panel Thickness Tolerances

(1)  The thickness specified in this Part for plywood, hardboard, particleboard, OSB and waferboard shall be subject to the tolerances permitted in the standards referenced for these products unless specifically indicated herein.

9.3.2.8.  Undersized Lumber

(1)  Joist, rafter, lintel and beam members up to 5% less than the actual Canadian standard sizes are permitted to be used provided the allowable spans for the grade and species of lumber under consideration are reduced 5% from those shown in the span tables for full size members.

9.3.2.9.  Termite and Decay Protection

(1)  In localities where termites are known to occur, the clearance between structural wood elements and the ground shall be not less than 450 mm, unless the structural wood elements are pressure treated with a chemical that is toxic to termites.

(2)  Structural wood elements shall be pressure treated with a preservative to resist decay where

(a)	the structural wood elements are in contact with the ground, or

(b)	the vertical clearance between structural wood elements and the ground is less than 150 mm.

(3)  Where wood is required by this Article to be treated to resist termites or decay, such treatment shall be in accordance with the requirements of

(a)	CAN/CSA-O80.1-M, “Preservative Treatment of All Timber Products by Pressure Process”,

(b)	CAN/CSA-O80.2-M, “Preservative Treatment of Lumber, Timber, Bridge Ties and Mine Ties by Pressure Process”,

(c)	CAN/CSA-O80.9-M, “Preservative Treatment of Plywood by Pressure Process”, or

(d)	CAN/CSA-O80.15-M, “Preservative Treatment of Wood for Building Foundation Systems, Basements and Crawl Spaces by Pressure Process”.

9.3.3. Metal

9.3.3.1.  Sheet Metal Thickness

(1)  Minimum thickness for sheet material given in this Part refer to the actual minimum thickness measured at any point of the material, and in the case of galvanized steel, include the thickness of the coating unless otherwise indicated.

9.3.3.2.  Galvanized Sheet Steel

(1)  Where galvanized sheet steel is intended for use in locations exposed to weather or as a flashing material, it shall have a zinc coating not less than the G90 coating designation in

(a)	ASTM A 653, “Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvanealed) by the Hot-Dip Process”, or

(b)	ASTM A 924, “Specification for General Requirements for Steel Sheet, Metallic-Coated by the Hot Dip Process”.

Section 9.4. Structural Requirements

9.4.1. General

9.4.1.1.  Structural Design

(1)  Except as provided in Sentence (2), Sentence 9.23.4.2.(2) and Subsections 9.4.2. to 9.4.4. and Subsection 9.40.3., structural members and their connections shall be designed in conformance with Part 4.

(2)  Where structural members and their connections conform to the requirements listed elsewhere in this Part, it shall be deemed that the structural design requirements have been met.

9.4.1.2.  Post, Beam and Plank Construction

(1)  Except for columns described in Section 9.17. and beams described in Subsection 9.23.4., post, beam and plank construction with the loadbearing framing members spaced more than 600 mm apart shall be designed in conformance with Subsection 4.3.1.

9.4.2. Specified Loads

9.4.2.1.  Application

(1)  This Subsection applies to wood frame assemblies with clear spans not exceeding 12.20 m and members spaced not more than 600 mm apart.

9.4.2.2.  Design Snow Loads

(1)  Except as provided in Sentences (2) and (3), specified snow loads shall be not less than the composite snow load listed in Column 12 of Table 2.5.1.1.

(2)  Where the entire width of a roof does not exceed 4.3 m, the specified snow load shall be not less than the composite snow load listed in Column 13 of Table 2.5.1.1.

(3)  In no case shall the specified snow load be less than 1 kPa.

(4)  Bow string, arch or semi-circular roof trusses having an unsupported span greater than 6 m shall be designed in conformance with the snow load requirements in Subsection 4.1.7.

9.4.2.3.  Balconies

(1)  Residential balconies not used as passageways shall be designed to carry the specified roof snow load or 1.9 kPa, whichever is greater.

9.4.2.4.  Attics

(1)  Residential attics having limited accessibility to preclude storage of equipment or material are permitted to be designed for a total specified load of 0.5 kPa, where the total specified load is the sum of the specified dead load plus the specified live ceiling load.

9.4.3. Deflections

9.4.3.1.  Deflections

(1)  The maximum deflection of structural members shall conform to Table 9.4.3.1.

Table 9.4.3.1.

Maximum Deflections

Forming Part of Sentence 9.4.3.1.(1)

| Structural Members | Type of Ceiling Supported | Max. Allowable Deflection as an Expressed Ratio of the Clear Span |
| --- | --- | --- |
| Roof rafters, roof joists, roof beams and roof decking of plank and beam construction | No ceiling | 1/180 |
|  | Other than plaster or gypsum board | 1/240 |
|  | Plaster or gypsum board | 1/360 |
| Ceiling joists | Other than plaster or gypsum board | 1/240 |
|  | Plaster or gypsum board | 1/360 |
| Floor beams, floor joists and floor decking | All cases | 1/360 |
| Column 1 | 2 | 3 |

(2)  Dead loads need not be considered in computing deflections referred to in Sentence (1).

9.4.4. Foundation Conditions

9.4.4.1.  Allowable Bearing Pressures

(1)  Where footing sizes for shallow foundations are not determined in conformance with Section 9.15., footings are permitted to be designed using maximum allowable bearing pressures in Table 9.4.4.1.

Table 9.4.4.1.

Allowable bearing Pressure for Soil or Rock

Forming Part of Sentence 9.4.4.1.(1)

| Type and Condition of Soil or Rock | Maximum Allowable Bearing Pressure, kPa |
| --- | --- |
| Dense or compact sand or gravel | 150 |
| Loose sand or gravel | 50 |
| Dense or compact silt | 100 |
| Stiff clay | 150 |
| Firm clay | 75 |
| Soft clay | 40 |
| Till | 200 |
| Clay shale | 300 |
| Sound rock | 500 |
| Column 1 | 2 |

(2)  The design procedures described in Section 4.2 are permitted to be used in lieu of the design procedures in this Subsection.

(3)  The design procedures described in Section 4.2 shall be used where

(a)	deep foundations are used,

(b)	the footing size falls outside the scope of this Section, or

(c)	the foundation is constructed on peat, filled ground or on sensitive clays as described in Article 9.15.1.1.

9.4.4.2.  Foundation Capacity in Weaker Soil and Rock

(1)  Where a soil or rock within a distance equal to twice the footing width below the bearing surface has a lower allowable bearing pressure than that at the bearing surface as shown in Article 9.4.4.1., the design capacity of the foundation shall not be greater than would cause the weakest soil or rock to be stressed beyond its allowable bearing pressure.

(2)  In calculating subsurface pressures referred to in Sentence (1), the loads from the footings shall be assumed to be distributed uniformly over a horizontal plane within a frustum extending downward from the footing at an angle of 60o to the horizontal.

9.4.4.3.  High Water Table

(1)  Where a foundation bears on gravel, sand or silt, and the water table is within a distance below the bearing surface equal to the width of the foundation, the allowable bearing pressure shall be 50% of that determined in Article 9.4.4.1.

9.4.4.4.  Soil Movement

(1)  Where a foundation is located in an area in which soil movement caused by changes in soil moisture content is known to occur to the extent that it will cause significant damage to a building, measures shall be taken to minimize the effect of such movement on the building.

9.4.4.5.  Walls Supporting Drained Earth

(1)  Walls supporting drained earth are permitted to be designed for pressure equivalent to that exerted by a fluid with a density of not less than 480 kg/m3 and having a depth equal to that of the retained earth.

(2)  Any surcharge shall be in addition to the equivalent fluid pressure specified in Sentence (1).

Section 9.5. Design of Areas and Spaces

9.5.1. General

9.5.1.1.  Application

(1)  Unless otherwise specifically indicated, this Section applies only to dwelling units that are intended for use on a continuing or year-round basis as the principal residence of the occupant.

9.5.1.2.  Method of Measurement

(1)  Unless otherwise indicated herein, the areas, dimensions and heights of rooms or spaces shall be measured between finished wall surfaces and between finished floor and ceiling surfaces.

9.5.1.3.  Floor Areas

(1)  Minimum floor areas specified in this Section do not include closets or built-in bedroom cabinets unless otherwise indicated.

9.5.1.4.  Combination Rooms

(1)  Two or more areas are considered as a combination room if the dividing wall occupies less than 60 per cent of the separating plane.

9.5.1.5.  Lesser Areas and Dimensions

(1)  Areas of rooms and spaces are permitted to be less than required in this Section provided it can be shown that the rooms and spaces are adequate for their intended use, such as by the provision of built-in furniture to compensate for reduced sizes.

9.5.2. Barrier-Free Design

9.5.2.1.  General

(1)  Except as provided in Sentence (2) and Article 3.8.1.1., every building shall be designed in conformance with Section 3.8.

(2)  The requirements of Section 3.8 need not be provided for houses including semi-detached houses, duplexes, triplexes, town houses, row houses and boarding, or rooming houses with fewer than 8 boarders or roomers.

9.5.2.2.  Protection on Floor Areas with a Barrier-Free Path of Travel

(1)  Where a barrier-free path of travel required in Article 9.5.2.1. is provided to any storey above the first storey, the requirements in Article 3.3.1.7. shall apply.

9.5.2.3.  Reserved

9.5.3. Ceiling Heights

9.5.3.1.  Heights of Rooms or Spaces

(1)  Heights of rooms or spaces in residential occupancies and live/work units shall conform to Table 9.5.3.1.

Table 9.5.3.1.

Room Heights

Forming Part of Sentence 9.5.3.1.(1)

| Room or Space | Minimum Heights |
| --- | --- |
| Living room or space, dining room or space, kitchen or kitchen space | 2 300 mm over at least 75 per cent of the required floor area with a clear height of 2 100 mm at any point over the required area |
| Bedroom or bedroom space | 2 300 mm over at least 50 per cent of the required area or 2 100 mm over all of the required floor area. Any part of the floor having a clear height of less than 1 400 mm shall not be considered in computing the required floor area |
| Basement space | 2 100 mm over at least 75 per cent of the basement area except that under beams and ducts the clearance is permitted to be reduced to 1 950 mm |
| Bathroom, water-closet room or laundry area above grade | 2 100 mm in any area where a person would normally be in a standing position |
| Passage, hall or main entrance vestibule and finished rooms not specifically mentioned above | 2 100 mm |
| Column 1 | 2 |

9.5.3.2.  Mezzanines

(1)  The clear height above and below a mezzanine floor assembly in all occupancies shall be not less than 2 100 mm.

9.5.3.3.  Storage Garages

(1)  The clear height in a storage garage shall be not less than 2 000 mm.

9.5.4. Living Rooms or Spaces Within Dwelling Units

9.5.4.1.  Areas of Living Rooms and Spaces

(1)  Living areas within dwelling units, either as separate rooms or in combination with other spaces, shall have an area not less than 13.5 m2.

(2)  Where the area of a living space is combined with a kitchen and dining area, the living area alone in a dwelling unit that contains sleeping accommodation for not more than 2 persons shall be not less than 11 m2.

9.5.5. Dining Rooms or Spaces Within Dwelling Units

9.5.5.1.  Area of Dining Rooms or Spaces

(1)  A dining space in combination with other space shall have an area of not less than 3.25 m2.

(2)  Dining rooms not combined with other space shall have a minimum area of 7 m2.

9.5.6. Kitchens Within Dwelling Units

9.5.6.1.  Kitchen Areas

(1)  Kitchen areas within dwelling units either separate from or in combination with other spaces, shall have an area of not less than 4.2 m2 including the area occupied by the base cabinets, except that in dwelling units containing sleeping accommodation for not more than 2 persons, the minimum area shall be 3.7 m2.

9.5.7. Bedrooms or Spaces in Dwelling Units and Dormitories

9.5.7.1.  Areas of Bedrooms

(1)  Except as provided in Articles 9.5.7.2. and 9.5.7.3., bedrooms in dwelling units shall have an area not less than 7 m2 where built-in cabinets are not provided and not less than 6 m2 where built-in cabinets are provided.

9.5.7.2.  Areas of Master Bedrooms

(1)  Except as provided in Article 9.5.7.3., not less than one bedroom in every dwelling unit shall have an area of not less than 9.8 m2 where built-in cabinets are not provided and not less than 8.8 m2 where built-in cabinets are provided.

9.5.7.3.  Areas of Combination Bedrooms

(1)  Bedroom spaces in combination with other spaces in dwelling units shall have an area not less than 4.2 m2.

9.5.7.4.  Areas of Other Sleeping Rooms

(1)  Sleeping rooms other than in dwelling units shall have an area not less than 7 m2 per person for single occupancy and 4.6 m2 per person for multiple occupancy.

9.5.7.5.  Recreational Camps

(1)  Recreational camps shall have an area in the sleeping quarters of at least 3.72 m2 per camper or, if double or triple tier bunk units are used, 2.79 m2 per camper.

9.5.7.6.  Camps for Housing Workers

(1)  A camp for housing of workers shall have a minimum area of 3.72 m2 per employee in every room used for sleeping purposes.

9.5.7A. Combined Spaces

9.5.7A.1.  Combined Living, Dining, Bedroom and Kitchen Spaces

(1)  Despite Subsections 9.5.4, 9.5.5, 9.5.6 and 9.5.7, where living, dining, bedroom and kitchen spaces are combined in a dwelling unit that contains sleeping accommodation for not more than 2 persons, the area of the combined spaces shall be not less than 13.5 m2.

9.5.8. Bathrooms and Water-Closet Rooms

9.5.8.1.  Space to Accommodate Fixtures

(1)  In every dwelling unit an enclosed space of sufficient size shall be provided to accommodate a water closet, lavatory and bathtub or shower stall.

9.5.9. Hallways

9.5.9.1.  Width of Hallway Within Dwelling Unit

(1)  The unobstructed width of a hallway within a dwelling unit shall be at least 860 mm, except that the hallway width is permitted to be 710 mm where

(a)	there are only bedrooms and bathrooms at the end of the hallway furthest from the living area, and

(b)	a second exit is provided

(i)	in the hallway near the end furthest from the living area, or

(ii)	in each bedroom served by the hallway.

Section 9.6. Doors

9.6.1. General

9.6.1.1.  Application

(1)  This Section applies to doors, to glazed areas in doors and to sidelights for doors.

9.6.2. Required Doors

9.6.2.1.  Doors for Dwelling Units

(1)  A door shall be provided at each entrance to a dwelling unit and to each room containing a water closet within a dwelling unit.

9.6.3. Doorway Sizes

9.6.3.1.  Doorway Opening Sizes

(1)  Except as provided in Articles 9.6.3.3. and 9.9.6.4., doorway openings within dwelling units shall be designed to accommodate at least the door sizes in Table 9.6.3.1. for swing-type doors or folding doors.

Table 9.6.3.1.

Minimum Size of Door

Forming Part of Sentence 9.6.3.1.(1)

| At Entrance to: | Minimum Width, mm | Minimum Height, mm |
| --- | --- | --- |
| Dwelling unit (required entrance) |  |  |
| Vestibule or entrance hall | 810 | 1 980 |
| Stairs to a floor level that contains a finished space |  |  |
| All doors in not less than one line of passage from the exterior to the basement |  |  |
| Utility rooms | 810 | 1 980 |
| Walk-in closet | 610 | 1 980 |
| Bathroom, water-closet room, shower room(1) | 610 | 1 980 |
| Rooms located off hallways that are permitted to be 710 mm wide | 610 | 1 980 |
| Rooms not mentioned above, exterior balconies | 760 | 1 980 |
| Column 1 | 2 | 3 |

Note to Table 9.6.3.1.:

(1)	 See Article 9.6.3.3.

9.6.3.2.  Doors to Public Water-Closet Rooms

(1)  Doors to public water-closet rooms shall be not less than 810 mm wide and 2 030 mm high.

9.6.3.3.  Doors to Bathrooms

(1)  Where a barrier-free path of travel conforming to Section 3.8. is provided into a suite of residential occupancy and where a bathroom within the suite is at the level of the suite entrance door, the doorway to such bathroom and to each bedroom at the same level as such bathroom shall have, when the door is in the open position, a clear width of not less than

(a)	760 mm where the door is served by a corridor or space not less than 1 060 mm wide, and

(b)	810 mm where the door is served by a corridor or space less than 1 060 mm wide.

9.6.4. Door Sill Height

9.6.4.1.  Height of Door Sills Above Floors or Ground

(1)  Doors in buildings of residential occupancy shall conform to Sentence (2) where

(a)	the top surface of the sill of a door, including sliding doors, is located less than 200 mm above the finished floor on one side of the door, and

(b)	the finished floor referred to in Clause (a) is more than 600 mm above the floor, landing, stair tread or ground level on the other side of the door.

(2)  Doors described in Sentence (1) shall be

(a)	permanently adjusted to prevent an opening greater than

(i)	200 mm where the height described in Clause (1)(b) is not more than 1 800 mm, and

(ii)	100 mm where the height described in Clause (1)(b) is greater than 1 800 mm, or

(b)	be protected by a guard in accordance with Section 9.8.

9.6.5. Exterior Doors

9.6.5.1.  Exterior Wood Doors

(1)  Exterior wood doors shall conform to CAN/CSA-O132.2-M, “Wood Flush Doors”.

(2)  Each door described in Sentence (1) shall indicate legibly

(a)	the name of the manufacturer,

(b)	the standard to which it is produced, and

(c)	that it is of an exterior type.

9.6.5.2.  Sliding Doors

(1)  Sliding doors shall conform to CAN/CGSB 82.1-M, “Sliding Doors”.

9.6.5.3.  Insulated Steel Doors

(1)  Insulated steel doors shall conform to CAN/CGSB-82.5-M, “Insulated Steel Doors”.

9.6.5.4.  Air Infiltration for Exterior Swing Type Doors

(1)  Except where a door is weather-stripped on all edges, and protected with a storm door, or by an enclosed unheated space, an exterior swing type door assemblies shall have a rate of air infiltration not exceeding 11.6 10-4 m3/s for each metre of crack length when tested at a pressure differential of 75 Pa in conformance with ASTM E283, “Standard Method of Test for Rate of Air Leakage Through Exterior Windows, Curtain Walls and Doors”.

9.6.5.5.  Air Infiltration for Patio Type Sliding Doors

(1)  A patio type sliding glass door shall have a rate of air infiltration not exceeding 38 10-4 m3/s for each square metre of door area when tested in conformance with ASTM E283.

9.6.5.6.  Weather Stripping

(1)  In buildings of residential occupancy weather stripping shall be provided around all exterior doors except garage doors.

9.6.6. Glass

9.6.6.1.  Maximum Area of Glass

(1)  The maximum area of individual panes of glass for doors shall conform to Table 9.6.6.1.

Table 9.6.6.1.

Maximum Glass Area for Doors

Forming Part of Sentence 9.6.6.1.(1)

| Glass Thickness, mm | Maximum Glass Area, m2 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Type of Glass |  |  |  |  |  |
|  | Annealed | Annealed Multiple-Glazed Factory-Sealed Units | Laminated | Wired | Heat Strengthened | Fully Tempered |
| 3 | 0.50 | 0.70 | (2) | (2) | 1.00 | 1.00 |
| 4 | 1.00 | 1.50 | (2) | (2) | 1.50 | 4.00 |
| 5 | 1.50 | 1.50 | (2) | (2) | 1.50 | No limit |
| 6 | 1.50 | 1.50 | 1.20 | 1.00 | 1.50 | No limit |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 |

Note to Table 9.6.6.1.

(2)	 Not generally available.

9.6.6.2.  Glass in Doors and Sidelights

(1)  Glass in doors and sidelights for doors shall conform to Sentence 9.7.3.1.(1).

(2)  Glass in sidelights greater than 500 mm wide that could be mistaken for doors, glass in storm doors and glass in sliding doors within or at every entrance to a dwelling unit and in public areas shall be

(a)	safety glass of the tempered or laminated type conforming to CAN/CGSB-12.1-M, “Tempered or Laminated Safety Glass”, or

(b)	wired glass conforming to CAN/CGSB-12.11-M, “Wired Safety Glass”.

(3)  Except as provided in Article 9.7.5.2., glass in entrance doors to dwelling units and in public areas other than the entrance door described in Sentence (2), shall be safety glass or wired glass of the type described in Sentence (2) where the glass area exceeds 0.5 m2 and extends to less than 900 mm from the bottom of the door.

9.6.6.3.  Mirrored Glass Doors

(1)  Mirrored glass doors are permitted to be used only at the entrance to clothes closets and shall conform to the requirements of CAN/CGSB-82.6-M, “Doors, Mirrored Glass, Sliding or Folding Wardrobe”.

(2)  Mirrored glass doors reinforced with a film backing shall meet the impact resistance requirements specified in CAN2-12.5-M, “Mirrors, Silvered”.

9.6.6.4.  Visibility of Glass or Transparent Doors

(1)  Except as provided in Article 9.7.5.3., every glass or transparent door accessible to the public shall be equipped with hardware, bars or other permanent fixtures designed so that the existence and position of such door will be readily apparent.

9.6.6.5.  Glass for Shower or Bathtub Enclosures

(1)  Glass other than safety glass shall not be used for a shower or bathtub enclosure.

9.6.7. Thermal Breaks

9.6.7.1.  Application

(1)  This Subsection applies to doors and sidelights separating heated space from unheated space or the exterior.

9.6.7.2.  Required Thermal Breaks

(1)  Except as provided in Sentence (2), metal frames for doors, for glazing in doors, and for sidelights for doors shall incorporate a thermal break.

(2)  Thermal breaks need not be installed in accordance with Sentence (1) where the doors are

(a)	garage doors,

(b)	storm doors, or

(c)	doors that are required to have a fire-resistance rating.

9.6.8. Resistance to Forced Entry

9.6.8.1.  Application

(1)  Except as permitted in Sentence (2), this Subsection applies to

(a)	swinging entrance doors to dwelling units,

(b)	swinging doors between dwelling units and attached garages or other ancillary spaces, and

(c)	swinging doors which provide access directly or indirectly from a storage garage to a dwelling unit.

(2)  Sentence (1) does not apply to exterior doors to garages and to other ancillary spaces.

9.6.8.2.  Wood Doors

(1)  Except as permitted in Article 9.6.8.10., wood doors as described in Sentence 9.6.8.1.(1) shall

(a)	be solid core or stile and rail type,

(b)	be not less than 45 mm thick, and

(c)	if of the stile and rail panel type, have a panel thickness of not less than 19 mm, with a total panel area not more than half of the door area.

9.6.8.3.  Deadbolt Lock

(1)  Except as permitted in Article 9.6.8.10., doors described in Sentence 9.6.8.1.(1) shall be provided with a deadbolt lock with a cylinder having no fewer than 5 pins and a bolt throw not less than 25 mm, protected with a solid or hardened free-turning ring or bevelled cylinder housing.

9.6.8.4.  Double Doors

(1)  Except as permitted in Article 9.6.8.10., an inactive leaf in double doors used in locations specified in Sentence 9.6.8.1.(1) shall be provided with heavy duty bolts top and bottom having an engagement of not less than 15 mm.

9.6.8.5.  Fastening of Hinges

(1)  Except as permitted in Article 9.6.8.10., hinges for doors in Sentence 9.6.8.1.(1) shall be fastened to wood doors with wood screws not less than 25 mm long and to wood frames with wood screws such that at least two screws per hinge penetrate not less than 30 mm into solid wood.

(2)  Except as permitted in Article 9.6.8.10., hinges for doors in Sentence 9.6.8.1.(1) shall be fastened to metal doors and metal frames with machine screws not smaller than No. 8 and not less than 10 mm long.

9.6.8.6.  Fastening of Strikeplates

(1)  Except as permitted in Article 9.6.8.10., strikeplates for deadbolts described in Article 9.6.8.3. shall be fastened to wood frames with wood screws that penetrate not less than 30 mm into solid wood.

(2)  Except as permitted in Article 9.6.8.10., strikeplates for deadbolts in Article 9.6.8.3. shall be fastened to metal frames with machine screws not smaller than No. 8 and not less than 10 mm long.

9.6.8.7.  Outward Swinging Doors

(1)  Except for storm doors or screen doors, doors described in Sentence 9.6.8.1.(1) which swing outward shall be provided with hinges or pins so that the doors cannot be removed when they are in the closed position.

9.6.8.8.  Door Viewer

(1)  Main entrance doors to dwelling units shall be provided with

(a)	a door viewer or transparent glazing in the door, or

(b)	a sidelight.

9.6.8.9.  Solid Blocking

(1)  Solid blocking shall be provided on both sides at the lock height between the jambs for doors described in Sentence 9.6.8.1.(1) and the structural framing so that the jambs will resist spreading by force.

9.6.8.10.  Alternate Test Procedure

(1)  Doors, frames and hardware which conform to a security level of at least Grade 10 as described in the Annex to ASTM F476, “Standard Test Methods for Security of Swinging Door Assemblies”, are not required to conform to Articles 9.6.8.2. to 9.6.8.6.

Section 9.7. Windows and Skylights

9.7.1. General

9.7.1.1.  Application

(1)  Windows shall conform to the requirements of this Section.

9.7.1.2.  Minimum Window Areas

(1)  Except as required in Article 9.7.1.3. and Sentence (3), the minimum window glass area for rooms in buildings of residential occupancy or which are used for sleeping shall conform to Table 9.7.1.2.

Table 9.7.1.2.

Glass Areas for Rooms of Residential Occupancy

Forming Part of Sentence 9.7.1.2.(1)

| Location | Minimum Unobstructed Glass Area |  |
| --- | --- | --- |
|  | With No Electric Lighting | With Electric Lighting |
| Laundry, basement recreation room, unfinished basement | 4% of area served | Windows not required |
| Water-closet room | 0.37 m2 | Windows not required |
| Kitchen, kitchen space, kitchen alcove | 10% of area served | Windows not required |
| Living rooms and dining rooms | 10% of area served | 10% of area served |
| Bedrooms and other finished rooms not mentioned above | 5% of area served(1) | 5% of area served(1) |
| Column 1 | 2 | 3 |

Note to Table 9.7.1.2.:

(1)	 See Article 9.7.1.3.

(2)  The unobstructed glass area of a door or skylight is considered equivalent to that of a window.

(3)  Work areas in live/work units shall conform to Clause 3.7.2.1.(2)(a).

9.7.1.3.  Bedroom Windows

(1)  Except where a door on the same floor level as the bedroom provides direct access to the exterior, every floor level containing a bedroom in a suite shall be provided with

(a)	at least 1 outside window that can be opened from the inside without the use of tools, and

(b)	each such window shall provide an individual, unobstructed open portion having a minimum area of 0.35 m2 with no dimension less than 380 mm.

(2)  Except for basement areas, the window described in Sentence (1) shall have a maximum sill height of 1 000 mm above the floor.

(3)  When sliding windows are used, the minimum dimension described in Sentence (1) shall apply to the openable portion of the window.

(4)  Where the sleeping area within a live/work unit is on a mezzanine with no obstructions more than 1 070 mm above the floor, the window required in Sentence (1) may be provided on the main level of the live/work unit provided the mezzanine is not more than 25% of the area of the live/work unit or 20 m2 whichever is less and an unobstructed direct path of travel is provided from the mezzanine to this window.

9.7.1.4.  Window Opening into a Window-Well

(1)  Where a window required in Article 9.7.1.3. opens into a window-well, a clearance of not less than 550 mm shall be provided in front of the window.

(2)  Where the sash of a window referred to in Sentence (1) swings towards the window-well, the operation of the sash shall not reduce the clearance in a manner that would restrict escape in an emergency.

9.7.1.5.  Termites

(1)  In localities where termites are known to occur and where windows or other openings at or below grade contain wood elements, the bottom of window wells or adjacent ground shall be at least 150 mm below the nearest wood unless the wood is pressure treated with a chemical toxic to termites in accordance with Article 9.3.2.9.

9.7.1.6.  Height of Window Sills above Floors or Ground

(1)  Except as provided in Sentence (2), openable windows in buildings of residential occupancy shall be protected by

(a)	a guard in accordance with Section 9.8., or

(b)	a mechanism capable of controlling the free swinging or sliding of the openable part of the window so as to limit any clear unobstructed opening to not more than 100 mm measured either vertically or horizontally where the other dimension is greater than 380 mm.

(2)  Windows need not be protected in accordance with Sentence (1) where

(a)	the window serves a dwelling unit that is not located above another suite,

(b)	the only opening greater than 100 mm by 380 mm is a horizontal opening at the top of the window,

(c)	the top surface of the window sill is located more than 480 mm above the finished floor on one side of the window, or

(d)	the window is located in a room or space with the finished floor described in Clause (c) located less than 1 800 mm above the floor or ground on the other side of the window.

9.7.1.7.  Air Infiltration of Exterior Windows

(1)  Air infiltration of exterior windows shall not exceed .775 dm3/s for each metre of sash crack when tested at a pressure differential of 75 Pa in conformance with ASTM E283, “Standard Method of Test Rate of Air Leakage through Exterior Windows, Curtain Walls and Doors”.

9.7.2. Window Standards

9.7.2.1.  Window Standard

(1)  Windows shall conform with CAN/CSA-A440-M, “Windows”, but need not meet air tightness, water tightness and wind load resistance requirements more stringent than those for classifications A1, B1 and C1 in CAN/CSA-A440-M.

9.7.3. Glass

9.7.3.1.  Glass Standards

(1)  Glass shall conform to

(a)	CAN/CGSB-12.1-M, “Tempered or Laminated Safety Glass”,

(b)	CAN/CGSB-12.2-M, “Flat, Clear Sheet Glass”,

(c)	CAN/CGSB-12.3-M, “Flat, Clear Float Glass”,

(d)	CAN/CGSB-12.4-M, “Heat-Absorbing Glass”,

(e)	CAN/CGSB-12.8-M, “Insulating Glass Units”,

(f)	CAN/CGSB-12.10, “Glass, Light and Heat/Reflecting”, or

(g)	CAN/CGSB-12.11-M, “Wired Safety Glass”.

9.7.3.2.  Structural Design of Glass

(1)  Glass in windows, sloped glazing and skylights shall be designed in conformance with CAN/CGSB-12.20-M, “Structural Design of Glass for Buildings”.

9.7.4. Caulking and Glazing

9.7.4.1.  Sealing Compound

(1)  The sealing compound used to seal the glass component of a factory-sealed double-glazed unit to the sash component shall be compatible with the material used to edge seal the glass component.

9.7.4.2.  Caulking Compound

(1)  Caulking shall be provided between window frames or trim and the exterior siding or masonry in conformance with Subsection 9.27.4.

9.7.5. Protection of Windows in Public Areas

9.7.5.1.  Transparent Panels

(1)  Except as provided in Article 9.7.5.2., transparent panels that could be mistaken as a means of egress shall be protected by barriers or railings.

9.7.5.2.  Sliding Glass Partitions

(1)  Sliding glass partitions which separate a public corridor from an adjacent occupancy and which are open during working hours need not conform to Article 9.7.5.1. and Sentence 9.6.6.2.(3), except that such partitions shall be suitably marked to indicate their existence and position.

9.7.5.3.  Windows in Exit Stairways

(1)  Windows in exit stairways that extend to less than 1 070 mm above the landing shall be

(a)	protected by guards, in accordance with Section 9.8, or

(b)	non-operable and designed to withstand the specified loads for balcony guards as provided in Part 4.

9.7.5.4.  Windows above the Second Storey

(1)  Windows in public areas that extend to less than 1 000 mm from the floor and are located above the second storey in buildings of residential occupancy shall be

(a)	protected by guards in accordance with Section 9.8., or

(b)	non-openable and designed to withstand the lateral design loads for balcony guards in Part 4.

9.7.6. Resistance to Forced Entry

9.7.6.1.  Forced Entry Through Windows

(1)  In dwelling units, windows, any part of which is located within 2 000 mm of adjacent ground level, shall conform to the requirements for resistance to forced entry as described in Clause 10.13 of CAN/CSA-A440-M, “Windows”.

9.7.7. Skylights

9.7.7.1.  Plastic Skylights

(1)  Plastic skylights shall conform to CAN/CGSB- 63.14-M, “Plastic Skylights”.

9.7.7.2.  Glass Skylights

(1)  Factory-built glass skylights shall meet the performance requirements of CAN/CGSB-63.14-M, “Plastic Skylights”.

Section 9.8. Stairs, Ramps, Handrails and Guards

9.8.1. Scope

9.8.1.1.  Application

(1)  This Section applies to the design and construction of interior and exterior stairs, steps, ramps, railings and guards.

9.8.1.2.  Exit Stairs

(1)  Where the stair forms part of an exit, the appropriate requirements in Sections 9.9. and 9.10. shall also apply.

9.8.1.3.  Escalators and Moving Walkways

(1)  Escalators and moving walkways shall conform to the appropriate requirements in Part 3.

9.8.2. General

9.8.2.1.  Uniform Treads and Risers

(1)  Treads and risers shall have uniform rise and run in any one flight.

(2)  A stairway that is not an exit is permitted to contain both a curved and straight portions of stairs in a single flight provided each curved portion conforms to Article 9.8.5.2. and the riser height is uniform throughout the flight.

9.8.2.2.  Minimum Number of Risers

(1)  Except for interior stairs within a dwelling unit, at least 3 risers shall be provided for interior stairs.

9.8.2.3.  Interior Stairs Extending Through the Roof

(1)  Interior stairways extending through the roof of a building shall be protected from ice and snow.

9.8.3. Stair Dimensions

9.8.3.1.  Rise, Run and Tread Depth of Stairs

(1)  Except as provided in Subsection 9.8.5., the rise, run and tread depth of stairs shall conform to Table 9.8.3.1.

Table 9.8.3.1.

Rise, Run and Tread Depth of Stairs

Forming Part of Sentence 9.8.3.1.(1)

| Stair Type | Rise, mm |  | Run, mm |  | Tread Depth, mm |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | max. | min. | max. | min. | max. | min. |
| Service and mezzanines in live/work units(1) | no limit | 125 | 355 | no limit | 355 | no limit |
| Private(2) | 200 | 125 | 355 | 210 | 355 | 235 |
| Public(3) | 200 | 125 | 355 | 230 | 355 | 250 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 |

Notes to Table 9.8.3.1.:

(1)	 Service stairs serve areas used only as service rooms or service spaces and stairs that serve mezzanines not exceeding 20 m2 within live/work units.

(2)	 Private stairs are interior stairs within dwelling units and exterior stairs serving a single dwelling unit.

(3)	 Public stairs are all stairs not described as service stair or private stairs.

9.8.3.2.  Nosings

(1)  Curved or bevelled leading edges of treads

(a)	shall not reduce the required tread depth by more than 15 mm, and

(b)	shall not, in any case, exceed 25 mm horizontally.

9.8.3.3.  Stair Width

(1)  Exit stairs and stairs used by the public shall have a width, measured between wall faces or guards, of not less than 900 mm.

(2)  At least 1 stairway between each floor level in a dwelling unit shall have a width between wall faces of not less than 860 mm.

9.8.3.4.  Headroom

(1)  The headroom measured vertically from a line drawn through the outer edges of the nosings shall be at least 1 950 mm for stairs located in dwelling units and 2 050 mm for all other stairs.

9.8.4. Landings

9.8.4.1.  Dimensions of Landings

(1)  Landings shall be at least as wide and as long as the width of stairs in which they occur, except that

(a)	the length of landing for exterior stairs serving not more than 1 dwelling unit need not exceed 900 mm, and

(b)	the length of landing for all other stairs in a straight run need not exceed 1 100 mm.

9.8.4.2.  Required Landings

(1)  Where a door swings towards a stair, the full arc of its swing shall be over a landing.

(2)  Except as provided in Sentence (3), a landing shall be provided at the top and bottom of each flight of interior stairs and where a doorway occurs in a stairway.

(3)  Where a door at the top of a stair in a dwelling unit swings away from the stair, no landing is required between the doorway and the stairs.

(4)  A landing shall be provided at the top of all exterior stairs, except that a landing is permitted to be omitted at a secondary entrance to a building containing a single dwelling unit provided the stair does not contain more than 3 risers.

9.8.4.3.  Height between Landings

(1)  The vertical height between any landings shall not exceed 3.7 m.

9.8.4.4.  Height over Landings

(1)  The clear height over landings shall be not less than 1 950 mm in dwelling units and 2 050 mm for other landings.

9.8.5. Curved Stairs and Winders

9.8.5.1.  Curved Stairs in Exits

(1)  Curved stairs used in exits shall conform to the requirements of Article 3.4.6.8.

9.8.5.2.  Curved Stairs not in Exits

(1)  Except as permitted in Article 9.8.5.3., a curved stair not required as an exit shall have an average run of not less than 200 mm and a minimum run of 150 mm and shall have risers conforming to Article 9.8.3.1.

9.8.5.3.  Winders

(1)  Stairs within dwelling units are permitted to contain winders that converge to a centre point provided

(a)	the winders turn through an angle of not more than 90°,

(b)	individual treads turn through an angle of not less than 30° or not more than 45°, and

(c)	adjacent winders turn through the same angle.

(2)  Where more than one set of winders described in Sentence (1) is provided in a single stairway between adjacent floor levels, such winders shall be separated in plan by at least 1 200 mm.

9.8.6. Pedestrian Ramps

9.8.6.1.  Ramps in a Barrier-Free Path of Travel

(1)  Ramps in a barrier-free path of travel shall conform to the requirements in Section 3.8.

9.8.6.2.  Maximum Slope

(1)  Except as provided in Article 9.8.6.1., the slope of interior pedestrian ramps shall be not more than

(a)	1 in 10 for residential occupancies,

(b)	1 in 6 for mercantile or industrial occupancies, and

(c)	1 in 8 for all other occupancies.

(2)  Except as provided in Article 9.8.6.1., the slope of every exterior ramp shall be not more than 1 in 10.

9.8.6.3.  Level Areas on Ramps

(1)  Except as provided in Article 9.8.6.1., where a doorway or stairway opens onto the side of a ramp, there shall be a level area extending across the full width of the ramp and for a distance of not less than 300 mm on either side of the wall opening.

(2)  Except as provided in Article 9.8.6.1., where a doorway or stairway opens onto the end of a ramp, there shall be a level area extending across the full width of the ramp and along it for not less than 900 mm.

9.8.7. Handrails

9.8.7.1.  Required Handrails

(1)  Except as permitted in Sentences (2) and (3), a handrail shall be provided on

(a)	at least one side of stairs less than 1 100 mm in width,

(b)	two sides of stairs 1 100 mm in width or greater, and

(c)	two sides of a curved stair used as an exit.

(2)  Handrails are not required for stairs within dwelling units having not more than 2 risers, or for exterior stairs having not more than 3 risers and serving not more than one dwelling unit.

(3)  Only one handrail is required on exterior stairs having more than 3 risers provided such stairs serve not more than one dwelling unit.

9.8.7.2.  Continuous Handrail

(1)  Except as provided in Sentence (2), at least one handrail shall be continuous throughout the length of the stairway, including landings, except where interrupted by

(a)	doorways, or

(b)	newel posts at changes in direction.

(2)  For stairs serving only 1 dwelling unit, at least one handrail shall be continuous throughout the length of the stairway except where interrupted

(a)	by doorways,

(b)	by newel posts,

(c)	at landings, or

(d)	at changes in direction.

9.8.7.3.  Termination of Handrails

(1)  Handrails shall be terminated in a manner that will not obstruct pedestrian travel or create a hazard.

(2)  Except for stairways serving only 1 dwelling unit, at least one handrail at the sides of a stairway or ramp shall extend horizontally not less than 300 mm beyond the top and bottom of the stairway or ramp.

9.8.7.4.  Height of Handrails

(1)  Height of handrails on stairs and ramps shall be measured vertically from a line drawn

(a)	through the outside edges of the stair nosing, or

(b)	from the surface of the ramp, floor or landing below the handrail.

(2)  Except as provided in Sentences (3) and (4), the height of handrails on stairs and ramps shall be

(a)	not less than 800 mm, and

(b)	not more than 965 mm.

(3)  Where guards are required, handrails on landings are permitted to be not more than 1 070 mm in height.

(4)  Handrails not meeting the requirements of Sentences (2) and (3) are permitted provided they are installed in addition to the required handrails.

9.8.7.5  Ergonomic Design

(1)  A clearance of not less than 40 mm shall be provided between each handrail and the wall to which it is fastened.

(2)  Required handrails shall be constructed so as to be continually graspable along their entire length with no obstruction on or above them to break a handhold, except where the handrail is interrupted by newels at changes in direction.

9.8.7.6.  Projections into Stairway

(1)  Handrails and constructions below handrails, including handrail supports and stair stringers shall not project more than 100 mm into the required width of a stairway.

9.8.7.7.  Handrails for Ramps

(1)  Where ramps are used in lieu of stairs, the handrail requirements for stairs in Articles 9.8.7.1. to 9.8.7.8. shall apply where the gradient exceeds 1 in 10.

9.8.7.8.  Attachment of Handrails

(1)  Handrails shall be attached to wood studs, wood blocking, steel studs or masonry at points spaced not more than 1 200 mm apart.

(2)  Attachment to wood studs and wood blocking required in Sentence (1) shall consist of not less than 2 wood screws at each point, penetrating not less than 32 mm into solid wood.

9.8.8. Guards

9.8.8.1.  Required Guards

(1)  Except for the edges of floor pits in repair garages and loading docks, every surface to which access is provided for other than maintenance purposes, including but not limited to exterior landings, porches, decks, balconies, mezzanines, galleries, raised walkways and roofs, shall be protected by a guard on each side which is not protected by a wall and where there is a difference in elevation to adjacent surfaces of more than 600 mm.

(2)  Every exterior stair with more than 6 risers and every ramp shall be protected with guards on all open sides where the difference in elevation between the adjacent ground level and the stair or ramp exceeds 600 mm.

(3)  When an interior stair has more than 2 risers, the sides of the stair and the landing or floor level around the stair well shall be enclosed by walls, or be protected by guards, except that a stair to an unfinished basement in a dwelling unit is permitted to have 1 unprotected side.

9.8.8.2.  Height of Guards

(1)  Except as provided in Sentences (2) to (4), all guards, including those for balconies, shall be at least 1 070 mm high.

(2)  Guards for porches, decks, landings and balconies are permitted to be a minimum of 900 mm high where

(a)	the walking surface of the porch, deck, landing or balcony served by the guard is not more than 1 800 mm above the finished ground level, and

(b)	the porch, deck, landing or balcony serves not more than one dwelling unit.

(3)  Except as provided in Sentence (4), guards for stairs shall be not less than 900 mm high measured vertically from a line drawn through the outside edges of the stair nosings, and 1 070 mm high at landings.

(4)  Guards for stairs within dwelling units and stairs serving not more than one dwelling unit shall be not less than 800 mm measured vertically above a line drawn through the outside edges of stair nosings, and not less than 900 mm above landings.

(5)  All required guards within dwelling units other than those described in Sentence (4) shall be not less than 900 mm high.

9.8.8.3.  Guards for Floors and Ramps in Garages

(1)  Except for floors of garages referred to in Section 9.35., a continuous curb not less than 150 mm in height and a guard not less than 1 070 mm above the floor level shall be provided at every opening through a garage floor and around the perimeter of such floor and ramps where the exterior walls are omitted and where the top of the floor is 600 mm or more above an adjacent ground or floor level.

9.8.8.4.  Openings in Guards

(1)  Except as provided in Sentence (2), openings through any guard which is required by Article 9.8.8.1. shall be of a size which will prevent the passage of a spherical object having a diameter of more than 100 mm unless it can be shown that the location and size of openings which exceed this limit do not represent a hazard.

(2)  Openings through any guard which is required by Article 9.8.8.1. and which is installed in a building of industrial occupancy shall be of a size which will prevent the passage of a spherical object having a diameter of more than 200 mm unless it can be shown that the location and size of such openings which exceed this limit do not represent a hazard.

(3)  Openings through any guard which is not required by Article 9.8.8.1. and which serves a building of other than industrial occupancy, shall be of a size which

(a)	will prevent the passage of a spherical object having a diameter of more than 100 mm, or

(b)	will permit the passage of a spherical object having a diameter of more than 200 mm unless it can be shown that the location and size of openings which exceed these limits do not represent a hazard.

9.8.8.5.  Design to Prevent Climbing

(1)  Guards required by Article 9.8.8.1. and serving buildings of residential occupancy shall be designed so that no member, attachment or opening located between 100 mm and 900 mm above the floor or walking surface protected by the guard will facilitate climbing.

9.8.8.6.  Guards for Ramps

(1)  Guards for ramps including vehicular ramps shall conform to the requirements for guards for stairs in Articles 9.8.8.2. and 9.8.8.4.

9.8.8.7.  Glass in Guards

(1)  Glass in guards shall be

(a)	safety glass of the laminated or tempered type conforming to CAN/CGSB-12.1-M, “Tempered or Laminated Safety Glass”, or

(b)	wired glass conforming to CAN/CGSB-12.11-M, “Wired Safety Glass”.

9.8.8.8.  Construction of Guards

(1)  Except as permitted in Sentence 2, guards shall conform to the loading criteria in Article 4.1.10.1.

(2)  Guards constructed in accordance with the requirements in the Supplementary Guidelines shall be deemed to satisfy the requirements of Sentence 9.1.

9.8.9. Construction

9.8.9.1.  Exterior Concrete Stair

(1)  Exterior concrete stairs with more than 2 risers and 2 treads shall be

(a)	supported on unit masonry or concrete walls or piers not less than 150 mm in cross section, or

(b)	cantilevered from the main foundation wall.

(2)  Stairs described in Sentence (1), when cantilevered from the foundation wall, shall be constructed and installed in conformance with Subsection 9.8.10.

(3)  The depth below ground level for foundations for exterior steps shall conform to the requirements in Section 9.12.

9.8.9.2.  Exterior Wood Steps

(1)  Exterior wood steps shall not be in direct contact with the ground unless suitably treated with a wood preservative.

9.8.9.3.  Wooden Stair Stringers

(1)  Wooden stair stringers shall

(a)	have a minimum effective depth of 90 mm and an over-all depth of not less than 235 mm,

(b)	be supported and secured top and bottom,

(c)	be not less than 25 mm actual thickness if supported along their length and 38 mm actual thickness if unsupported along their length, and

(d)	except as permitted in Sentence (2), be spaced not more than 900 mm o.c. for stairs serving not more than one dwelling unit, and 600 mm o.c. in other stairs.

(2)  For stairs serving not more than one dwelling unit where risers support the front portion of the tread, the space between stringers shall be not more than 1 200 mm.

9.8.9.4.  Treads

(1)  Stair treads lumber, plywood or O-2 grade OSB within dwelling units shall be not less than 25 mm actual thickness, except that if open risers are used and the distance between stringers exceeds 750 mm, the treads shall be not less than 38 mm actual thickness.

(2)  Stair treads of plywood or O-2 grade OSB shall have their face grain or direction of face orientation at right angles to the stringers.

9.8.9.5.  Finish for Treads and Landings

(1)  The finish for treads and landings of interior stairs in dwelling units, other than stairs to unfinished basements, shall consist of hardwood, vertical grain softwood, resilient flooring or other material providing equivalent performance.

(2)  Treads and landings of interior and exterior stairs and ramps, other than those within dwelling units, shall have a slip-resistant finish or be provided with slip-resistant strips which extend not more than 1 mm above the surface.

9.8.10. Cantilevered Precast Concrete Steps

9.8.10.1.  Design

(1)  Exterior concrete steps and their anchorage system that are cantilevered from a foundation wall shall be designed and installed to support the loads to which they may be subjected.

9.8.10.2.  Anchorage

(1)  Cantilevered concrete steps in Article 9.8.10.1. shall be anchored to concrete foundation walls at least 200 mm thick.

9.8.10.3.  Prevention of Damage Due to Frost

(1)  Suitable precautions shall be taken during backfilling and grading operations to ensure that subsequent freezing of the soil will not cause uplift forces on the underside of cantilevered concrete steps to the extent that the steps or the walls to which they are attached will be damaged.

Section 9.9. Means of Egress

9.9.1. Scope

9.9.1.1.  Application

(1)  Stairways, handrails and guards in a means of egress shall conform to the requirements in Section 9.8. as well as to the requirements in this Section.

9.9.1.2.  Fire Protection

(1)  Flame-spread ratings, fire-resistance ratings and fire-protection ratings shall conform to Section 9.10.

9.9.1.3.  Occupant Load

(1)  The occupant load of a floor area or part of a floor area, or of a building or part of a building not having a floor area, shall be based on

(a)	2 persons per sleeping room or sleeping area in a dwelling unit or suite, and

(b)	for occupancies other than as described in Clause (a), the number of persons

(i)	for which the area is designed, or

(ii)	determined from Table 3.1.16.1.

9.9.2. General

9.9.2.1.  Egress from Roof Area, Podiums, Terraces, Platforms and Contained Open Spaces

(1)  An access to exit shall be provided from every roof intended for occupancy and from every podium, terrace, platform or contained open space.

(2)  Where a roof is intended for an occupant load of more than 60 persons, at least 2 separate means of egress shall be provided from the roof to stairs designed in conformance with the requirements for exit stairs and located remote from each other.

(3)  Where a podium, terrace, platform or contained open space is provided, egress requirements shall conform to the appropriate requirements for rooms or suites in Article 9.9.7.3.

9.9.2.2.  Types of Exits

(1)  An exit from any floor area shall be one of the following used singly or in combination:

(a)	an exterior doorway,

(b)	an exterior passageway,

(c)	an exterior ramp,

(d)	an exterior stairway,

(e)	a fire escape (as described in Subsection 3.4.7.),

(f)	a horizontal exit,

(g)	an interior passageway,

(h)	an interior ramp, or

(i)	an interior stairway.

9.9.2.3.  Fire Escapes

(1)  Fire escapes are permitted to be used as exits on existing buildings provided they are designed and installed in conformance with Part 3.

(2)  Fire escapes shall not be installed on any new building.

9.9.2.4.  Elevators, Slide Escapes and Windows

(1)  Elevators, slide escapes or windows shall not be considered as part of a required means of egress.

(2)  Except for floor areas of mercantile occupancy, casement windows not less than 1 060 mm high, 560 mm wide, with a sill height not more than 900 mm above the inside floor, are permitted to be considered part of a required means of egress to provide access to fire escapes, when fire escapes are permitted.

9.9.2.5.  Purpose of Exits

(1)  An exit shall be designed for no purpose other than for exiting except that an exit may also serve as an access to a floor area.

9.9.2.6.  Ancillary Rooms

(1)  Ancillary rooms such as storage rooms, washrooms, toilet rooms, laundry rooms and service rooms shall not open directly into an exit.

9.9.2.7.  Horizontal Exits

(1)  Where a horizontal exit is used, it shall conform to Part 3.

9.9.2.8.  Front Edge of Stair Treads

(1)  Except for curved stairs the front edge of stair treads in exits and access to exits shall be at right angles to the direction of exit travel.

9.9.2.9.  Exterior Exit Stairs that Serve a Hotel

(1)  Treads and landings of exterior exit stairs that serve a hotel shall be designed to be free from ice and snow accumulation.

9.9.3. Dimensions of Means of Egress

9.9.3.1.  Application

(1)  This Subsection applies to every means of egress except exits that serve not more than 1 dwelling unit and access to exits within dwelling units.

9.9.3.2.  Exit Width

(1)  Except for doors and corridors, the width of every exit facility shall be not less than 900 mm.

9.9.3.3.  Width of Corridors

(1)  The width of every public corridor, corridor used by the public, and exit corridor shall be not less than 1 100 mm.

9.9.3.4.  Headroom Clearance

(1)  Except for stairways, doorways and storage garages, the minimum headroom clearance in exits and access to exits shall be 2 100 mm.

(2)  The clear height of every storey in a storage garage shall be not less than 2 000 mm.

9.9.4. Fire Protection of Exits

9.9.4.1.  Application

(1)  Except as provided in Article 9.9.4.4., this Subsection applies to the fire protection of all exits except exits serving not more than one dwelling unit.

9.9.4.2.  Fire Separation for Exits

(1)  Except as provided in Sentence (5) and Article 9.9.8.5., every exit other than an exit doorway, shall be separated from each adjacent floor area or from another exit by a fire separation having a fire-resistance rating not less than that required for the floor assembly above the floor area.

(2)  Where there is no floor assembly above, the fire-resistance rating required in Sentence (1) shall not be less than that required by Subsection 9.10.8. for the floor assembly below, but in no case shall the fire-resistance rating be less than 45 min.

(3)  A fire separation common to 2 exits shall be smoke-tight and not be pierced by doorways, duct work, piping or any other opening that may affect the continuity of the separation.

(4)  A fire separation that separates an exit from the remainder of the building shall have no openings except those for electrical wiring, noncombustible conduit and noncombustible piping that serve only the exit and for standpipes, sprinkler piping, exit doorways and wired glass and glass block permitted in Article 9.9.4.3.

(5)  The requirements in Sentence (1) do not apply to an exterior exit passageway provided the passageway has at least 50 per cent of its exterior sides open to the outdoors and is served by an exit stair at each end of the passageway.

9.9.4.3.  Wired Glass or Glass Block

(1)  This Article applies to wired glass in doors, and wired glass or glass block in sidelights, where these are installed in fire separations between exit enclosures and floor areas.

(2)  Except as provided in Sentence (3), the combined area of glazing in doors and sidelights shall not exceed 0.8 m2.

(3)  Where an exit enclosure connects with a floor area through an enclosed vestibule or corridor separated from the floor area by fire separations having not less than a 45 min fire-resistance rating, the glazed areas described in Sentence (1) need not be limited as required in Sentence (2).

9.9.4.4.  Openings Near Unenclosed Exit Stairs and Ramps

(1)  Where an unenclosed exterior exit stair or ramp provides the only means of egress from a suite, and is exposed to fire from openings in the exterior walls of another fire compartment, the openings in the exterior walls of the building shall be protected with wired glass in fixed steel frames or glass block conforming to Articles 9.10.13.5. and 9.10.13.7. when the openings in the exterior walls of the building are within 3 m horizontally and less than 10 m below or less than 5 m above the exit stair or ramp.

9.9.4.5.  Openings in Exterior Walls of Exits

(1)  Either openings in the exterior walls of an exit or openings in adjacent exterior walls of the building the exit serves shall be protected with wired glass in steel frames or glass block installed in accordance with Articles 9.10.13.5. and 9.10.13.7., where

(a)	the exit enclosure has exterior walls that intersect the exterior walls of the building at an angle of less than 135° measured on the outside of the building, and

(b)	the openings in the exterior walls of the building are within 3 m horizontally and less than 2 000 mm above the openings in the exterior walls of the exit.

9.9.4.6.  Openings Near Exit Doors

(1)  Where an exterior exit door in one fire compartment is within 3 m horizontally of openings in another fire compartment, and the exterior walls of these fire compartments intersect at an exterior angle of less than 135°, the openings shall be protected with wired glass in fixed steel frames or glass block conforming to Articles 9.10.13.5. and 9.10.13.7.

9.9.4.7.  Stairways in Group D or E Buildings

(1)  Notwithstanding the requirements of Sentences 9.9.4.2.(1), 9.9.8.2.(1) and Article 9.10.9.5., where a suite of Group D or E occupancy is located partly on the first storey and partly on the second storey or partly on the second storey and partly on the third storey, stairways serving that suite need not be constructed as exit stairs provided

(a)	the building is not greater than 3 storeys in building height,

(b)	the suite is separated from other occupancies by at least a 45 min fire separation,

(c)	the area occupied by the suite is not greater than 100 m2 per storey, other than the exit level storey,

(d)	the maximum travel distance from any point in the suite to an exterior exit is not greater than 25 m,

(e)	the floor assemblies have a fire-resistance rating of not less than 45 min or are of noncombustible construction,

(f)	the basement and first storey are separated by a fire separation having a fire-resistance rating of not less than 45 min, and

(g)	a smoke alarm is installed on each floor of the suite, including the basement, in accordance with Subsection 9.10.18.

(2)  The requirements of Article 9.10.12.1., for separation of exterior openings, do not apply to an occupancy conforming with Sentence (1).

9.9.5. Obstructions and Hazards in Means of Egress

9.9.5.1.  Application

(1)  This Subsection applies to obstructions and hazards in every means of egress except those within a dwelling unit or serving not more than 1 dwelling unit.

9.9.5.2.  Occupancies in Public Corridors

(1)  Where a public corridor or a corridor used by the public contains an occupancy, such occupancy shall not reduce the unobstructed width of the corridor to less than the required width of the corridor.

9.9.5.3.  Obstructions in Public Corridors

(1)  Except as permitted in Sentence (2), obstructions located within 1 980 mm of the floor shall not project horizontally more than 100 mm into exit passageways, corridors used by the public or public corridors in a manner that would create a hazard for visually impaired persons travelling adjacent to walls.

(2)  The horizontal projection of an obstruction in Sentence (1) is permitted to exceed 100 mm where the obstruction extends to less than 680 mm above the floor.

9.9.5.4.  Obstructions in Exits

(1)  Except as permitted in Subsection 9.9.6. and Article 9.8.7.8., no fixture, turnstile or construction shall project within the required width of an exit.

9.9.5.5.  Obstructions in Means of Egress

(1)  No obstructions such as posts or turnstiles shall be placed so as to restrict the width of a required means of egress from a floor area or part of a floor area to less than 750 mm unless an alternate unobstructed means of egress is provided adjacent to and plainly visible from the restricted egress.

(2)  Except as provided in Sentence (3), no obstructions, such as counter gates, which do not meet the requirements for exit doors, shall be placed in a required means of egress from a floor area or part of a floor area unless an alternate unobstructed means of egress is provided adjacent to and plainly visible from the restricted egress.

(3)  Obstructions, such as counter gates, which do not satisfy Sentence (2), are permitted to be placed in a required means of egress from a part of a floor area in mercantile occupancies and business and personal services occupancies, provided that the part of the floor area served by the unobstructed means of egress is not generally accessible to the public.

9.9.5.6.  Mirrors or Draperies

(1)  No mirror shall be placed in or adjacent to any exit so as to confuse the direction of exit, and no mirror or draperies shall be placed on or over exit doors.

9.9.5.7.  Fuel-Fired Appliances

(1)  Fuel-fired appliances shall not be installed in an exit or corridor serving as an access to exit.

9.9.5.8.  Service Rooms

(1)  Service rooms containing equipment subject to possible explosion, such as boilers designed to operate at a pressure in excess of 100 kPa, and certain types of refrigerating and transformer equipment, shall not be located under required exits.

9.9.5.9.  Ancillary Rooms

(1)  Ancillary rooms such as storage rooms, washrooms, toilet rooms, laundry rooms and service rooms shall not open directly into an exit.

9.9.6. Doors in a Means of Egress

9.9.6.1.  Application

(1)  This Subsection applies to all doors in a means of egress except doors within dwelling units and exterior doors serving not more than 1 dwelling unit unless otherwise stated herein.

9.9.6.2.  Obstruction by Doors

(1)  Exit doors shall not decrease the required exit width by more than 100 mm in exit corridors, and not more than 50 mm for other exit facilities.

(2)  Doors in their swing shall not reduce the width of the path of travel to less than

(a)	the required exit width in exit corridors and passageways, and

(b)	750 mm on exit stairs and landings.

9.9.6.3.  Headroom Obstructions

(1)  No door closer or other device shall be installed in an exit in such a manner as to reduce the headroom clearance to less than 1 980 mm.

9.9.6.4.  Door Sizes

(1)  Every exit door or door that opens into or is located within a public corridor or other facility that provides access to exit from a suite shall

(a)	be not less than 2 030 mm high,

(b)	be not less than 810 mm wide where there is only one door leaf, and

(c)	shall have no single leaf less than 610 mm wide in any multiple leaf door.

9.9.6.5.  Direction of Door Swing

(1)  Except as provided in Sentence 3.3.1.11.(1), every door that opens onto a corridor or other facility that provides access to exit from a room or suite having an occupant load of more than 60 persons, and every door that is located within a corridor that is required to be separated from the remainder of the floor area by a fire separation shall swing on a vertical axis in the direction of exit travel and shall not open onto a step.

(2)  Except as permitted in Sentences (4) and (5) and in Sentences 3.4.6.11.(3) and 3.4.6.13.(1), every required exit door shall open in the direction of exit travel and shall swing on its vertical axis.

(3)  Except as provided in Sentences (4) and (5), every required exit door shall open in the direction of exit travel.

(4)  An exit door serving not more than one dwelling unit is permitted to swing inward.

(5)  Exit doors serving a storage garage serving not more than one dwelling unit, or doors serving other accessory buildings where there is no danger to life safety, need not conform to Sentence (2) or (3).

9.9.6.6.  Nearness of Doors to Stairs

(1)  Except as provided in Sentence (2), the distance between a stair riser and the leading edge of a door during its swing shall be not less than 300 mm.

(2)  Where there is a danger of blockage from ice or snow, an exit door is permitted to open onto not more than 1 step provided the riser of such step does not exceed 150 mm.

9.9.6.7.  Revolving Doors

(1)  Revolving doors used as exits shall conform to Article 3.4.6.14.

9.9.6.8.  Door Opening Mechanism

(1)  Except as provided in Sentence 3.4.16.15.(4) for electromagnetic locking systems, exit doors and doors to suites, including exterior doors to dwelling units, shall be openable from the inside without requiring keys, special devices or specialized knowledge of the door opening mechanism.

9.9.6.9.  Automatic Locking Prohibited

(1)  Except for hotels and motels, a door opening onto a public corridor which provides access to exit from suites shall be designed not to lock automatically when such doors are equipped with automatic self-closing devices.

9.9.6.10.  Effort Required to Open

(1)  Every exit door shall be designed and installed so that when the latch is released the door will open in the direction of exit travel under a force of not more than 90 N applied at the knob or other latch releasing device.

9.9.6.11.  Arabic Numerals

(1)  Where an exit stair serves a hotel, Arabic numerals indicating the assigned floor number shall be

(a)	mounted permanently on each side of the exit door to the exit stair shaft,

(b)	not less than 60 mm high, raised approximately 0.7 mm above the door surface,

(c)	located 1 500 mm from the finished floor, and

(d)	contrasting in colour with the door surface on which they are applied.

9.9.7. Access to Exits

9.9.7.1.  Means of Egress from Suites

(1)  Except as permitted in Sentences 9.9.8.2.(2) and 9.9.9.3.(1), each suite in a floor area occupied by more than one suite shall have

(a)	an exterior exit doorway, or

(b)	a doorway to a public corridor or to an exterior passageway.

(2)  Except as provided in Sentence 9.9.7.2.(1), from the point where a doorway described in Clause (1)(b) enters the public corridor or exterior passageway, it shall be possible to go in opposite directions to each of 2 separate exits.

9.9.7.2.  Dead End Corridors

(1)  A dead-end public corridor is permitted in an occupancy shown in Table 9.9.7.2. where

(a)	a dead-end corridor

(i)	does not exceed the distance of travel measured from the most remote point of the dead-end to a point where it is possible to go in opposite directions to each of two separate exits, and

(ii)	is provided with doors equipped with self-closing devices, or

(b)	there is a second and separate egress doorway from each room or suite not leading into the dead-end corridor.

(2)  Dead-end public corridors in residential occupancies and business and personal services occupancies shall contain only suite door openings arranged so that not more than 2 such doors have to be passed to reach the nearest exit.  The area of wired glass in such doors shall not exceed 645 cm2.

Table 9.9.7.2.

Dead End Public Corridors

Forming Part of Sentence 9.9.7.2.(1)

| Occupancy | Maximum Length of Dead-End Public Corridor, m | Maximum Occupant Load or Suites Served by Dead-End Public Corridor |
| --- | --- | --- |
| Group C | 6 | 4 suites |
| Group D | 6 | 30 |
| Group E | 9 | 30 |
| Group F | 9 | 30 |
| Column 1 | 2 | 3 |

9.9.7.3.  Number and Spacing of Egress Doors

(1)  Except for dwelling units, at least 2 egress doors shall be provided where

(a)	the area of a room or suite exceeds 200 m2 in a Group D, E, F2 and F3 occupancy, or 150 m2 in a Group C occupancy, or

(b)	the distance measured from any point within a room or suite to the nearest egress door exceeds 25 m.

(2)  Doors in Sentence (1) shall be spaced so that in the event one door is made inaccessible by a fire within such a room or suite, the other door will provide safe egress.

9.9.7.4.  Independent Access to Exit

(1)  Required access to exit from suites shall not be through any other dwelling unit, service room or other occupancy.

9.9.7.5.  Travel Distance within Rooms and Suites

(1)  Except for dwelling units, the travel distance from any point within the room or suite to the nearest egress door shall not exceed the maximum travel distance in Article 9.9.8.2.

9.9.8. Exits From Floor Areas

9.9.8.1.  Measurement of Travel Distance

(1)  Except as provided in Sentences (2) and (3), for the purposes of this Subsection, travel distance means the distance from any point in the floor area to an exit measured along the path of exit travel.

(2)  Where a room or suite is separated from the remainder of the floor area by a fire separation having a fire-resistance rating of at least 45 min, or in a sprinklered building, by a fire separation which is not required to have a fire-resistance rating, the travel distance is permitted to be measured from an egress door of the room or suite to the nearest exit.

(3)  Where a public corridor is not less than 9 m wide and conforms to Clause 3.4.2.5.(1)(d), the travel distance is permitted to be determined in accordance with that Clause.

9.9.8.2.  Number of Required Exits

(1)  Except as provided in Sentences (2) and (3) and Subsection 9.9.9., not less than 2 exits shall be provided from every floor area, spaced so that the travel distance to the nearest exit is not more than

(a)	40 m in the case of business and personal services occupancies,

(b)	45 m for all occupancies where the floor area is sprinklered, and

(c)	30 m for all other occupancies.

(2)  Except as provided in Subsection 9.9.9., a single exit is permitted from each storey in buildings of 1 and 2 storeys in building height provided the floor area and travel distance requirements conform to those required in Article 9.9.7.3. and the total occupant load served by an exit facility does not exceed 60 persons.

(3)  In boarding, lodging or rooming houses

(a)	where sleeping accommodation is provided for not more than 8 persons, a single exit is permitted from each floor area, or

(b)	where sleeping accommodation is not provided in the basement, a single exit is permitted from the basement floor area.

9.9.8.3.  Contribution of Each Exit

(1)  Where more than 1 exit is required from a floor area, each exit shall be considered as contributing not more than half the required exit width.

9.9.8.4.  Location of Exits

(1)  Where more than 1 exit is required from a floor area, not less than 2 exits shall be independent of each other and be placed remote from each other along the path of travel between them.

9.9.8.5.  Exiting through a Lobby

(1)  Not more than one exit from a floor area is permitted to lead through a lobby.

(2)  The floor of the lobby referred to in Sentence (1) shall be not more than 4.5 m above grade, and the path of travel through the lobby to the outdoors shall not exceed 15 m.

(3)  The lobby referred to in Sentence (1) shall conform in all respects with the requirements for exits, except that rooms other than service rooms, storage rooms and rooms of residential or industrial occupancy are permitted to open directly onto such lobby.

(4)  Except as required in Sentence (5), an exit is permitted to lead through a lobby referred to in Sentence (1) provided the lobby is not located within an interconnected floor space other than as described in Sentence 3.2.8.2.(6).

(5)  An exit which serves a hotel is permitted to lead through a lobby referred to in Sentence (1) provided the lobby is not located within an interconnected floor space.

(6)  Where the lobby referred to in Sentence (1) and adjacent occupancies that are permitted to open into the lobby are sprinklered, the fire separation between such occupancies and the lobby need not have a fire-resistance rating.

9.9.8.6.  Exits for Mezzanines

(1)  A mezzanine shall be provided with exits on the same basis as required for a floor area where a mezzanine is considered to be a storey in Subsection 9.10.4. or is of a size required to have more than one exit.

9.9.9. Egress from Dwelling Units

9.9.9.1.  Travel Limit to Exits or Egress Doors

(1)  Except as provided in Sentences (2) and (3), every dwelling unit containing more than 1 storey shall have exits or egress doors located so that it shall not be necessary to travel up or down more than 1 storey to reach a level served by

(a)	an egress door to a public corridor, enclosed exit stair or exterior passageway, or

(b)	an exit doorway not more than 1 500 mm above adjacent ground level.

(2)  Where a dwelling unit is not located above or below another suite, the travel limit from a floor level in the dwelling unit to an exit or egress door is permitted to exceed 1 storey where that floor level is served by an openable window or door

(a)	providing an unobstructed opening of not less than 1 000 mm in height and 550 mm in width, and

(b)	located so that the sill is not more than

(i)	1 000 mm above the floor, and

(ii)	7 m above adjacent ground level.

(3)  The travel limit from a floor level in a dwelling unit to an exit or egress door is permitted to exceed 1 storey where that floor level has direct access to a balcony.

9.9.9.2.  Two Separate Exits

(1)  Except as provided in Sentence 9.9.7.2.(1), where an egress door from a dwelling unit opens onto a public corridor or exterior passageway it shall be possible from the location where the egress door opens onto the corridor or exterior passageway to go in opposite directions to 2 separate exits unless the dwelling unit has a second and separate means of egress.

9.9.9.3.  Shared Egress Facilities

(1)  A dwelling unit shall be provided with a second and separate means of egress where an egress door from the dwelling unit opens onto

(a)	an exit stairway serving more than 1 suite,

(b)	a public corridor serving more than one suite served by a single exit stairway,

(c)	an exterior passageway more than 1 500 mm above adjacent ground level, serving more than one suite and served by a single exit stairway, or

(d)	a balcony more than 1 500 mm above adjacent ground level, serving more than one suite and served by a single exit stairway.

9.9.10. Signage

9.9.10.1.  Application

(1)  This Subsection applies to all exits except those serving not more than 1 dwelling unit.

9.9.10.2.  Visibility of Exits

(1)  Exits shall be located so as to be clearly visible or their locations shall be clearly indicated.

9.9.10.3.  Required Exit Signs

(1)  Except as required in Sentence (2), every exit door other than a main entrance to a room or building shall have an exit sign over or adjacent to it when the exit serves

(a)	a three storey building,

(b)	a building with an occupant load greater than 150, or

(c)	a room or floor area that has a fire escape as part of a required means of egress.

(2)  Except for suite doors opening directly to the exterior, every exit serving a hotel shall have an exit sign placed over or adjacent to it.

9.9.10.4.  Exit Direction Signs

(1)  Exit direction signs shall be placed in corridors and passageways where necessary to indicate the direction of exit travel.

9.9.10.5.  Visibility of Exit Signs

(1)  Exit signs shall be installed so as to be visible from the exit approach.

9.9.10.6.  Lettering

(1)  Exit signs shall have the word EXIT or the words EXIT/SORTIE in red letters on a contrasting background or a red background with contrasting letters when the sign is internally lighted, and white letters on a red background or red letters on a white background when the sign is externally lighted.

(2)  Lettering referred to in Sentence (1) shall be made with not less than 19 mm wide strokes and be not less than 150 mm high when the sign is externally lighted, and at least 114 mm high when the sign is internally lighted.

(3)  Where an exit sign having the word EXIT is installed in conformance with Sentence (1), an additional sign having the word SORTIE is permitted to be installed.

9.9.10.7.  Illumination

(1)  Illumination of exit signs required in Article 9.9.10.3. shall conform to Sentences 9.9.11.3.(2) and (3).

(2)  Where illumination of exit signs required in Article 9.9.10.3. is provided by an electrical circuit, that circuit shall serve no equipment other than emergency equipment.

9.9.10.8.  Exits Continuing to a Basement

(1)  In buildings 3 storeys in building height any part of an exit ramp or stair that continues down to a basement past an exterior exit door shall be clearly marked to indicate that it does not lead to an exit, where the portion below ground level may be mistaken as the direction of exit travel.

9.9.10.9.  Floor Numbering

(1)  Arabic numerals indicating the assigned floor number shall be

(a)	mounted permanently on the stair side of the wall at the latch side of doors to exit stair shafts,

(b)	not less than 60 mm high, raised approximately 0.7 mm above the surface,

(c)	located 1 500 mm from the finished floor and not more than 300 mm from the door, and

(d)	contrasting in colour with the surface on which they are applied.

9.9.11. Lighting

9.9.11.1.  Application

(1)  This Subsection applies to the lighting of all exits except those serving not more than 1 dwelling unit.

9.9.11.2.  Required Lighting in Egress Facilities

(1)  Every exit, public corridor or corridor providing access to exit for the public shall be equipped to provide illumination to an average level of not less than 50 lx at floor or tread level and at all points such as angles and intersections at changes of level where there are stairs or ramps.

9.9.11.3.  Emergency Lighting

(1)  Emergency lighting shall be provided in

(a)	exits,

(b)	principal routes providing access to exit in an open floor area,

(c)	corridors used by the public,

(d)	underground walkways, and

(e)	public corridors.

(2)  Emergency lighting required in Sentence (1) shall be provided from a source of energy separate from the electrical supply for the building.

(3)  Lighting required in Sentence (1) shall be designed to be automatically actuated for a period of not less than 30 min when the electric lighting in the affected area is interrupted.

(4)  Illumination from lighting required in Sentence (1) shall be provided to average levels of not less than 10 lx at floor or tread level.

(5)  Where incandescent lighting is provided, lighting equal to 1 W/m2 of floor area shall be considered to meet the requirement in Sentence (4).

(6)  Where self-contained emergency lighting units are used, they shall conform to CSA C22.2 No. 141-M, “Unit Equipment for Emergency Lighting”.

Section 9.10. Fire Protection

9.10.1. General

9.10.1.1.  Support of Noncombustible Construction

(1)  Where an assembly is required to be of noncombustible construction and to have a fire-resistance rating, it shall be supported by noncombustible construction.

9.10.1.2.  Sloped Roofs

(1)  For the purposes of this Section, roofs with slopes of 60° or more to the horizontal and which are adjacent to a room or space intended for occupancy shall be considered as a wall.

9.10.1.3.  Items Under Part 3 Jurisdiction

(1)  Tents, air-supported structures, transformer vaults, walkways, elevators and escalators shall conform to Part 3.

(2)  Where rooms or spaces are intended for an assembly occupancy, such rooms or spaces shall conform to Part 3.

(3)  Basements containing more than 1 storey or exceeding 600 m2 in area shall conform to Part 3.

(4)  Where rooms or spaces are intended for the storage, manufacture or use of hazardous or explosive material, such rooms or spaces shall conform to Part 3.

(5)  Reserved

(6)  Openings through floors that are not protected by shafts or closures shall be protected in conformance with Subsection 3.2.8.

(7)  Chutes and shafts shall conform to Subsection 3.6.3. except where they are contained entirely within a dwelling unit.

(8)  Where sprinkler, standpipe and hose systems are installed, they shall be installed in conformance with Part 3.

9.10.1.4.  Items Under Part 6 Jurisdiction

(1)  In kitchens containing commercial cooking equipment used in processes producing grease-laden vapours, the equipment shall be designed and installed in conformance with Part 6.

(2)  Where fuel-fired appliances are installed on a roof, such appliances shall be installed in conformance with Part 6.

9.10.2. Occupancy Classification

9.10.2.1.  Occupancy Classification

(1)  Except as provided in Article 9.10.2.2., every building or part thereof shall be classified according to its major occupancy as belonging to one of the groups or divisions described in Table 9.10.2.1.

Table 9.10.2.1.

Occupancy Classifications

Forming Part of Sentence 9.10.2.1.(1)

| Group | Division | Description of Major Occupancies |
| --- | --- | --- |
| C | — | Residential occupancy |
| C | — | Business and personal services occupancies |
| E | — | Mercantile occupancies |
| F | 2 | Medium hazard industrial occupancies |
| F | 3 | Low hazard industrial occupancies (Does not include storage garages serving individual dwelling units) |
| Column 1 | 2 | 3 |

9.10.2.2.  Custodial and Convalescent Homes

(1)  Children’s custodial homes and convalescent homes for ambulatory occupants living as a single housekeeping unit in a dwelling unit with sleeping accommodation for not more than 10 persons is permitted to be classified as residential occupancies (Group C).

9.10.2.3.  Major Occupancies above Other Major Occupancies

(1)  Except as permitted in Article 9.10.2.4., in any building containing more than 1 major occupancy in which one major occupancy is located entirely above another, the requirements of Article 9.10.8.1. for each portion of the building containing a major occupancy shall be applied to that portion as if the entire building was of that major occupancy.

9.10.2.4.  Buildings Containing More Than One Major Occupancy

(1)  In a building containing more than 1 major occupancy, where the aggregate area of all major occupancies in a particular group or division does not exceed 10% of the floor area on the storey on which they are located, they need not be considered as major occupancies for the purposes of Articles 9.10.8.1. and 9.10.2.3. provided they are not classified as Group F, Division 2 occupancies.

9.10.2.5.  Restaurants

(1)  A restaurant is permitted to be classified as a Group E major occupancy provided such restaurant is designed to accommodate not more than 30 persons consuming food or drink.

9.10.3. Ratings

9.10.3.1.  Fire-Resistance and Fire-Protection Ratings

(1)  Where a fire-resistance rating or a fire-protection rating is required in this Section for an element of a building, such rating shall be determined in conformance with the test methods described in Part 3, or the Supplementary Guidelines.

9.10.3.2.  Flame-Spread Rating

(1)  Where a flame-spread rating is required in this Section for an element of a building, such rating shall be determined in accordance with the test methods described in Part 3, or in accordance with the Supplementary Guidelines.

(2)  Unless the flame-spread rating is referred to herein as a “surface flame-spread rating”, it shall apply to any surface of the element being considered that would be exposed by cutting through it as well as to the exposed surface of the element.

9.10.3.3.  Fire Exposure

(1)  Floor, roof and ceiling assemblies shall be rated for exposure to fire on the underside.

(2)  Exterior walls shall be rated for exposure to fire from inside the building, except that such walls need not comply with the temperature rise limitations required by the standard tests referred to in Article 9.10.3.1. if such walls have a limiting distance of not less than 1 200 mm, and due allowance is made for the effects of heat radiation in accordance with the requirements in Part 3.

(3)  Firewalls and Interior vertical fire separations required to have fire-resistance ratings shall be rated for exposure to fire on each side.

9.10.3.4.  Suspended Membrane Ceiling

(1)  Where a ceiling construction has a suspended membrane ceiling with lay-in panels or tiles which contribute to the required fire-resistance rating, hold down clips or other means shall be provided to prevent the lifting of such panels or tiles in the event of a fire.

9.10.4. Building Size Determination

9.10.4.1.  Mezzanines not Considered as Storeys

(1)  Mezzanines shall not be considered as storeys for the purpose of determining building height where the aggregate area of mezzanine floors does not exceed 10% of

(a)	the suite in which it is located, where there is more than one suite in the storey, or

(b)	the storey in which it is located, in all other cases.

(2)  Mezzanines shall not be considered as storeys for the purpose of determining building height where they occupy an aggregate area not exceeding 40% of the area of the room or the storey in which they are located provided the space above the mezzanine floor has no visual obstructions more than 1 070 mm above such floors.

9.10.4.2.  More Than One Level of Mezzanine

(1)  Where more than 1 level of mezzanine is provided in a storey, each level additional to the first shall be considered as a storey.

9.10.4.3.  Basement Storage Garage

(1)  Where a basement is used primarily as a storage garage, the basement is permitted to be considered as a separate building for the purposes of this Section provided the floor above the basement and the exterior walls of the basement above the adjoining ground level are constructed as fire separations of masonry or concrete having a fire-resistance rating of not less than 2 h.

9.10.4.4.  Roof-Top Enclosures

(1)  Roof-top enclosures provided for elevator machinery, stairways and service rooms, used for no purpose other than for service to the building, shall not be considered as a storey in calculating the building height.

9.10.5. Permitted Openings in Wall and Ceiling Assemblies

9.10.5.1.  Permitted Openings in Wall and Ceiling Membranes

(1)  Except as permitted in Sentences (2) and (4), a membrane forming part of an assembly required to have a fire-resistance rating shall not be pierced by openings into the assembly unless the assembly has been tested and rated for such openings.

(2)  A wall or ceiling membrane forming part of an assembly required to have a fire-resistance rating is permitted to be pierced by openings for electrical and similar service outlet boxes provided such outlet boxes are tightly fitted.

(3)  Where boxes referred to in Sentence (2) are located on both sides of walls required to provide a fire-resistance rating, they shall be offset where necessary to maintain the integrity of the fire separation.

(4)  A membrane ceiling forming part of an assembly assigned a fire-resistance rating on the basis of Table A-9.10.3.1.B. in the Supplementary Guidelines, is permitted to be pierced by openings leading to ducts within the ceiling space provided the ducts, the amount of openings and their protection conform to the requirements in the Supplementary Guidelines.

9.10.6. Construction Types

9.10.6.1.  Combustible Elements in Noncombustible Construction

(1)  Where a building or part of a building is required to be of noncombustible construction, combustible elements shall be limited in conformance with the requirements in Subsection 3.1.5.

9.10.6.2.  Heavy Timber Construction

(1)  Heavy timber construction shall be considered to have 45 min fire-resistance rating when it is constructed in accordance with the requirements for heavy timber construction in Article 3.1.4.6.

9.10.7. Steel Members

9.10.7.1.  Protection of Structural Steel Members

(1)  Except as permitted in Article 3.2.2.3., structural steel members used in construction required to have a fire-resistance rating shall be protected to provide the required fire-resistance rating.

9.10.8. Fire Resistance in Relation to Occupancy and Height

9.10.8.1.  Fire Resistance Ratings for Floors and Roofs

(1)  Except as otherwise provided in this Subsection, the fire-resistance ratings of floors and roofs shall conform to Table 9.10.8.1.

Table 9.10.8.1.

Fire Resistance Ratings for Structural Members and Assemblies

Forming Part of Sentence 9.10.8.1.(1)

| Major Occupancy | Maximum Building Height, Storeys | Minimum Fire Resistance Rating by Building Element, min |  |  |
| --- | --- | --- | --- | --- |
|  |  | Floors Except Floors over Crawl Spaces | Mezzanine Floors | Roofs |
| Residential (Group C) | 3 | 45 | 45 | — |
| All other | 2 | 45 | — | — |
| occupancies | 3 | 45 | 45 | 45 |
| Column 1 | 2 | 3 | 4 | 5 |

9.10.8.2.  Fire-Resistance Ratings in Sprinklered Buildings

(1)  The requirements in Table 9.10.8.1. for roof assemblies to have a fire-resistance rating are permitted to be waived in sprinklered buildings where

(a)	the sprinkler system is electrically supervised in conformance with Sentence 3.2.4.9.(2), and

(b)	the operation of the sprinkler system will cause a signal to be transmitted to the fire department in conformance with Sentence 3.2.4.7.(4).

9.10.8.3.  Fire-Resistance Ratings for Walls, Columns and Arches

(1)  Except as otherwise provided in this Subsection, all loadbearing walls, columns and arches in the storey immediately below a floor or roof assembly shall have a fire-resistance rating of not less than that required for the supported floor or roof assembly.

9.10.8.4.  Service Rooms

(1)  Construction supporting a service room need not conform to Article 9.10.8.3.

9.10.8.5.  Mezzanines

(1)  Mezzanines required to be counted as storeys in Articles 9.10.4.1. and 9.10.4.2. shall be constructed in conformance with the requirements for “Floors Except Floors over Crawl Spaces” in Table 9.10.8.1.

9.10.8.6.  Roofs Supporting an Occupancy

(1)  Where a portion of a roof supports an occupancy, that portion shall be constructed as a fire separation having a fire-resistance rating conforming to the rating for “Floors Except Floors over Crawl Spaces” in Table 9.10.8.1.

9.10.8.7.  Floors of Exterior Passageways

(1)  Except as provided in Sentences (2) and (3), the floor assembly of every exterior passageway used as part of a means of egress shall have a fire-resistance rating of not less than 45 min or be of noncombustible construction.

(2)  No fire-resistance rating is required for floors of exterior passageways serving buildings of Group D, E or F major occupancy that are not more than 2 storeys in building height.

(3)  No fire-resistance rating is required for floors of exterior passageways serving a single dwelling unit where no suite is located above or below the dwelling unit.

9.10.8.8.  Crawl Spaces

(1)  Where a crawl space exceeds 1 800 mm in height or is used for any occupancy or as a plenum in combustible construction or for the passage of flue pipes, it shall be considered as a basement in applying the requirements in Article 9.10.8.1.

9.10.8.9.  Application to Houses

(1)  Table 9.10.8.1. does not apply to a dwelling unit which has no other dwelling unit above or below it or to a dwelling unit which is not above or below another major occupancy.

9.10.8.10.  Part 3 as an Alternative

(1)  The fire-resistance ratings of floors, roofs, loadbearing walls, columns and arches need not conform to this Subsection if such assemblies conform in all respects to the appropriate requirements in Section 3.2.

9.10.9. Fire Separations Between Rooms and Spaces Within Buildings

9.10.9.1.  Application

(1)  This Subsection applies to fire separations required between rooms and spaces in buildings except between rooms and spaces within a dwelling unit.

9.10.9.2.  Continuous Barrier

(1)  Except as permitted in Article 9.10.9.3., a wall or floor assembly required to be a fire separation shall be constructed as a continuous barrier against the spread of fire.

9.10.9.3.  Openings to be Protected With Closures

(1)  Except as permitted in Articles 9.10.9.5., 9.10.9.6. and 9.10.9.7., openings in required fire separations shall be protected with closures conforming to Subsection 9.10.13.

9.10.9.4.  Floor Assemblies

(1)  Except as permitted in Sentences (2) to (4), all floor assemblies shall be constructed as fire separations.

(2)  Floor assemblies contained within dwelling units need not be constructed as fire separations.

(3)  Floor assemblies for which no fire-resistance rating is required by Subsection 9.10.8. and floors of mezzanines not required to be counted as storeys in Articles 9.10.4.1. and 9.10.4.2. need not be constructed as fire separations.

(4)  Where a crawl space is not required by Article 9.10.8.8. to be constructed as a basement, the floor above it need not be constructed as a fire separation.

9.10.9.5.  Interconnected Floor Spaces

(1)  Except as permitted in Article 9.9.4.7., interconnected floor spaces shall conform to the requirements of Subsection 3.2.8.

9.10.9.6.  Service Equipment Penetrating a Fire Separation

(1)  Piping, tubing, ducts, chimneys, wiring, conduit, electrical outlet boxes and other similar service equipment that penetrate a required fire separation shall be tightly fitted or fire stopped to maintain the integrity of the separation.

(2)  Except as provided in Sentences (3) to (9) and Article 9.10.9.7., pipes, ducts, electrical outlet boxes, totally enclosed raceways or other similar service equipment that partly or wholly penetrate an assembly required to have a fire-resistance rating shall be noncombustible unless the assembly has been tested incorporating such equipment.

(3)  Electrical wires or other similar wiring enclosed in noncombustible totally enclosed raceways are permitted to partly or wholly penetrate an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required in Sentence (2).

(4)  Electrical wires or cables, single or grouped, with combustible insulation or jacketing that is not totally enclosed in raceways of noncombustible material, are permitted to partly or wholly penetrate an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required in Sentence (2) provided the overall diameter of the wiring is not more than 25 mm.

(5)  Combustible totally enclosed raceways which are embedded in a concrete floor slab are permitted in an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required in Sentence (2), where the concrete provides at least 50 mm of cover between the raceway and the bottom of slab.

(6)  Combustible outlet boxes are permitted in an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required in Sentence (2) provided the opening through the membrane into the box does not exceed 160 cm2.

(7)  Combustible water distribution piping that has an outside diameter not more than 30 mm is permitted to partly or wholly penetrate a vertical fire separation that is required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required in Sentence (2) provided the piping is sealed in conformance with Article 3.1.9.1.

(8)  Combustible sprinkler piping is permitted to penetrate a fire separation provided the fire compartments on each side of the fire separation are sprinklered.

(9)  Combustible piping for central vacuum systems is permitted to penetrate a fire separation provided the installation conforms to the requirements that apply to combustible piping in Sentences 9.10.9.7.(2) to (6).

9.10.9.7.  Combustible Piping

(1)  Except as permitted in Sentences (2) to (6), combustible piping shall not be used where any part of a piping system partly or wholly penetrates a fire separation required to have a fire-resistance rating or penetrates a membrane that contributes to the required fire-resistance rating of an assembly.

(2)  Combustible piping not located in a vertical shaft is permitted to penetrate a fire separation required to have a fire-resistance rating or a membrane that forms part of an assembly required to have a fire-resistance rating provided the piping is sealed at the penetration by a firestop system that has an F rating not less than the fire-resistance rating required for the fire separation.

(3)  The rating referred to in Sentence (2) shall be based on CAN4-S115, “Standard Method of Fire Tests for Firestop Systems” with a pressure differential of 50 Pa between the exposed and unexposed sides, with the higher pressure on the exposed side.

(4)  Combustible drain piping is permitted to penetrate a horizontal fire separation or a membrane that contributes to the required fire-resistance rating of a horizontal fire separation provided it leads directly from a noncombustible water closet through a concrete floor slab.

(5)  Combustible piping is permitted

(a)	on one side of a vertical fire separation provided it is not located in a vertical shaft, and

(b)	to penetrate a vertical or horizontal fire separation when the fire compartment on each side of the fire separation is sprinklered.

(6)  In buildings containing 2 dwelling units only, combustible piping is permitted on one side of a horizontal fire separation.

9.10.9.8.  Collapse of Combustible Construction

(1)  Combustible construction that abuts on or is supported by a noncombustible fire separation shall be constructed so that its collapse under fire conditions will not cause collapse of the fire separation.

9.10.9.9.  Reduction in Thickness of Fire Separation by Beams and Joists

(1)  Beams and joists framed into a masonry or concrete fire separation shall not reduce the thickness of the fire separation to less than

(a)	100 mm of solid masonry or solid concrete, or

(b)	the equivalent thickness of the masonry or concrete determined in accordance with the Supplementary Guidelines.

9.10.9.10.  Concealed Spaces above Fire Separations

(1)  Except as provided in Sentence (2), a horizontal service space or other concealed space located above a required vertical fire separation shall be divided at the fire separation by an equivalent fire separation within the space.

(2)  Where a horizontal service space or other concealed space is located above a required vertical fire separation other than a vertical shaft, such space need not be divided as required in Sentence (1) provided the construction between such space and the space below is constructed as a fire separation having a fire-resistance rating not less than that required for the vertical fire separation, except that where the vertical fire separation is not required to have a fire-resistance rating greater than 45 min, the fire-resistance rating of the ceiling is permitted to be reduced to 30 min.

9.10.9.11.  Separation of Residential Occupancies

(1)  Except as provided in Sentences (2) and (4), residential occupancies shall be separated from all other major occupancies by a fire separation having a fire-resistance rating of not less than 1 h.

(2)  Except as provided in Sentence (3), a major occupancy classified as a residential occupancy, including live/work units, shall be separated from other major occupancies classified as mercantile or medium hazard industrial occupancies by a fire separation having a fire-resistance rating of not less than 2 h.

(3)  Where not more than 2 dwelling units or live/work units are located in a building containing a mercantile occupancy, such mercantile occupancy shall be separated from the dwelling units or live/work units by a fire separation having not less than 1 h fire-resistance rating.

(4)  The requirement for fire separations between major occupancies in Sentence (1) is waived for the occupancies allowed within live/work units.

9.10.9.12.  Residential Suites, Live/Work Units and Industrial Buildings

(1)  Except as provided in Sentence (2), not more than 1 suite of residential occupancy shall be contained within a building classified as a Group F, Division 2 major occupancy.

(2)  Except where a Group F Division 2 major occupancy is directly related to live/work units, not more than one suite of residential occupancy shall be contained within a building classified as Group F, Division 2 major occupancy.

9.10.9.13.  Separation of Suites

(1)  Except as required in Article 9.10.9.14., and as permitted by Sentence (2), each suite in other than business and personal services occupancies shall be separated from adjoining suites by a fire separation having a fire-resistance rating of not less than 45 min.

(2)  In sprinklered buildings, suites of business and personal services occupancy and mercantile occupancy that are served by public corridors conforming with Sentence 3.3.1.4.(4) are not required to be separated from each other by fire separations.

9.10.9.14.  Separation of Residential Suites

(1)  Except as provided in Sentences (2) and (3) and Article 9.10.20.2., suites in residential occupancies shall be separated from adjacent rooms and suites by a fire separation having a fire-resistance rating of not less than 45 min.

(2)  Sleeping rooms in boarding, lodging or rooming houses where sleeping accommodation is provided for not more than 8 boarders or lodgers shall be separated from the remainder of the floor area by a fire separation having a fire-resistance rating of not less than 30 min where the sleeping rooms form part of the proprietor’s residence and do not contain cooking facilities.

(3)  Dwelling units that contain 2 or more storeys including basements shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 1 h.

9.10.9.15.  Separation of Public Corridors

(1)  Except as provided in Sentences (2) and (3), public corridors shall be separated from the remainder of the building by a fire separation having not less than a 45 min fire-resistance rating.

(2)  In other than residential occupancies, no fire-resistance rating is required for fire separations between a public corridor and the remainder of the building if

(a)	the floor area is sprinklered,

(b)	the sprinkler system is electrically supervised in conformance with Sentence 3.2.4.9.(2), and

(c)	the operation of the sprinkler system will cause a signal to be transmitted to the fire department in conformance with Sentence 3.2.4.7.(4).

(3)  In other than residential occupancies, no fire separation is required between a public corridor and the remainder of the building if

(a)	the floor area is sprinklered,

(b)	the sprinkler system is electrically supervised in conformance with Sentence 3.2.4.9.(2),

(c)	the operation of the sprinkler system will cause a signal to be transmitted to the fire department in conformance with Sentence 3.2.4.7.(4), and

(d)	the corridor exceeds 5 m in width.

9.10.9.16.  Separation of Storage Garages

(1)  Except as provided in Sentences (2) and (3), a storage garage shall be separated from other occupancies by a fire separation having not less than a 1.5 h fire-resistance rating.

(2)  Except as permitted in Sentence (3), storage garages containing 5 motor vehicles or fewer shall be separated from other occupancies by a fire separation of not less than 1 h.

(3)  Where a storage garage serves only the dwelling unit to which it is attached or built in, it shall be considered as part of that dwelling unit and the fire separation required in Sentence (2) need not be provided between the garage and the dwelling unit where

(a)	the construction between the garage and the dwelling unit provides an effective barrier to gas and exhaust fumes, and

(b)	every door between the garage and dwelling unit conforms to Article 9.10.13.15.

9.10.9.17.  Separation of Repair Garages

(1)  Except as provided in Sentence (2), a repair garage shall be separated from other occupancies by a fire separation having a fire-resistance rating of not less than 2 h.

(2)  Ancillary spaces directly serving a repair garage, including waiting rooms, reception rooms, tool and parts storage areas and supervisory office space need not be separated from the repair garage but shall be separated from other occupancies as required in Sentence (1).

9.10.9.18.  Exhaust Ducts Serving More Than One Fire Compartment

(1)  Where a vertical service space contains an exhaust duct that serves more than one fire compartment, the duct shall have a fan located at or near the exhaust outlet to ensure that the duct is under negative pressure.

(2)  Individual fire compartments referred to in Sentence (1) shall not have fans that exhaust directly into the duct in the vertical service space.

9.10.9.19.  Central Vacuum Systems

(1)  A central vacuum system shall serve not more than one suite.

9.10.10. Service Rooms

9.10.10.1.  Application

(1)  This Subsection applies to service rooms in all buildings except rooms located within a dwelling unit.

9.10.10.2.  Service Room Floors

(1)  The fire-resistance rating requirements in this Subsection do not apply to the floor assembly immediately below a service room.

9.10.10.3.  Separation of Service Rooms

(1)  Except as required in Sentence (2) and Articles 9.10.10.5. and 9.10.10.6., service rooms shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 1 h when the floor area containing the service room is not sprinklered.

(2)  Where a room contains a limited quantity of service equipment and the service equipment does not constitute a fire hazard, the requirements in Sentence (1) shall not apply.

9.10.10.4.  Appliances and Equipment to be Located in a Service Room

(1)  Except as provided in Sentence (2) and Article 9.10.10.5., fuel-fired appliances other than fireplaces shall be located in a service room separated from the remainder of the building by a fire separation having not less than a 1 h fire-resistance rating.

(2)  Except as required in the appliance installation standards referenced in Sentences 6.2.1.5.(1), 9.33.5.2.(1) and 9.33.5.3.(1), fuel-fired space-heating appliances, space-cooling appliances and service water heaters need not be separated from the remainder of the building as required in Sentence (1) where the equipment serves

(a)	not more than one room or suite, or

(b)	a building with a building area of not more than 400 m2 and a building height of not more than 2 storeys.

9.10.10.5.  Incinerators

(1)  Service rooms containing incinerators shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 2 h.

(2)  The design, construction, installation and alteration of each indoor incinerator shall conform to NFPA 82, “Incinerators, Waste and Linen Handling Systems and Equipment”.

(3)  Every incinerator shall be connected to a chimney flue conforming to the requirements in Section 9.21 and serving no other appliance.

(4)  An incinerator shall not be located in a room with other fuel-fired appliances.

9.10.10.6.  Storage Rooms

(1)  Rooms for the temporary storage of combustible refuse in all occupancies or for public storage in residential occupancies shall be separated from the remainder of the building by a fire separation having not less than a 1 h fire-resistance rating, except that a 45 min fire separation is permitted where the fire-resistance rating of the floor assembly is not required to exceed 45 min, or where such rooms are sprinklered.

9.10.11. Firewalls

9.10.11.1.  Required Firewalls

(1)  Except as provided in Articles 9.10.11.2. and 9.10.11.4., a party wall on a property line shall be constructed as a firewall.

9.10.11.2.  Firewalls Not Required

(1)  In a building of residential occupancy in which there is no dwelling unit above another dwelling unit, a party wall on a property line between dwelling units need not be constructed as a firewall provided it is constructed as a fire separation having not less than a 1 h fire-resistance rating.

(2)  The wall described in Sentence (1) shall provide continuous protection from the top of the footings to the underside of the roof deck.

(3)  Any space between the top of the wall described in Sentence (1) and the roof deck shall be tightly filled with mineral wool or noncombustible material.

9.10.11.3.  Construction of Firewalls

(1)  Where firewalls are used, the requirements in Part 3 shall apply.

9.10.11.4.  Firewalls in Detached Garages

(1)  Where a garage is detached from the dwelling unit but attached to another garage on the adjacent property, the party wall so formed shall be constructed as a fire separation having a fire-resistance rating of not less than 45 min.

9.10.12. Prevention of Fire Spread at Exterior Walls and between Storeys

9.10.12.1.  Separation of Exterior Openings

(1)  In buildings of mercantile or medium hazard industrial occupancy, exterior openings in one storey shall be separated from openings in an adjacent storey by

(a)	a wall not less than 1 000 mm in vertical dimension, or

(b)	a canopy or balcony not less than 1 000 mm in width.

(2)  The wall, canopy or balcony described in Sentence (1) shall have a fire-resistance rating not less than that required for the floor assembly separating the storeys, except that the rating need not exceed 1 h.

9.10.12.2.  Termination of Floors or Mezzanines

(1)  Except as provided in Sentence (2) and in Articles 9.10.1.3. and 9.10.9.5., the portions of a floor area or mezzanine that do not terminate at an exterior wall, a firewall or a vertical shaft, shall terminate at a vertical fire separation having a fire-resistance rating not less than that required for the floor assembly that terminates at the separation.

(2)  A mezzanine need not terminate at a vertical fire separation where the mezzanine is not required to be considered as a storey in Articles 9.10.4.1. and 9.10.4.2.

9.10.12.3.  Location of Skylights

(1)  Where a wall in a building is exposed to a fire hazard from an adjoining roof of a separate unsprinklered fire compartment in the same building, the roof shall contain no skylights within a horizontal distance of 5 m of the windows in the exposed wall.

9.10.12.4.  Exterior Walls Meeting at an Angle

(1)  Except as provided in Article 9.9.4.5., where exterior walls of a building meet at an external angle of less than 135°, the horizontal distance from an opening in one wall to an opening in the other wall shall be not less than 1 200 mm where the openings are in different fire compartments.

(2)  The exterior wall of each fire compartment referred to in Sentence (1) within the 1 200 mm distance, shall have a fire-resistance rating not less than that required for the interior vertical fire separation between the compartment and the remainder of the building.

9.10.12.5.  Protection of Soffits

(1)  Except as provided in Sentences (2) and (3), where a common attic or roof space spans more than 2 suites of residential occupancy, and projects beyond the exterior wall of the building, the portion of any soffit or other surface enclosing the projection which is less than 2 500 mm vertically above a window or door and less than 1 200 mm from either side of the window or door, shall have no unprotected openings and shall be protected by

(a)	noncombustible material having a minimum thickness of 0.38 mm and a melting point not below 650°C,

(b)	not less than 12.7 mm thick gypsum soffit board or gypsum wallboard installed according to CSA A82.31-M, “Gypsum Board Application”,

(c)	not less than 11 mm thick plywood,

(d)	not less than 12.5 mm thick OSB or waferboard, or

(e)	not less than 11 mm thick lumber.

(2)  Where the soffit or other surface described in Sentence (1) is completely separated from the remainder of the attic or roof space by firestopping, the requirements in Sentence (1) do not apply.

(3)  Where all suites spanned by a common attic or roof space are sprinklered, the requirements in Sentence (1) do not apply provided that all rooms, including closets and bathrooms, having openings in the wall beneath the soffit are sprinklered, notwithstanding any exceptions in the sprinkler standards referenced in Article 3.2.5.13.

9.10.13. Doors, Dampers and Other Closures in Fire Separations

9.10.13.1.  Closures

(1)  Except as provided in Article 9.10.13.2., openings in required fire separations shall be protected with a closure conforming to Table 9.10.13.1. and shall be installed in conformance with Chapters 2 to 14 of NFPA 80, “Fire Doors and Windows” unless otherwise specified herein.

Table 9.10.13.1.

Fire-Protection Ratings for Closures

Forming Part of Sentence 9.10.13.1.(1)

| Required Fire-Resistance Rating of Fire Separation | Required Fire-Protection Rating of Closure |
| --- | --- |
| 30 or 45 min | 20 min(1) |
| 1 h | 45 min(1) |
| 1.5 h | 1 h |
| 2 h | 1.5 h |
| 3 h | 2 h |
| 4 h | 3 h |
| Column 1 | 2 |

Note to Table 9.10.13.1.:

(1)	 See Article 9.10.13.2.

9.10.13.2.  Solid Core Wood Door as a Closure

(1)  A 45 mm thick solid core wood door is permitted to be used where a minimum fire-protection rating of 20 min is permitted or between a public corridor and a suite provided the door conforms to CAN4-S113, “Standard Specification for Wood Core Doors Meeting the Performance Required by CAN4-S104 for Twenty Minute Fire-Rated Closure Assemblies”.

(2)  Doors described in Sentence (1) shall have not more than a 6 mm clearance beneath and not more than 3 mm at the sides and top.

(3)  Where a 45 mm thick solid core wood door is permitted in a required fire separation, the requirement for a noncombustible sill in NFPA 80, “Fire Doors and Windows” shall not apply.

9.10.13.3.  Unrated Wood Door Frames

(1)  Doors required to provide a 20 min fire-protection rating or permitted to be 45 mm solid core wood shall be mounted in a wood frame of at least 38 mm thickness where the frame has not been tested and rated.

9.10.13.4.  Doors as a Means of Egress

(1)  Doors forming part of an exit or a public means of egress shall conform to Subsection 9.9.6. in addition to this Subsection.

9.10.13.5.  Wired Glass as a Closure

(1)  Wired glass conforming to Article 9.7.3.1. which has not been tested in accordance with Article 9.10.3.1. is permitted as a closure in a vertical fire separation required to have a fire-resistance rating of not more than 1 h provided such glass is not less than 6 mm thick and is mounted in conformance with Sentence (2).

(2)  Wired glass described in Sentence (1) shall be mounted in fixed steel frames having a minimum metal thickness of not less than 1.35 mm and a glazing stop of not less than 20 mm on each side of the glass.

(3)  Individual panes of glass described in Sentence (1) shall not exceed 0.8 m2 in area or 1 400 mm in height or width, and the area of glass not structurally supported by mullions shall not exceed 7.5 m2.

9.10.13.6.  Steel Door Frames

(1)  Steel door frames forming part of a closure in a fire separation, including anchorage requirements, shall conform to CAN4-S105, “Standard Specification for Fire Door Frames Meeting the Performance Required by CAN4-S104.”

9.10.13.7.  Glass Block as a Closure

(1)  Glass block that has not been tested in accordance with Article 9.10.3.1. is permitted as a closure in a fire separation required to have a fire-resistance rating of not more than 1 h.

9.10.13.8.  Maximum Size of Opening

(1)  The size of an opening in an interior fire separation, even where protected with a closure, shall not exceed 11 m2, with no dimension greater than 3.7 m, if a fire compartment on either side of the fire separation is not sprinklered.

(2)  The size of an opening in an interior fire separation, even where protected with a closure, shall not exceed 22 m2, with no dimension greater than 6 m, when the fire compartments on both sides of the fire separation are sprinklered.

9.10.13.9.  Door Latch

(1)  Every swing type door in a fire separation shall be equipped with a latch.

9.10.13.10.  Self-Closing Device

(1)  Except as described in Sentence (2), every door in a fire separation shall have a self-closing device.

(2)  Self-closing devices are not required between public corridors and suites in business and personal services occupancies, except in

(a)	dead-end corridors, or

(b)	a corridor which serves a hotel.

9.10.13.11.  Hold-Open Devices

(1)  Where hold-open devices are used on doors in required fire separations, they shall be installed in accordance with Article 3.1.8.12.

9.10.13.12.  Service Room Doors

(1)  Swing-type doors shall open into service rooms containing fuel-fired equipment where such doors lead to public corridors or rooms used for assembly but shall swing outward from such rooms in all other cases.

9.10.13.13.  Fire Dampers

(1)  Except as permitted in Sentences (2) to (5) and 9.10.5.1.(4) ducts that connect 2 fire compartments or penetrate an assembly required to be a fire separation with a fire-resistance rating shall be equipped with a fire damper in conformance with Article 3.1.8.9.

(2)  A fire damper is not required where a noncombustible branch duct pierces a required fire separation provided the duct

(a)	has melting point not below 760°C,

(b)	has a cross-sectional area less than 0.013 m2, and

(c)	supplies only air-conditioning units or combined air-conditioning and heating units discharging air at not more than 1 200 mm above the floor.

(3)  A fire damper is not required where a noncombustible branch duct pierces a required fire separation around an exhaust duct riser in which the air flow is upward provided

(a)	the melting point of the branch duct is not below 760°C,

(b)	the branch duct is carried up inside the riser at least 500 mm, and

(c)	the exhaust duct is under negative pressure as described in Article 9.10.9.18.

(4)  Noncombustible ducts that penetrate a fire separation separating a vertical service space from the remainder of the building need not be equipped with a fire damper at the fire separation provided

(a)	the ducts have a melting point above 760°C, and

(b)	each individual duct exhausts directly to the outside at the top of the vertical service space.

(5)  A duct serving commercial cooking equipment and piercing a required fire separation need not be equipped with a fire damper at the fire separation.

9.10.13.14.  Fire Stop Flaps

(1)  Fire stop flaps in ceiling membranes required in Sentence 9.10.5.1.(4) shall be constructed in conformance with the Supplementary Guidelines.

9.10.13.15.  Doors Between Garages and Dwelling Units

(1)  A door between an attached or built-in garage and a dwelling unit shall be tight-fitting and weatherstripped to provide an effective barrier against the passage of gases and exhaust fumes and shall be fitted with a self-closing device.

(2)  A doorway between an attached or built-in garage and a dwelling unit shall not be located in a room intended for sleeping.

9.10.13.16.  Door Stops

(1)  Where a door is installed so that it may damage the integrity of a fire separation if its swing is unrestricted, door stops shall be installed to prevent such damage.

9.10.14. Spatial Separations between Buildings

9.10.14.1.  Maximum Percentage Area of Unprotected Openings

(1)  Except as provided in Sentence (2) and Articles 9.10.14.3. to 9.10.14.11., the maximum percentage of unprotected openings in an exposing building face shall conform to Table 9.10.14.1. or to Subsection 3.2.3., whichever is the least restrictive for the occupancy being considered.

(2)  An opening in an exposing building face not more than 0.013 m2 shall not be considered an unprotected opening.

Table 9.10.14.1.

Maximum Percentage of Unprotected Openings or Glazed Areas, % of Exposing Building Face Area

Forming Part of Sentence 9.10.14.1.(1)

| Occupancy Classification of Building | Maximum Area of Exposing Building Face, m2 | Limiting Distance, m |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Less than 1.2 | 1.2 | 1.5 | 2.0 | 2.5 | 3.0 | 4.0 | 6.0 | 8.0 | 10.0 | 12.0 | 16.0 | 20.0 | 25.0 |
| Residential, | 10 | 0 | 8 | 12 | 21 | 33 | 55 | 96 | 100 | — | — | — | — | — | — |
| business and | 15 | 0 | 8 | 10 | 17 | 25 | 37 | 67 | 100 | — | — | — | — | — | — |
| personal | 20 | 0 | 8 | 10 | 15 | 21 | 30 | 53 | 100 | — | — | — | — | — | — |
| services and | 25 | 0 | 8 | 9 | 13 | 19 | 26 | 45 | 100 | — | — | — | — | — | — |
| low hazard | 30 | 0 | 7 | 9 | 12 | 17 | 23 | 39 | 88 | 100 | — | — | — | — | — |
| industrial | 40 | 0 | 7 | 8 | 11 | 15 | 20 | 32 | 69 | 100 | — | — | — | — | — |
|  | 50 | 0 | 7 | 8 | 10 | 14 | 18 | 28 | 57 | 100 | — | — | — | — | — |
|  | 100 | 0 | 7 | 8 | 9 | 11 | 13 | 18 | 34 | 56 | 84 | 100 | — | — | — |
|  | Over 100 | 0 | 7 | 7 | 8 | 9 | 10 | 12 | 19 | 28 | 40 | 55 | 92 | 100 | — |
| Mercantile | 10 | 0 | 4 | 6 | 10 | 17 | 25 | 48 | 100 | — | — | — | — | — | — |
| and medium | 15 | 0 | 4 | 5 | 8 | 13 | 18 | 34 | 82 | 100 | — | — | — | — | — |
| hazard | 20 | 0 | 4 | 5 | 7 | 11 | 15 | 27 | 63 | 100 | — | — | — | — | — |
| industrial | 25 | 0 | 4 | 5 | 7 | 9 | 13 | 22 | 51 | 94 | 100 | — | — | — | — |
|  | 30 | 0 | 4 | 4 | 6 | 9 | 12 | 20 | 44 | 80 | 100 | — | — | — | — |
|  | 40 | 0 | 4 | 4 | 6 | 8 | 10 | 16 | 34 | 61 | 97 | 100 | — | — | — |
|  | 50 | 0 | 4 | 4 | 5 | 7 | 9 | 14 | 29 | 50 | 79 | 100 | — | — | — |
|  | 100 | 0 | 4 | 4 | 4 | 5 | 6 | 9 | 17 | 28 | 42 | 60 | 100 | — | — |
|  | Over 100 | 0 | 4 | 4 | 4 | 4 | 5 | 6 | 10 | 14 | 20 | 27 | 46 | 70 | 100 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |

9.10.14.2  Area of Exposing Building Face

(1)  The area of an exposing building face shall be calculated as the total area of exterior wall facing in 1 direction on any side of a building measured from the finished ground level to the uppermost ceiling, except that where a building is divided by fire separations into fire compartments, the area of exposing building face is permitted to be calculated for each fire compartment provided such separations have not less than a 45 min fire-resistance rating.

9.10.14.3.  Inadequate Fire-fighting Facilities

(1)  Where there is no fire department or where a fire department is not organized, trained and equipped to meet the needs of the community, the required limiting distance determined from Article 9.10.14.1. or required in Articles 9.10.14.12., 9.10.14.14., and 9.10.14.16., shall be doubled for a building that is not sprinklered.

9.10.14.4.  Alternate Method of Determining Limiting Distance

(1)  The limiting distance shown in Table 9.10.14.1. is permitted to be reduced provided it is not less than the square root of

(a)	the aggregate area of unprotected openings in an exposing building face in residential occupancies, business and personal services occupancies and low hazard industrial occupancies, and

(b)	twice the aggregate area of unprotected openings in mercantile occupancies and medium hazard industrial occupancies.

9.10.14.5.  Openings in Walls Having a Limiting Distance Less Than 1.2 m.

(1)  Openings in a wall having a limiting distance of less than 1.2 m shall be protected by closures, of other than wired glass or glass block, whose fire protection rating is in conformance with the fire-resistance rating required for the wall.

9.10.14.6.  Allowance for Sprinklers and Wired Glass or Glass Block

(1)  The maximum area of unprotected openings is permitted to be doubled where the building is sprinklered provided all rooms, including closets and bathrooms, that are adjacent to the exposing building face and that have unprotected openings are sprinklered, notwithstanding any exemptions in the sprinkler standards referenced in Article 3.2.5.13.

(2)  The maximum area of unprotected openings is permitted to be doubled where the unprotected openings are glazed with wired glass in steel frames or glass blocks as described in Articles 9.10.13.5. and 9.10.13.7.

9.10.14.7.  Exterior Wall Construction for Irregular-Shaped or Skewed Walls

(1)  For the purpose of using Table 9.10.14.11. to determine the required type of construction, cladding and fire-resistance rating for an exterior wall

(a)	the exposing building face is permitted to be divided into any number of portions and the fire-resistance rating, type of cladding and percentage of unprotected openings limitations is permitted to be determined individually for each portion based on the limiting distance for each portion so divided;

(b)	the exposing building face shall be taken as the projection of the exterior wall onto a vertical plane located so that no portion of the exterior wall of the building is between the vertical plane and the line to which the limiting distance is established in Clause (a), and

(c)	for the purpose of determining the actual area of unprotected openings permitted in an exterior wall, the unprotected openings shall be projected onto the vertical plane established in Clause (b).

(2)  Unprotected openings in the exposing building face referred to in Sentence (1) shall not be permitted if the limiting distance is less than 1.2 m and shall be limited in conformance with the requirements for unprotected openings in Table 9.10.14.1. where the limiting distance is 1.2 m or greater.

9.10.14.8.  Percentage of Unprotected Openings for Irregular-Shaped or Skewed Walls

(1)  For the purpose of using Table 9.10.14.1. to determine the actual percentage of unprotected openings permitted in an irregularly-shaped or skewed exterior wall, the location of the exposing building face is permitted to be taken at a vertical plane located so that there are no unprotected openings between the vertical plane and the line to which limiting distance is measured.

9.10.14.9.  Storeys at Street Level

(1)  The exposing building face of a storey that faces a street and is at approximately the same level as the street is permitted to have unlimited unprotected openings if the limiting distance is not less than 9 m.

9.10.14.10.  Open-Air Storage Garages

(1)  When a storage garage has all storeys constructed as open-air storeys, the exposing building face of such garage is permitted to have unlimited unprotected openings provided it has a limiting distance of not less than 3 m.

9.10.14.11.  Construction of Exposing Building Face

(1)  Except as permitted in Sentence (2) and Articles 9.10.14.12. to 9.10.14.16., each exposing building face and any exterior wall located above an exposing building face that encloses an attic or roof space shall be constructed in conformance with Table 9.10.14.11. and Subsection 9.10.8.

(2)  Cladding installed on exposing building faces and exterior walls located above exposing building faces that enclose an attic or roof space need not conform to “Type of Cladding Required” in Table 9.10.14.11. provided

(a)	the limiting distance is not less than 600 mm,

(b)	the exposing face is constructed with no unprotected openings, and

(c)	the cladding conforms to Clauses 9.10.14.12.(3)(a) to (d).

Table 9.10.14.11.

Minimum Construction Requirements for Exposing Building Faces

Forming Part of Article 9.10.14.11.

| Occupancy Classification of Building | Maximum Area of Unprotected Openings Permitted, % of Exposing Building Face Area | Minimum Required Fire-Resistance Rating | Type of Construction Required | Type of Cladding Required |
| --- | --- | --- | --- | --- |
| Residential, business and personal services, and low hazard industrial | 0 - 10 | 1 h | Noncombustible | Noncombustible |
|  | 11 - 25 | 1 h | Combustible or noncombustible | Noncombustible |
|  | 26 - < 100 | 45 min | Combustible or noncombustible | Combustible or noncombustible |
| Mercantile and medium hazard industrial | 0 - 10 | 2 h | Noncombustible | Noncombustible |
|  | 11 - 25 | 2 h | Combustible or noncombustible | Noncombustible |
|  | 26 - < 100 | 1 h | Combustible or noncombustible | Combustible or noncombustible |
| Column 1 | 2 | 3 | 4 | 5 |

9.10.14.12.  Exposing Building Face of Houses

(1)  For the purposes of application of this Article

(a)	the exposing building face is permitted to be divided into any number of portions and the fire-resistance rating, type of cladding and glazed area limitations is permitted to be determined individually for each portion based on the limiting distance for each portion so divided,

(b)	the exposing building face shall be taken as the projection of the exterior wall onto a vertical plane located so that no portion of the exterior wall of the building is between the vertical plane and the line to which the limiting distance is established in Clause (a), and

(c)	for the purpose of determining the actual percentage of glazed areas permitted in an exterior wall, the glazed area shall be projected onto the vertical plane established in Clause (b).

(2)  Except as required in Article 9.10.14.3. and as provided in Sentence (4), in buildings containing only dwelling units in which there is no dwelling unit above another dwelling unit, the requirements of Article 9.10.14.11. do not apply provided that the exposing building face

(a)	has a fire-resistance rating of not less than 45 min where the limiting distance is less than 1.2 m, and

(b)	is clad with non-combustible material where the limiting distance is less than 600 mm.

(3)  Cladding on the exposing building face described in Sentence (2) is permitted to be vinyl when the limiting distance is less than 600 mm provided the cladding

(a)	conforms to Subsection 9.27.13.,

(b)	is installed over sheathing paper and 12.7 mm gypsum sheathing,

(c)	has a flame spread rating not greater than 25 when tested in accordance with Sentence 3.1.12.1.(2), and

(d)	material thickness is not more than 2 mm exclusive of fasteners, joints and local reinforcements.

(4)  Glazed areas in the exposing building face referred to in Sentence (1)

(a)	shall not be permitted if the limiting distance is less than 1.2 m, and

(b)	shall be limited in conformance with the requirements for glazed areas in Table 9.10.14.1. where the limiting distance is 1.2 m or greater.

(5)  The required limiting distance for an exposing building face is permitted to be measured to a point beyond the property line that is not the centre line of a street, lane or public thoroughfare if

(a)	the owners of the properties on which the limiting distance is measured and the municipality enter into an agreement in which such owners agree that,

(i)	each owner covenants that, for the benefit of land owned by the other covenantors, the owner will not construct a building on his or her property unless the limiting distance for exposing building faces in respect of the proposed construction is measured in accordance with the agreement,

(ii)	the covenants contained in the agreement are intended to run with the lands, and the agreement shall be binding on the parties and their respective heirs, executors, administrators, successors and assigns,

(iii)	the agreement shall not be amended or deleted from title without the consent of the municipality, and

(iv)	they will comply with such other conditions as the municipality considers necessary, including indemnification of the municipality by the other parties, and

(b)	the agreement referred to in Clause (a) is registered against the title of the properties to which it applies.

(6)  Where an agreement referred to in Sentence (5) is registered against the title of a property, the limiting distance for exposing building faces in respect of the construction of any buildings on the property shall be measured to the point referred to in the agreement.

9.10.14.13.  Combustible Projections

(1)  Except for buildings containing 1 or 2 dwelling units only, combustible projections on the exterior of a wall that are more than 1 000 mm above ground level, such as balconies, platforms, canopies, eave projections and stairs, and that could expose an adjacent building to fire spread, shall not be permitted within

(a)	1 200 mm of a property line or the centreline of a public way, or

(b)	2 400 mm of a combustible projection on another building on the same property.

9.10.14.14.  Detached Garage or Accessory Building Serving One Dwelling Unit

(1)  Except as required in Article 9.10.14.3., the exposing building face of a garage or accessory building that serves one dwelling unit only and is detached from any building shall have a fire-resistance rating of at least 45 min, except that no fire-resistance rating is required where the limiting distance is 600 mm or greater.

(2)  The exterior cladding of detached garages or accessory buildings described in Sentence (1) is not required to be noncombustible regardless of the limiting distance.

(3)  The percentage of glazed areas permitted in the exposing building face of detached garages or accessory buildings described in Sentence (1) shall conform to the requirements for glazed areas in Table 9.10.14.1.

(4)  The requirements for limiting distance shall not apply between a detached garage or accessory building and a dwelling unit where

(a)	the detached garage or accessory building serves only one dwelling unit,

(b)	the detached garage or accessory building is located on the same property as that dwelling unit, and

(c)	the dwelling unit served by the detached garage or accessory building is the only major occupancy on the property.

9.10.14.15.  Heavy Timber and Steel Columns

(1)  Heavy timber and steel columns need not conform to the requirements of Article 9.10.14.11. provided the limiting distance is not less than 3 m.

9.10.14.16.  Low Fire Load Occupancies

(1)  Except as required in Article 9.10.14.3., in buildings of 1 storey in building height of noncombustible construction classified as low hazard industrial occupancy which are used only for low fire load occupancies such as power generating plants or plants for the manufacture or storage of noncombustible materials, non-loadbearing wall components need not have a minimum fire-resistance rating provided the limiting distance is 3 m or more.

9.10.15. Fire Stops

9.10.15.1.  Required Fire Stops in Concealed Spaces

(1)  Concealed spaces in interior walls, ceilings and crawl spaces shall be separated by fire stops from concealed spaces in exterior walls and attic or roof spaces.

(2)  Fire stops shall be provided at all interconnections between concealed vertical and horizontal spaces in interior coved ceilings, drop ceilings and soffits where the exposed construction materials within the concealed spaces have a surface flame-spread rating greater than 25.

(3)  Fire stops shall be provided at the top and bottom of each run of stairs where they pass through a floor containing concealed space in which the exposed construction materials within the space have a surface flame-spread rating greater than 25.

(4)  In unsprinklered buildings of combustible construction, every concealed space created by a ceiling, roof space or unoccupied attic space shall be separated by fire stops into compartments of not more than not more than 300 m2 in area where such space contains exposed construction materials having a surface flame-spread rating greater than 25.

(5)  No dimension of such space shall exceed 20 m.

(6)  Concealed spaces in mansard or gambrel style roofs, exterior cornices, balconies and canopies of combustible construction in which the exposed construction materials within the space have a surface flame-spread rating exceeding 25 shall have vertical fire stops at intervals of not more than 20 m and at points where such concealed spaces extend across the ends of required vertical fire separations.

9.10.15.2.  Required Fire Stops in Wall Assemblies

(1)  Except as permitted in Sentences (2) and (3), fire stops shall be provided to block off concealed spaces within wall assemblies, including spaces created by furring

(a)	at each floor level,

(b)	at each ceiling level where the ceiling contributes to part of the required fire-resistance rating, and

(c)	at other locations within the wall, so that the distance between fire stops does not exceed 20 m horizontally and 3 m vertically.

(2)  Fire stops required in Sentence (1) are not required provided

(a)	the width of the concealed wall space does not exceed 25 mm,

(b)	the exposed construction materials within the space are noncombustible, or

(c)	the exposed construction materials within the space, including insulation, but not including wiring, piping or similar services, have a flame-spread rating of not more than 25.

(3)  Fire stops required in Sentence (1) are not required provided the wall space is filled with insulation.

9.10.15.3.  Fire Stop Materials

(1)  Fire stops shall be constructed of not less than

(a)	0.38 mm sheet steel,

(b)	6 mm asbestos board,

(c)	12.7 mm gypsum wallboard,

(d)	12 mm plywood, OSB or waferboard, with joints having continuous support,

(e)	2 layers of 19 mm lumber with joints staggered,

(f)	38 mm lumber, or

(g)	materials conforming to Sentence 3.1.11.7.(1).

9.10.15.4.  Penetration of Fire Stops

(1)  Where fire stops are pierced by pipes, ducts or other elements, the effectiveness of the fire stops shall be maintained around such elements.

9.10.16. Flame Spread Limits

9.10.16.1.  Flame Spread Rating of Interior Surfaces

(1)  Except as otherwise provided in this Subsection, the exposed surface of every interior wall and ceiling, including skylights and glazing, shall have a surface flame-spread rating of not more than 150.

(2)  Except as permitted in Sentence (3), doors need not conform to Sentence (1) provided they have a surface flame-spread rating of not more than 200.

(3)  Doors within dwelling units, other than vehicle garage doors, need not conform to Sentences (1) and (2).

9.10.16.2.  Ceilings in Exits or Public Corridors

(1)  At least 90% of the exposed surface of every ceiling in an exit or unsprinklered ceiling in a public corridor shall have a surface flame-spread rating of not more than 25.

9.10.16.3.  Walls in Exits

(1)  Except as provided in Sentence (2), at least 90% of the exposed surfaces of every wall in an exit shall have a surface flame-spread rating of not more than 25.

(2)  At least 75% of the wall surface of a lobby used as an exit in Article 9.9.8.5. shall have a surface flame-spread rating of not more than 25.

9.10.16.4.  Exterior Exit Passageways

(1)  Where an exterior exit passageway provides the only means of egress from the rooms or suites it serves, the wall and ceiling finishes of that passageway, including the soffit beneath and the guard on the passageway, shall have a surface flame-spread rating of not more than 25, except that up to 10% of the total wall area and 10% of the total ceiling area is permitted to have a surface flame-spread rating of not more than 150.

9.10.16.5.  Walls in Public Corridors

(1)  At least 90% of the total wall surface in any unsprinklered public corridor shall have a surface flame-spread rating of not more than 75, or at least 90% of the upper half of such walls shall have a surface flame-spread rating of not more than 25.

9.10.16.6.  Calculation of Wall and Ceiling Areas

(1)  Skylights, glazing, combustible doors, and combustible light diffusers and lenses shall not be considered in the calculation of wall and ceiling areas in this Subsection.

9.10.16.7.  Corridors Containing an Occupancy

(1)  Where a public corridor or a corridor used by the public contains an occupancy, the interior finish materials used on the walls or ceiling of such occupancy shall have a surface flame-spread rating in conformance with that required for public corridors.

9.10.16.8.  Light Diffusers and Lenses

(1)  Light diffusers and lenses having flame-spread ratings that exceed those permitted for the ceiling finish, shall conform to the requirements of Sentence 3.1.13.4.(1).

9.10.16.9.  Combustible Skylights

(1)  Individual combustible skylights in corridors required to be separated from the remainder of the building by fire separations shall not exceed 1 m2 in area and shall be spaced not less than 1 200 mm apart.

9.10.16.10.  Protection of Foamed Plastics

(1)  Except as provided in Sentence (2), foamed plastics which form part of a wall or ceiling assembly in combustible construction shall be protected from adjacent space in the building other than adjacent concealed spaces within attic or roof spaces, crawl spaces, and wall assemblies, by

(a)	one of the finishes described in Subsections 9.29.4. to 9.29.9.,

(b)	sheet metal mechanically fastened to the supporting assembly independent of the insulation and having a thickness of not less than 0.38 mm and a melting point not below 650°C provided the building does not contain a Group C major occupancy, or

(c)	any thermal barrier that meets the requirements of Clause 3.1.5.11.(2)(e).

(2)  Foamed plastic insulation having a flame-spread rating of not more than 500 is permitted to be used in factory-assembled doors in storage garages serving buildings of residential occupancy provided that

(a)	the insulation is covered on the interior with a metallic foil,

(b)	the assembly has a surface flame-spread rating of not more than 200, and

(c)	the assembly incorporates no air spaces.

9.10.16.11.  Walls and Ceilings in Bathrooms

(1)  The interior finish of walls and ceilings in bathrooms within suites of residential occupancy shall have a surface flame-spread rating of not more than 200.

9.10.16.12.  Coverings or Linings of Ducts

(1)  Where a covering or a lining is used with a duct, such lining or covering shall have a flame-spread rating conforming to Part 6.

9.10.17. Alarm and Detection Systems

9.10.17.1.  Access Provided through a Firewall

(1)  Where access is provided through a firewall, the requirements in this Subsection shall apply to the floor areas on both sides of the firewall as if they were in the same building.

9.10.17.2.  Fire Alarm System Required

(1)  Except as provided in Sentence (2), a fire alarm system shall be installed

(a)	in every building that contains more than 3 storeys, including storeys below the first storey,

(b)	where the total occupant load exceeds 300, or

(c)	when the occupant load for any major occupancy in Table 9.10.17.2. is exceeded.

Table 9.10.17.2.

Maximum Occupant Load for Buildings without Fire Alarm Systems

Forming Part of Sentence 9.10.17.2.(1)

| Major Occupancy Classification | Occupant Load above which Fire Alarm System is required |
| --- | --- |
| Residential | 10 (sleeping accommodation) |
| Business and personal services, mercantile | 150 above or below the first storey |
| Low or medium hazard industrial | 75 above or below the first storey |
| Column 1 | 2 |

(2)  A fire alarm system is not required in a residential occupancy where an exit or public corridor serves not more than 4 suites or where each suite has direct access to an exterior exit facility leading to ground level.

9.10.17.3.  Rooms and Spaces Requiring Heat Detectors or Smoke Detectors

(1)  Where a fire alarm system is required, every public corridor in buildings of residential occupancy and every exit stair shaft shall be provided with smoke detectors.

(2)  Except as provided in Sentence (3), buildings required to have a fire alarm system shall be equipped with heat detectors or smoke detectors in storage rooms, service rooms, elevator shafts, chutes, janitors closets and any other rooms where hazardous substances are intended to be used or stored.

(3)  Except as required in Sentence (4), heat detectors and smoke detectors described in Sentence (2), are not required in dwelling units or in sprinklered buildings in which the sprinkler system is electrically supervised and equipped with a water flow alarm.

(4)  Where a fire alarm system is required in a hotel, heat detectors shall be installed in every room in a suite and in every room not located in a suite in a floor area containing a hotel other than washrooms within a suite, saunas, refrigerated areas and swimming pools.

9.10.17.4.  Smoke Detectors in Recirculating Air Handling Systems

(1)  Except for a recirculating air system serving not more than 1 dwelling unit, where a fire alarm system is required to be installed, every recirculating air handling system shall be designed to prevent the circulation of smoke upon a signal from a duct-type smoke detector where such system supplies more than one suite on the same floor or serves more than 1 storey.

9.10.17.5.  Portions of Buildings Considered as Separate Buildings

(1)  Except as provided in Sentence (2), where a vertical fire separation having a fire-resistance rating of at least 1 h separates a portion of a building from the remainder of the building and there are no openings through the fire separation other than those for piping, tubing, wiring and conduit, the requirements for fire alarm and detection systems is permitted to be applied to each portion so separated as if it were a separate building.

(2)  The permission in Sentence (1) to consider separated portions of a building as separate buildings does not apply to service rooms and storage rooms.

9.10.17.6.  Design and Installation Requirements

(1)  Fire alarm, fire detection and smoke detection devices and systems, and their installation, shall conform to Subsection 3.2.4.

9.10.17.7.  Reserved

9.10.17.8.  Open-Air Storage Garages

(1)  Except as required in Article 9.10.17.1., a fire alarm system is not required in a storage garage conforming to Article 3.2.2.60. provided there are no other occupancies in the building.

9.10.17.9.  Fire Alarm System in a Hotel

(1)  If a fire alarm system is required in a building containing a hotel, a single stage fire alarm system shall be provided.

9.10.18. Smoke Alarms

9.10.18.1.  Required Smoke Alarms

(1)  Smoke alarms conforming to CAN/ULC-S531, “Standard for Smoke Alarms” shall be installed in each dwelling unit and in each sleeping room not within a dwelling unit.

9.10.18.2.  Location of Smoke Alarms

(1)  Within dwelling units, sufficient smoke alarms shall be installed so that

(a)	there is at least one smoke alarm on each floor level, including basements, that is 900 mm or more above or below an adjacent floor level,

(b)	each bedroom is protected by a smoke alarm either inside the bedroom or, if outside, within 5 m, measured following corridors and doorways, of the bedroom door, and

(c)	the distance, measured following corridors and doorways, from any point on a floor level to a smoke alarm on the same level does not exceed 15 m.

(2)  Smoke alarms required in Article 9.10.18.1. and Sentence (1) shall be installed on or near the ceiling.

(3)  Smoke alarms required in Sentences (1) and (2) shall be audible within the bedrooms when the intervening doors are closed.

(4)  Smoke alarms required in Sentences (1) and (2) shall be installed in conformance with the manufacturers instructions.

9.10.18.3.  Power Supply

(1)  Except as permitted in Sentence (2), smoke alarms shall be installed by permanent connections to an electrical circuit and shall have no disconnect switch between the overcurrent circuit device and the smoke alarm.

(2)  Where the building is not supplied with electrical power, smoke alarms are permitted to be battery operated.

9.10.18.4.  Interconnection of Smoke Alarms

(1)  Where more than one smoke alarm is required in a dwelling unit, the smoke alarms shall be wired so that the activation of one alarm will cause all alarms within the dwelling unit to sound.

9.10.18.5.  Instructions for Maintenance and Repair

(1)  Where instructions are necessary to describe the maintenance and care required for smoke alarms to ensure continuing satisfactory performance, they shall be posted in a location where they will be readily available to the occupants for reference.

9.10.18.6.  Silencing of Alarm Noise

(1)  A manually operated device is permitted to be incorporated within the circuitry of a smoke alarm installed in a dwelling unit so that it will silence the signal emitted by the smoke alarm for a period of not more than 10 min, after which the smoke alarm will reset and again sound the alarm if the level of smoke in the vicinity is sufficient to reactuate the smoke alarm.

9.10.19. Fire-fighting

9.10.19.1.  Windows or Access Panels Required

(1)  Except as provided in Sentence (3), a window or access panel providing an opening not less than 1 100 mm high and 550 mm wide and having a sill height of not more than 900 mm above the floor shall be provided on the second and third storeys of every building in at least one wall facing on a street if such storeys are not sprinklered.

(2)  Access panels required in Sentence (1) shall be readily openable from both inside and outside or be glazed with plain glass.

(3)  Access panels required in Sentence (1) need not be provided in buildings containing only dwelling units where there is no dwelling unit above another dwelling unit.

9.10.19.2.  Access to Basements

(1)  Except in basements serving not more than one dwelling unit, each unsprinklered basement exceeding 25 m in length or width shall be provided with direct access to the outdoors to not less than one street.

(2)  Access required in Sentence (1) is permitted to be provided by a door, window or other means that provides an opening not less than 1 100 mm high and 550 mm wide, the sill height of which shall not be more than 900 mm above the floor.

(3)  Access required in Sentence (1) is also permitted to be provided by an interior stair accessible from the outdoors.

9.10.19.3.  Fire Department Access to Buildings

(1)  Access for fire department equipment shall be provided to each building by means of a street, private roadway or yard.

(2)  Where access to a building as required in Sentence (1) is provided by means of a roadway or yard, the design and location of such roadway or yard shall take into account connection with public thoroughfares, weight of fire fighting equipment, width of roadway, radius of curves, overhead clearance, location of fire hydrants, location of fire department connections and vehicular parking.

9.10.19.4.  Portable Extinguishers

(1)  Portable extinguishers shall be installed in all buildings, except within dwelling units, in conformance with the provisions of the Ontario Fire Code made under the Fire Protection and Prevention Act, 1997.

9.10.19.5.  Freeze Protection for Fire Protection Systems

(1)  Equipment forming part of a fire protection system that may be adversely affected by freezing temperatures and that is located in an unheated area shall be protected from freezing.

9.10.20. Fire Protection for Construction Camps

9.10.20.1.  Requirements for Construction Camps

(1)  Except as provided in Articles 9.10.20.2. to 9.10.20.9., camps for housing of workers shall conform to Subsections 9.10.1. to 9.10.19.

9.10.20.2.  Separation of Sleeping Rooms

(1)  Except for sleeping rooms within dwelling units, sleeping rooms in a building in a camp for housing of workers shall be separated from each other and from the remainder of the building by a fire separation having not less than a 30 min fire-resistance rating.

9.10.20.3.  Floor Assemblies Between the First and Second Storey

(1)  Except in a dwelling unit, a floor assembly in a building in a camp for housing of workers separating the first storey and the second storey shall be constructed as a fire separation having not less than a 30 min fire-resistance rating.

9.10.20.4.  Walkways Connecting Buildings

(1)  Walkways of combustible construction connecting buildings shall be separated from each connected building by a fire separation having not less than a 45 min fire-resistance rating.

9.10.20.5.  Spatial Separations

(1)  Buildings in a camp for housing of workers shall be separated from each other by a distance of not less than 10 m unless otherwise permitted in Subsection 9.10.14.

9.10.20.6.  Flame Spread Ratings

(1)  Except in dwelling units and except as provided in Sentence (2), the surface flame-spread rating of wall and ceiling surfaces in corridors and walkways, exclusive of doors, shall not exceed 25 over not less than 90 per cent of the exposed surface area and not more than 150 over the remaining surface area.

(2)  Except within dwelling units, corridors that provide access to exit from sleeping rooms and having a fire-resistance rating of not less than 45 min shall have a flame-spread rating conforming to the appropriate requirements in Subsection 9.10.16.

9.10.20.7.  Smoke Detectors

(1)  Except in dwelling units, corridors providing access to exit from sleeping rooms in every building in a camp for housing of workers with sleeping accommodation for more than 10 persons shall have a smoke detector connected to the building alarm system.

9.10.20.8.  Portable Fire Extinguishers

(1)  Each building in a camp for housing of workers shall be provided with portable fire extinguishers in conformance with the provisions of the Ontario Fire Code made under the Fire Protection and Prevention Act, 1997.

9.10.20.9.  Hose Stations

(1)  Every building in a camp for housing of workers providing sleeping accommodation for more than 30 persons shall be provided with a hose station that is protected from freezing and equipped with a hose of sufficient length so that every portion of the building is within the range of a hose stream.

(2)  Hose stations required in Sentence (1) shall be located near an exit.

(3)  Hoses referred to in Sentence (1) shall be not less than 19 mm inside diam and shall be connected to a central water supply or to a storage tank having a capacity of at least 4 500 L with a pumping system capable of supplying a flow of at least 5 L/s at a gauge pressure of 300 kPa.

9.10.21. Fire Protection for Gas and Electric Ranges

9.10.21.1.  Installation of Gas Ranges

(1)  Reserved

(2)  Clearances for gas ranges shall be not less than those provided in Articles 9.10.21.2. and 9.10.21.3.

9.10.21.2.  Vertical Clearances

(1)  Except as provided in Sentence (2), framing, finishes and cabinetry installed directly above the location of the range shall be not less than 750 mm above the level of the electric or gas range burners or elements.

(2)  The vertical clearance described in Sentence (1) for framing, finishes and cabinets located directly above the location of the range is permitted to be reduced to 600 mm above the level of the elements or burners provided the framing, finishes and cabinets

(a)	are noncombustible, or

(b)	are protected by

(i)	asbestos millboard not less than 6 mm thick, covered with sheet metal not less than 0.33 mm thick, or

(ii)	a metal hood with a 125 mm projection beyond the framing, finishes and cabinets.

9.10.21.3.  Horizontal Clearances

(1)  Except as provided in Sentences (2) to (3), combustible wall framing, finishes or cabinets within 450 mm of the area where the range is to be located shall be protected above the level of the heating elements by material providing fire resistance not less than that of a 9.5 mm thickness of gypsum board.

(2)  Counter-top splash boards or back plates which extend above the level of the heating elements need not be protected as described in Sentence (1).

(3)  Except for cabinetry described in Article 9.10.21.2., cabinetry located not less than 450 mm above the level of the heating elements need not be protected as described in Sentence (1).

Section 9.11. Sound Control

9.11.1. Sound Transmission Class Rating (Airborne Sound)

9.11.1.1.  Determination of Sound Class Transmission Rating

(1)  Sound transmission class ratings shall be determined in accordance with ASTM E413, “Classification for Rating Sound Insulation”, using results from measurements in accordance with

(a)	ASTM E 90, “Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions”, or

(b)	ASTM E 336, “Measurement of Airborne Sound Insulation in Buildings”.

9.11.2. Required Sound Control Locations (Airborne Sound)

9.11.2.1.  Minimum Sound Transmission Class Rating

(1)  Except as provided in Sentence (2), every dwelling unit and every suite in hotels and motels, shall be separated from every other space in a building in which noise may be generated, by a construction providing a sound transmission class rating of at least 50, measured in accordance with Subsection 9.11.1. or as listed in Tables 8.1 and 8.2 in the Supplementary Guidelines.

(2)  Where a dwelling unit is adjacent to an elevator shaft or a refuse chute, the separating construction shall have a sound transmission class rating of at least 55, measured in accordance with Subsection 9.11.1.or as listed in Tables 8.1 and 8.2 in the Supplementary Guidelines.

9.11.2.2.  Building Services in an Assembly

(1)  Building services located in an assembly required to have a sound transmission class rating shall be installed in a manner that will not decrease the required rating of the assembly.

Section 9.12. Excavation

9.12.1. General

9.12.1.1.  Removal of Topsoil and Organic Matter

(1)  The topsoil and vegetable matter in all unexcavated areas under a building shall be removed.

(2)  In localities where termite infestation is known to be a problem, all stumps, roots and other wood debris shall be removed from the soil to a depth of not less than 300 mm in unexcavated areas under a building.

(3)  The bottom of every excavation shall be free of all organic material.

9.12.1.2.  Standing Water

(1)  Excavations shall be kept free of standing water.

9.12.1.3.  Protection from Freezing

(1)  The bottom of excavations shall be kept from freezing throughout the entire construction period.

9.12.1.4.  Precautions During Excavation

(1)  Every excavation shall be undertaken in such a manner to prevent damage to adjacent property, existing structures, utilities, roads and sidewalks at all stages of construction.

(2)  Material shall not be placed nor shall equipment be operated or placed in or adjacent to an excavation in a manner that may endanger the integrity of the excavation or its supports.

9.12.2. Depth

9.12.2.1.  Excavation to Undisturbed Soil

(1)  Excavations for foundations shall extend to undisturbed soil.

9.12.2.2.  Minimum Depth of Foundations

(1)  Except as provided in Sentences (4) and (5), the minimum depth of foundations below finished ground level shall conform to Table 9.12.2.2.

Table 9.12.2.2.

Minimum Depths of Foundation

Forming Part of Sentence 9.12.2.2.(1)

| Type of Soil | Foundation containing heated Basement or Crawl Space(1) |  | Foundation Containing no Heated Space(2) |  |
| --- | --- | --- | --- | --- |
|  | Good Soil Drainage(3) | Poor Soil Drainage | Good Soil Drainage(3) | Poor Soil Drainage |
| Rock | No limit | No limit | No limit | No limit |
| Coarse grained soils | No limit | No limit | No limit | Below the depth of frost penetration |
| Silt | No limit | No limit | Below the depth of frost penetration | Below the depth of frost penetration |
| Clay or soils not clearly defined | 1.2 m | 1.2 m | 1.2 m but not less than the depth of frost penetration | 1.2 m but not less than the depth of frost penetration |
| Column 1 | 2 | 3 | 4 | 5 |

Notes to Table 9.12.2.2.:

(1)	 Foundation not insulated to reduce heat loss through the footings.

(2)	 Including foundations containing heated space insulated to reduce heat loss through the footings.

(3)	 To not less than the depth of frost penetration.

(2)  Where a foundation is insulated in a manner that will reduce the heat flow to the soil beneath the footings, the foundation depth shall conform to that required for foundations containing no heated space.

(3)  The minimum depth of foundations for exterior concrete steps with more than 2 risers shall conform to Sentences (1) to (5).

(4)  Concrete steps with 1 and 2 risers are permitted to be laid on ground level.

(5)  The foundation depths required in Sentence (1) are permitted to be decreased where experience with local soil conditions shows that lesser depths are satisfactory, or where the foundation is designed for lesser depths.

(6)  The foundation depths required in Sentence (1) do not apply to foundations for buildings of other than masonry or masonry veneer construction

(a)	whose superstructure conforms with the requirements of the deformation resistance test in CAN/CSA-Z240.2.1., “Structural Requirements for Mobile Homes”, or

(b)	used as accessory buildings of not more than 1 storey in building height and not more than 50 m2 in building area.

9.12.3. Backfill

9.12.3.1.  Placement of Backfill

(1)  Backfill shall be placed to avoid damaging the foundation wall, the drainage tile, drainage layer, externally applied thermal insulation, waterproofing and dampproofing of the wall.

9.12.3.2.  Grading of Backfill

(1)  Backfill shall be graded to prevent drainage towards the foundation after settling.

9.12.3.3.  Deleterious Debris and Boulders

(1)  Backfill within 600 mm of the foundation shall be free of deleterious debris and boulders larger than 250 mm diam.

9.12.3.4.  Lateral Support of Foundation Wall

(1)  Where the height of foundation wall is such that lateral support is required, or where the required concrete strength of the wall has not been reached, the wall shall be braced or laterally supported before backfilling.

9.12.4. Trenches Beneath Footings

9.12.4.1.  Compacting or Filling With Concrete

(1)  The soil in trenches beneath footings for sewers and watermains shall be compacted by tamping up to the level of the footing base, or shall be filled with concrete having a strength not less than 10 MPa to support the footing.

Section 9.13. Dampproofing, Waterproofing and Soil Gas Control

9.13.1. General

9.13.1.1.  Required Dampproofing

(1)  Except as provided in Article 9.13.1.2., where the exterior finished ground level is at a higher elevation than the ground level inside the foundation walls, exterior surfaces of foundation walls below ground level shall be dampproofed.

(2)  Except as provided in Sentence (3) and Article 9.13.1.2., floors-on-ground shall be dampproofed.

(3)  Floors in garages, floors in unenclosed portions of buildings and floors installed over granular fill in conformance with Article 9.16.2.1. need not be dampproofed.

(4)  Dampproofing in Sentence (1) is not required where the exterior surfaces of foundation walls below ground level are waterproofed.

9.13.1.2.  Required Waterproofing

(1)  Where hydrostatic pressure occurs, floors-on-ground and exterior surfaces of walls below ground level shall be waterproofed.

(2)  Roofs of underground structures shall be waterproofed to prevent the entry of water into the structure.

9.13.1.3.  Required Soil Gas Control

(1)  Except as provided in Sentence (2), all wall, roof and floor assemblies in contact with the ground shall be constructed to resist the leakage of soil gas from the ground into the building.

(2)  Construction to resist leakage of soil gas into the building is not required for

(a)	garages and unenclosed portions of buildings,

(b)	buildings constructed in areas where it can be demonstrated that soil gas does not constitute a hazard, or

(c)	buildings that contain a single dwelling unit and are constructed to provide for sub-floor depressurization in accordance with the Supplementary Guidelines.

9.13.1.4.  Standards for Application

(1)  The method of application of all bituminous waterproofing and dampproofing materials shall conform to

(a)	CAN/CGSB 37.3-M, “Application of Emulsified Asphalts for Dampproofing or Waterproofing”,

(b)	CGSB 37-GP-12Ma, “Application of Unfilled Cutback Asphalt for Dampproofing”, or

(c)	CAN/CGSB-37.22-M, “Application of Unfilled Cutback Tar Foundation Coating for Dampproofing”.

9.13.2. Material

9.13.2.1.  Material Standards

(1)  Except as otherwise specified in this Section, materials used for exterior dampproofing or waterproofing shall conform to

(a)	CAN/CGSB-37.1-M, “Chemical Emulsified Type, Emulsified Asphalt for Dampproofing”,

(b)	CAN/CGSB-37.2-M, “Emulsified Asphalt, Mineral Colloid Type, Unfilled, for Dampproofing and Waterproofing and for Roof Coatings”,

(c)	CGSB 37-GP-6Ma, “Asphalt, Cutback, Unfilled, for Dampproofing”,

(d)	CAN/CGSB-37.16-M, “Filled, Cutback Asphalt for Dampproofing and Waterproofing”,

(e)	CGSB 37-GP-56M, “Membrane, Modified, Bituminous, Prefabricated, and Reinforced for Roofing”,

(f)	CGSB 37-GP-18Ma, “Tar, Cutback, Unfilled, for Dampproofing”,

(g)	CAN/CGSB-51.34-M, “Vapour Barrier, Polyethylene Sheet, for Use in Building Construction”, or

(h)	CSA A123.4, “Bitumen for Use in Construction of Built-Up Roof Coverings and Dampproofing and Waterproofing Systems”.

(2)  Materials used to provide a barrier to soil gas ingress shall conform to CAN/CGSB-51.34-M, “Vapour Barrier, Polyethylene Sheet, for Use in Building Construction”.

9.13.3. Dampproofing of Walls

9.13.3.1.  Preparation of Surface

(1)  Unit masonry walls to be dampproofed shall be

(a)	parged on the exterior face below ground level with not less than 6 mm of mortar conforming to Section 9.20, and

(b)	coved over the footing when the first course of block is laid.

(2)  Concrete walls to be dampproofed shall have holes and recesses resulting from the removal of form ties sealed with cement mortar or dampproofing material.

9.13.3.2.  Application of Dampproofing Material

(1)  Dampproofing material shall be applied over the parging or concrete below ground level.

9.13.3.3.  Interior Dampproofing of Walls

(1)  Where a separate interior finish is applied to a concrete or unit masonry wall which is in contact with the soil, or where wood members are applied to such walls for the installation of insulation or finish, the interior surface of the foundation wall below ground level shall be dampproofed.

(2)  The dampproofing required in Sentence (1) shall extend from the basement floor and shall terminate at ground level.

(3)  No membrane or coating with a permeance less than 170 ng/(Pa.s.m2) shall be applied to the interior surface of the foundation wall above ground level between the insulation and the foundation wall.

9.13.3.4.  Dampproofing of Preserved Wood Foundation Walls

(1)  Preserved wood foundation walls shall be dampproofed as described in CAN3-S406, “Construction of Preserved Wood Foundations”.

9.13.4. Dampproofing of Floors-on-Ground

9.13.4.1.  Location of Dampproofing

(1)  When floors are dampproofed, the dampproofing shall be installed below the floor, except that where a separate floor is provided over a slab, the dampproofing is permitted to be applied to the top of the slab.

9.13.4.2.  Dampproofing below the Floor

(1)  When installed below the floor, dampproofing membranes shall consist of polyethylene not less than 0.15 mm thick, or type S roll roofing.

(2)  Joints in dampproofing membranes shall be lapped not less than 300 mm.

9.13.4.3.  Dampproofing above the Slab

(1)  When installed above the slab, dampproofing shall consist of not less than

(a)	2 mopped-on coats of bitumen,

(b)	0.05 mm polyethylene, or

(c)	other material providing equivalent performance.

9.13.5. Waterproofing of Walls

9.13.5.1.  Preparation of Surface

(1)  Except where it can be shown to be unnecessary, unit masonry walls to be waterproofed shall be parged on exterior surfaces below ground level with not less than 6 mm of mortar conforming to Section 9.20.

(2)  Concrete walls to be waterproofed shall have all holes and recesses resulting from removal of form ties sealed with mortar or waterproofing material.

9.13.5.2.  Application of Waterproofing Membranes

(1)  Concrete or unit masonry walls to be waterproofed shall be covered with not less than 2 layers of bitumen-saturated membrane, with each layer cemented in place with bitumen and coated over-all with a heavy coating of bitumen.

9.13.6. Waterproofing of Floors-on-Ground

9.13.6.1.  Floor Waterproofing System

(1)  Basement floors-on-ground to be waterproofed shall have a system of membrane waterproofing provided between 2 layers of concrete, each of which shall be not less than 75 mm thick, with the floor membrane mopped to the wall membrane to form a complete seal.

9.13.7. Soil Gas

9.13.7.1.  Soil Gas Control

(1)  Where methane or radon gases are known to be a problem, construction shall comply with the requirements for soil gas control in the Supplementary Guidelines.

Section 9.14. Drainage

9.14.1. Scope

9.14.1.1.  Application

(1)  This Section applies to subsurface drainage and to surface drainage.

9.14.1.2.  Crawl Spaces

(1)  Drainage for crawl spaces shall conform to Section 9.18.

9.14.1.3.  Floors-on-Ground

(1)  Drainage requirements beneath floors-on-ground shall conform to Section 9.16.

9.14.2. Foundation Drainage

9.14.2.1.  Foundation Wall Drainage

(1)  Unless it can be shown to be unnecessary, drainage shall be provided at the bottom of every foundation wall that contains the building interior.

(2)  Except as permitted in Sentences (4), (5) and (6), where the insulation on a foundation wall extends to more than 900 mm below the adjacent exterior ground level

(a)	a drainage layer shall be installed adjacent to the exterior surface of a foundation wall consisting of

(i)	not less than 19 mm mineral fibre insulation with a density of not less than 57 kg/m3, or

(ii)	not less than 100 mm of free draining granular material, or

(b)	a system shall be installed which can be shown to provide equivalent performance to that provided by the materials described in Clause (a).

(3)  Where mineral fibre insulation, crushed rock or other drainage layer medium is provided adjacent to the exterior surface of a foundation wall, it shall extend to the footing level and facilitate drainage of ground water to the foundation drainage system.

(4)  Except when the insulation provides the drainage layer required in Clause (2)(a), when exterior insulation is provided, the drainage layer shall be installed on the exterior face of the insulation.

(5)  The drainage layer required in Sentence (2) is not required

(a)	when the foundation wall is not required to be dampproofed, or

(b)	when the foundation wall is waterproofed.

(6)  The drainage layer in Sentence (1) is only required where the foundation wall is constructed after the day this Regulation comes into force.

(7)  Where drainage is required in Sentence (1), the drainage shall conform to Subsection 9.14.3. or 9.14.4.

9.14.3. Drainage Tile and Pipe

9.14.3.1.  Material Standards

(1)  Drain tile and drain pipe for foundation drainage shall conform to

(a)	ASTM C 4, “Clay Drain Tile”,

(b)	ASTM C 412M, “Concrete Drain Tile (Metric)”,

(c)	ASTM C 444M, “Perforated Concrete Pipe (Metric)”,

(d)	ASTM C 700, “Vitrified Clay Pipe, Extra Strength, Standard Strength and Perforated”,

(e)	CAN/CGSB-34.22-M, “Pipe, Asbestos-Cement, Drain”,

(f)	CAN/CSA-B182.1-M, “Plastic Drain and Sewer Pipe and Pipe Fittings”,

(g)	CAN3-G401, “Corrugated Steel Pipe Products”, or

(h)	BNQ 3624-115, “Thermo-Plastic Pipe — Flexible Corrugated Tubing and Fittings for Soil Drainage”.

9.14.3.2.  Minimum Size

(1)  Drain tile or pipe used for foundation drainage shall be not less than 100 mm in diam.

9.14.3.3.  Installation

(1)  Drain tile or pipe shall be laid on undisturbed or well-compacted soil so that the top of the tile or pipe is below the bottom of the floor slab or crawl space.

(2)  Drain tile or pipe with butt joints shall be laid with 6 mm to 10 mm open joints.

(3)  The top half of joints referred to in Sentence (2) shall be covered with sheathing paper, 0.10 mm polyethylene or No.15 asphalt or tar-saturated felt.

(4)  The top and sides of drain pipe or tile shall be covered with not less than 150 mm of crushed stone or other coarse clean granular material containing not more than 10% of material that will pass a 4 mm sieve.

9.14.4. Granular Drainage Layer

9.14.4.1.  Type of Granular Material

(1)  Granular material used to drain the bottom of a foundation shall consist of a continuous layer of crushed stone or other coarse clean granular material containing not more than 10% of material that will pass a 4 mm sieve.

9.14.4.2.  Installation

(1)  Granular material described in Article 9.14.4.1. shall be laid on undisturbed or compacted soil to a minimum depth of not less than 125 mm beneath the building and extend not less than 300 mm beyond the outside edge of the footings.

9.14.4.3.  Grading

(1)  The bottom of an excavation drained by a granular layer shall be graded so that the entire area described in Article 9.14.4.2. is drained to a sump conforming to Article 9.14.5.2.

9.14.4.4.  Wet Site Conditions

(1)  Where because of wet site conditions soil becomes mixed with the granular drainage material, sufficient additional granular material shall be provided so that the top 125 mm is kept free of soil.

9.14.5. Drainage Disposal

9.14.5.1.  Drainage Disposal

(1)  Foundation drains shall drain to a sewer, drainage ditch or dry well.

9.14.5.2.  Sump Pits

(1)  Where gravity drainage is not practical, a covered sump with an automatic pump shall be installed to discharge the water into a sewer, drainage ditch or dry well.

(2)  Covers for sump pits shall be designed to resist removal by children.

9.14.5.3.  Dry Wells

(1)  Dry wells are permitted to be used only when located in areas where the natural groundwater level is below the bottom of the dry well.

(2)  Dry wells shall be not less than 5 m from the building foundation and located so that drainage is away from the building.

9.14.6. Surface Drainage

9.14.6.1.  Surface Drainage

(1)  The building shall be located or the building site graded so that water will not accumulate at or near the building and will not adversely affect adjacent properties.

9.14.6.2.  Drainage away from Wells or Septic Disposal Beds

(1)  Surface drainage shall be directed away from the location of a water supply well or septic tank disposal bed.

9.14.6.3.  Window Wells

(1)  Every window well shall be drained to the footing level or other suitable location.

9.14.6.4.  Catch Basin

(1)  Where runoff water from a driveway is likely to accumulate or enter a garage, a catch basin shall be installed to provide adequate drainage.

9.14.6.5.  Downspouts

(1)  Downspouts shall conform to Article 9.26.18.2.

Section 9.15. Footings and Foundations

9.15.1. Scope

9.15.1.1.  Application

(1)  Except as provided in Articles 9.15.1.2. and 9.15.1.3. and 9.15.1.4., this Section applies to poured-in-place concrete or unit masonry foundation walls and poured-in-place concrete footings on soils with an allowable bearing pressure of 75 kPa or greater for buildings of wood frame or masonry construction.

(2)  Except as provided in Sentences (3) and (4), foundations for applications other than as described in Sentence (1) shall be designed in accordance with Section 9.4.

(3)  Where a foundation is erected on filled ground, peat or sensitive clay, the footing sizes shall be designed in conformance with Section 4.2.

(4)  For the purpose of Sentence (3), sensitive clay means the grain size of the majority of the particles is smaller than 0.002 mm, including leda clay.

9.15.1.2.  Permafrost

(1)  Buildings erected on permafrost shall have foundations designed by a designer competent in this field in accordance with the appropriate requirements of Part 4.

9.15.1.3.  Wood-Frame Foundations

(1)  Foundations of wood frame construction are permitted to be used provided they conform to Sentence (2) or (3).

(2)  Except as provided in Sentence (3), wood-frame foundations shall be designed in conformance with Part 4.

(3)  Wood-frame foundations conforming to CAN3-S406, “Construction of Preserved Wood Foundations” need not comply with Sentence (2) provided

(a)	they are supported on soil having an allowable bearing pressure of not less than 75 kPa, and

(b)	their configuration conforms with the design assumptions stated in the standard.

9.15.1.4.  Foundations for Deformation Resistant Buildings

(1)  Where the superstructure of a detached building conforms to the requirements of the deformation resistance test in CAN/CSA-Z240.2.1., “Structural Requirements for Mobile Homes”, the foundation is permitted to be constructed in conformance with CSA Z240.10.1., “Site Preparation, Foundation and Anchorage of Mobile Homes”.

9.15.2. General

9.15.2.1.  Concrete

(1)  Concrete shall conform to Section 9.3.

9.15.2.2.  Concrete Block

(1)  Concrete block shall conform to CAN/CSA-A165.1, “Concrete Masonry Units” and shall have a compressive strength over the net area of the block of not less than 15 MPa.

9.15.2.3.  Unit Masonry Construction

(1)  Mortar, mortar joints, corbelling and protection for unit masonry shall conform to Section 9.20.

9.15.2.4.  Pier Type Foundations

(1)  Where pier type foundations are used, the piers shall be designed to support the applied loads from the superstructure.

(2)  Where piers are used as a foundation system in a building of 1 storey in building height, the piers shall be installed to support the principal framing members and shall be spaced not more than 3.5 m apart along the framing, unless the piers and their footings are designed for larger spacings.

(3)  The height of piers described in Sentence (2) shall not exceed 3 times their least dimension at the base of the pier.

(4)  Where concrete block is used for piers described in Sentence (2), they shall be laid with cores placed vertically, and when the width of the building is 4.3 m or less, placed with their longest dimension at right angles to the longest dimension of the building.

9.15.3. Footings

9.15.3.1.  Footings Required

(1)  Footings shall be provided under walls, pilasters, columns, piers, fireplaces and chimneys that bear on soil or rock, except that footings are permitted to be omitted under piers or monolithic concrete walls if the safe loadbearing capacity of the soil or rock is not exceeded.

9.15.3.2.  Support of Footings

(1)  Footings shall rest on undisturbed soil, rock or compacted granular fill.

9.15.3.3.  Footing Sizes

(1)  Except as provided in Sentences (2) to (8) and in Articles 9.15.3.4. and 9.15.3.5., the minimum footing size shall be as shown in Table 9.15.3.3. provided the length of supported joists does not exceed 4.9 m and the design live load on any floor supported by the footing does not exceed 2.4 kPa.

(2)  Where the specified live load exceeds 2.4 kPa footings shall be designed in accordance with Section 4.2.

(3)  Except as provided in Sentence (4), where the span of the supported joists exceeds 4.9 m, footings shall be designed in accordance with Section 4.2.

(4)  Where the supported joist span exceeds 4.9 m, footing sizes are permitted to be determined according to the calculation provided in the Supplementary Guidelines.

(5)  The strip footing sizes for exterior walls shown in Table 9.15.3.3. shall be increased by 65 mm for each storey of masonry veneer over wood frame construction supported by the foundation wall.

(6)  The strip footing sizes for exterior walls shown in Table 9.15.3.3. shall be increased by 130 mm for each storey of masonry construction supported by the foundation wall.

(7)  The minimum strip footing sizes for interior walls shown in Table 9.15.3.3. shall be increased by 100 mm for each storey of masonry construction supported by the footing.

(8)  The footing area for column spacings other than shown in Table 9.15.3.3. shall be adjusted in proportion to the distance between columns.

Table 9.15.3.3.

Minimum Footing Sizes

Forming Part of Article 9.15.3.3.

| Floors Supported | Minimum Width of Strip Footings, mm |  | Minimum Footing Area for Columns Spaced 3 m o.c.(1) m2 |
| --- | --- | --- | --- |
|  | Supporting Exterior Walls | Supporting Interior Walls |  |
| 1 | 250(2) | 200(3) | 0.4 |
| 2 | 350(2) | 350(3) | 0.75 |
| 3 | 450(2) | 500(3) | 1.0 |
| Column 1 | 2 | 3 | 4 |

Notes to Table 9.15.3.3.:

(1)	 See Sentence 9.15.3.3.(8).

(2)	 See Sentences 9.15.3.3.(5) and (6).

(3)	 See Sentence 9.15.3.3.(7).

9.15.3.4.  High Water Table

(1)  Where a foundation rests on gravel, sand or silt in which the water table level is less than the width of the footings below the bearing surface, the footing width shall be not less than twice the width required by Article 9.15.3.3.

9.15.3.5.  Non-Loadbearing Walls

(1)  Footings for interior non-loadbearing masonry walls shall be not less than 200 mm wide for walls up to 5.5 m high and shall be increased by 100 mm for each additional 2 700 mm of height.

9.15.3.6.  Thickness

(1)  Footings shall be not less than 100 mm in thickness except when greater thicknesses are required because of the projection of the footing beyond the supported element.

9.15.3.7.  Footing Projection

(1)  The projection of an unreinforced footing beyond the supported element shall be not greater than the thickness of the footing.

9.15.3.8.  Step Footings

(1)  When step footings are used

(a)	the vertical rise between horizontal portions shall not exceed 600 mm, for firm soils and 400 mm for sand or gravel, and

(b)	the horizontal distance between risers shall be not less than 600 mm.

9.15.4. Foundation Walls

9.15.4.1.  Foundation Wall Thickness

(1)  Where average stable soils are encountered, the thickness of foundation walls subject to lateral earth pressure shall conform to Table 9.15.4.1. for walls not exceeding 2 500 mm in unsupported height.

Table 9.15.4.1.

Thickness of Foundation Walls

Forming Part of Sentence 9.15.4.1.(1)

| Type of Foundation wall | Minimum Wall Thickness, Mm | Maximum Height of Finish Ground Above Basement Floor or Crawl space Ground cover, m |  |
| --- | --- | --- | --- |
|  |  | Foundation Wall Laterally Unsupported at the Top(1) | Foundation Wall Laterally Supported at the Top(1) |
| Solid concrete 15 MPa min. strength | 150 | 0.80 | 1.50 |
|  | 200 | 1.20 | 2.15 |
|  | 250 | 1.40 | 2.30 |
|  | 300 | 1.50 | 2.30 |
| Solid concrete 20 MPa min. strength | 150 | 0.80 | 1.80 |
|  | 200 | 1.20 | 2.30 |
|  | 250 | 1.40 | 2.30 |
|  | 300 | 1.50 | 2.30 |
| Unit masonry | 140 | 0.60 | 0.80 |
|  | 190 | 0.90 | 1.20 |
|  | 240 | 1.20 | 1.80 |
|  | 290 | 1.40 | 2.20 |
| Column 1 | 2 | 3 | 4 |

Note to Table 9.15.4.1.:

(1)	 See Article 9.15.4.2.

9.15.4.2.  Lateral Support

(1)  For the purposes of Article 9.15.4.1., foundation walls shall be considered laterally supported at the top if such walls support solid masonry superstructure or if the floor joists are embedded in the top of the foundation walls.

(2)  Foundation walls shall also be considered to be supported at the top if the floor system is anchored to the top of the foundation walls with anchor bolts, in which case the joists are permitted to run either parallel or perpendicular to the foundation wall.

(3)  When a foundation wall contains an opening more than 1 200 mm in length or contains openings in more than 25% of its length, that portion of the wall beneath such openings shall be considered laterally unsupported, unless the wall around the opening is reinforced to withstand the earth pressure.

(4)  When the length of solid wall between windows is less than the average length of the windows, the combined length of such windows shall be considered as a single opening for the purposes of Sentence (3).

9.15.4.3.  Extension above Ground Level

(1)  Exterior foundation walls shall extend not less than 150 mm above finished ground level.

9.15.4.4.  Reduction in Thickness

(1)  Where the top of a foundation wall is reduced in thickness to permit the installation of floor joists, the reduced section shall be not more than 350 mm high and not less than 90 mm thick.

(2)  Where the top of a foundation wall is reduced in thickness to permit the installation of a masonry exterior facing, the reduced section shall be

(a)	not less than 90 mm thick, and

(b)	tied to the facing material with metal ties conforming to Sentence 9.20.9.4.(3) spaced not more than

(i)	200 mm o.c. vertically, and

(ii)	900 mm o.c. horizontally.

(3)  The space between wall and facing described in Sentence (2) shall be filled with mortar.

9.15.4.5.  Corbelling

(1)  Corbelling of masonry foundation walls supporting cavity walls shall conform to Article 9.20.12.2.

9.15.4.6.  Crack Control Joints

(1)  Crack control joints shall be provided in foundation walls more than 25 m long at intervals of not more than 15 m.

(2)  Joints required in Sentence (1) shall be designed to resist moisture penetration and shall be keyed to prevent relative displacement of the wall portions adjacent to the joint.

9.15.4.7.  Interior Masonry Walls

(1)  Interior masonry foundation walls not subject to lateral earth pressure shall conform to Section 9.20.

9.15.5. Joist and Beam Support

9.15.5.1.  Support of Floor Joists

(1)  Except as permitted in Sentence (2), foundation walls of hollow unit masonry supporting floor joists shall be

(a)	capped with not less than 50 mm of solid masonry or concrete, or

(b)	have the top course filled with mortar or concrete.

(2)  Capping required in Sentence (1) is permitted to be omitted

(a)	in localities where termites are not known to occur,

(b)	when the joists are supported on a wood plate not less than 38 mm by 89 mm, and

(c)	when the siding overlaps the foundation wall not less than 12 mm.

9.15.5.2.  Support of Beams

(1)  Not less than a 190 mm depth of solid masonry shall be provided beneath beams supported on masonry.

(2)  Where the beam referred to in Sentence (1) is supported below the top of the foundation walls, the ends of such beams shall be protected from the weather.

9.15.5.3.  Pilasters

(1)  Pilasters shall be provided under beams that frame into unit masonry foundation walls 140 mm or less in thickness.

(2)  Pilasters required in Sentence (1) shall be not less than 90 mm by 290 mm and shall be bonded or tied into the wall.

(3)  The top 200 mm of pilasters required in Sentence (1) shall be solid.

9.15.6. Parging and Finishing

9.15.6.1.  Foundation Walls below Ground

(1)  Concrete block foundation walls shall be parged on the exterior face below ground level as required in Section 9.13.

9.15.6.2.  Foundation Walls above Ground

(1)  Exterior surfaces of concrete block foundation walls above ground level shall have tooled joints, or shall be rendered, parged or otherwise suitably finished.

9.15.6.3.  Form Ties

(1)  All form ties shall be removed at least flush with the concrete surface.

Section 9.16. Slabs-on-Ground

9.16.1. Scope

9.16.1.1.  Application

(1)  This Section applies to floors supported on ground or granular fill which do not provide structural support for the superstructure.

9.16.1.2.  Structural Floor Slabs

(1)  Floors-on-ground that support loads from the superstructure shall be designed in conformance with Part 4.

9.16.1.3.  Required Floors-on-Ground

(1)  All spaces within dwelling units, except crawl spaces, shall be provided with a floor-on-ground, where

(a)	access is provided to the space, and

(b)	a floor supported by the structure is not provided.

9.16.1.4.  Dampproofing and Waterproofing

(1)  Dampproofing and waterproofing shall conform to Section 9.13.

9.16.2. Granular Material beneath Floors

9.16.2.1.  Required Installation of Granular Fill

(1)  Except as provided in Sentence (2), not less than 100 mm of coarse clean granular material containing not more than 10% of material that will pass a 4 mm sieve shall be placed beneath floors-on-ground.

(2)  Granular material need not be installed under

(a)	slabs in garages, carports or accessory buildings, or

(b)	buildings of industrial occupancy where the nature of the process contained therein permits or requires the use of large openings in the building envelope even during the winter.

(3)  Any fill beneath the top portion of coarse clean granular material referred to in Sentence (1) shall be compacted.

(4)  Any fill placed beneath slabs in garages other than coarse clean granular material as described in Sentence (1) shall be compacted to provide uniform support for the slab.

9.16.3. Drainage

9.16.3.1.  Control of Water Ingress

(1)  Except as provided in Article 9.16.3.2. or where it can be shown to be unnecessary, ingress of water underneath a floor-on-ground shall be prevented by grading or drainage.

9.16.3.2.  Hydrostatic Pressure

(1)  Where groundwater levels may cause hydrostatic pressure beneath a floor-on-ground, the floor-on-ground shall be

(a)	a cast in place concrete slab, and

(b)	designed to resist such pressures.

9.16.3.3.  Floor Drains

(1)  When floor drains are required, the floor surface shall be sloped so that no water can accumulate.

9.16.4. Concrete

9.16.4.1.  Floor Finish

(1)  The finished surface of concrete floor slabs shall be trowelled smooth and even.

(2)  Dry cement shall not be added to the floor surfaces to absorb surplus water.

9.16.4.2.  Compressive Strength

(1)  Where dampproofing is not provided the concrete used for floors-on-ground shall have a compressive strength of not less than 25 MPa after 28 days.

(2)  Where dampproofing is provided as described in Subsection 9.13.6., the concrete used for floors-on-ground shall have a compressive strength of not less than 15 MPa after 28 days.

9.16.4.3.  Topping Course

(1)  Where a topping course is provided for a concrete floor slab, it shall consist of 1 part cement to 2.5 parts clean, well graded sand by volume, with a water/cement ratio approximately equal to that of the base slab.

(2)  When concrete topping is provided it shall not be less than 20 mm thick.

9.16.4.4.  Thickness

(1)  Concrete slabs shall be not less than 75 mm thick exclusive of concrete topping.

9.16.4.5.  Bond Break

(1)  A bond-breaking material shall be placed between the slab and footings or rock.

9.16.5. Wood

9.16.5.1.  Wood Frame Floors

(1)  Floors-on-ground constructed of wood shall conform to CAN/CSA-S406, “Construction of Preserved Wood Foundations”.

Section 9.17. Columns

9.17.1. Scope

9.17.1.1.  Application

(1)  This Section applies to columns used to support carport roofs, and beams carrying loads from not more than 2 wood-frame floors where the length of joists carried by such beams does not exceed 5 m and the live load on any floor does not exceed 2.4 kPa.

(2)  Columns for applications other than as described in Sentence (1) shall be designed in accordance with Part 4.

9.17.2. General

9.17.2.1.  Location

(1)  Columns shall be centrally located on a footing conforming to Section 9.15.

9.17.2.2.  Fastening

(1)  Columns shall be securely fastened to the supported member to prevent lateral movement.

9.17.3. Steel Columns

9.17.3.1.  Size and Thickness

(1)  Except as permitted in Sentence (2), steel pipe columns shall have an outside diameter of not less than 73 mm and a wall thickness of not less than 4.76 mm.

(2)  Columns of sizes other than as specified in Sentence (1) are permitted to be used where the loadbearing capacities are shown to be adequate.

9.17.3.2.  End Bearing Plates

(1)  Except as permitted in Sentence (2), steel columns shall be fitted with not less than 100 mm by 100 mm by 6.35 mm thick steel plates at each end, and where the column supports a wooden beam, the top plate shall extend across the full width of the beam.

(2)  The top plate required in Sentence (1) need not be provided where a column supports a steel beam and provision is made for the attachment of the column to the beam.

9.17.3.3.  Paint

(1)  Steel columns shall be treated on the outside surface with not less than 1 coat of rust-inhibitive paint.

9.17.3.4.  Adjustable Steel Columns

(1)  Adjustable steel columns shall conform to CAN/CGSB-7.2-M, “Adjustable Steel Columns”.

9.17.4. Wood Columns

9.17.4.1.  Column Sizes

(1)  The width or diameter of a wood column shall be not less than the width of the supported member.

(2)  Except as provided in Article 9.35.4.2., columns shall be not less than 184 mm for round columns and 140 mm by 140 mm for rectangular columns, unless calculations are provided to show that lesser sizes are adequate.

9.17.4.2.  Materials

(1)  Wood columns shall be either solid, glue-laminated or built-up.

(2)  Built-up columns shall consist of not less than 38 mm thick full-length members

(a)	bolted together with not less than 9.52 mm diam bolts spaced not more than 450 mm o.c., or

(b)	nailed together with not less than 76 mm nails spaced not more than 300 mm o.c.

(3)  Glued-laminated columns shall conform to Section 4.3.

9.17.4.3.  Columns in Contact with Concrete

(1)  Wood columns shall be separated from concrete in contact with the ground by 0.05 mm polyethylene film or Type S roll roofing.

9.17.4.4.  Wood Column Termite Protection

(1)  Where termites are known to exist, exterior wood columns such as porch supports shall be

(a)	pressure treated with a chemical that is toxic to such termites, in accordance with Article 9.3.2.9., or

(b)	supported on non-cellulosic material extending not less than 150 mm above grade and located not less than 50 mm from the exterior wall of an adjacent building.

9.17.5. Unit Masonry Columns

9.17.5.1.  Materials

(1)  Unit masonry columns shall be built of masonry units

(a)	conforming to CAN/CSA-A165.1, “Concrete Masonry Units”, and

(b)	have a compressive strength over the net area of the block of not less than 15 MPa.

9.17.5.2.  Sizes

(1)  Unit masonry columns shall be not less than 290 mm by 290 mm or 240 mm by 380 mm in size.

9.17.6. Solid Concrete Columns

9.17.6.1.  Materials

(1)  Concrete shall conform to Section 9.3.

9.17.6.2.  Sizes

(1)  Concrete columns shall be not less than 200 mm by 200 mm for rectangular columns and 230 mm diam for circular columns.

Section 9.18. Crawl Spaces

9.18.1. General

9.18.1.1.  Application

(1)  In this Section a crawl space refers to an enclosed space between the underside of a floor assembly and the ground cover directly below, with a clearance less than 1 800 mm in height.

9.18.1.2.  Foundations

(1)  Foundations enclosing crawl spaces shall conform to Section 9.15.

9.18.1.3.  Heated and Unheated Crawl Spaces

(1)  Crawl spaces shall be considered to be heated where the space

(a)	is used as a hot air plenum,

(b)	contains heating ducts or heating pipes that are not sealed and insulated to minimize heat loss to the space, or

(c)	is not separated from heated space in accordance with Section 9.25.

(2)  Heating of heated crawl spaces shall conform to Section 9.33.

(3)  Insulation, an air barrier system and a vapour barrier shall be installed in the walls of heated crawl spaces in accordance with Section 9.25.

9.18.2. Access

9.18.2.1.  Access Openings

(1)  An access opening of not less than 500 mm by 700 mm shall be provided to each crawl space where the crawl space serves a single dwelling unit, and not less than 550 mm by 900 mm for other crawl spaces.

(2)  Access openings shall be fitted with a door or hatch, except when the crawl space is heated and the access opening into the crawl space is from the adjacent heated space.

9.18.3. Ventilation

9.18.3.1.  Ventilation of Unheated Crawl Spaces

(1)  Unheated crawl spaces shall be ventilated by natural or mechanical means.

(2)  Where an unheated crawl space is ventilated by natural means, ventilation shall be provided to the outside air by not less than 0.1 m2 of unobstructed vent area for every 50 m2 of floor area.

(3)  Vents shall be

(a)	uniformly distributed on opposite sides of the building, and

(b)	designed to prevent the entry of snow, rain and insects.

9.18.3.2.  Ventilation of Heated Crawl Spaces

(1)  Heated crawl spaces shall be ventilated in accordance with Section 9.32.

9.18.4. Clearance

9.18.4.1.  Access Way to Services

(1)  Where equipment requiring service such as plumbing cleanouts, traps and burners is located in crawl spaces, an access way with a height and width of not less than 600 mm shall be provided from the access door to the equipment and for a distance of 900 mm on the side or sides of the equipment to be serviced.

9.18.5. Drainage

9.18.5.1.  Drainage

(1)  Except where it can be shown to be unnecessary, the ingress of water into a crawl space shall be controlled by grading or drainage.

(2)  Drainage of foundation walls shall conform to Article 9.14.2.1.

(3)  Drainage of the ground cover or floor-on-ground in the crawl space shall conform to Article 9.16.3.1.

(4)  Drains shall conform to Section 9.14.

9.18.6. Ground Cover

9.18.6.1.  Ground Cover in Unheated Crawl Spaces

(1)  Where a crawl space is unheated, a ground cover shall be provided consisting of not less than

(a)	50 mm of asphalt paving material,

(b)	100 mm of 15 MPa Portland cement concrete,

(c)	Type S roll roofing, or

(d)	0.10 mm polyethylene.

(2)  Joints in sheet-type ground cover required in Sentence (1) shall be lapped not less than 100 mm and weighted down.

9.18.6.2.  Ground Cover in Heated Crawl Spaces

(1)  Where a crawl space is heated, a ground cover consisting of not less than 0.15 mm polyethylene sheet conforming to CAN/CGSB-51.34-M, “Vapour Barrier, Polyethylene Sheet, for Use in Building Construction” shall be provided.

(2)  Joints in the ground cover required in Sentence (1) shall be lapped not less than 300 mm, and

(a)	sealed and weighted down, or

(b)	covered with a concrete skim coat not less than 50 mm thick.

(3)  The perimeter of the ground cover required in Sentence (1) shall be sealed to the foundation wall.

9.18.7. Fire Protection

9.18.7.1.  Crawl Spaces as Warm Air Plenums

(1)  Only Crawl spaces under 1-storey portions of dwelling units shall be used as warm-air plenums.

(2)  Enclosing material in crawl spaces described in Sentence (1) including insulation shall have a surface flame-spread rating not greater than 150.

(3)  Combustible ground cover used as enclosing material in Sentence (2) shall be covered with noncombustible material.

Section 9.19. Roof Spaces

9.19.1. Venting

9.19.1.1.  Required Venting

(1)  Except where it can be shown to be unnecessary, where insulation is installed between a ceiling and the underside of the roof sheathing, a space shall be provided between the insulation and the sheathing, and vents shall be installed to permit the movement of air from the space to the exterior.

9.19.1.2.  Vent Requirements

(1)  Except as provided in Sentence (2), the unobstructed vent area shall be not less than 1/300 of the insulated ceiling area.

(2)  Where the roof slope is less than 1 in 6 or in roofs that are constructed with roof joists, the unobstructed vent area shall be not less than 1/150 of the insulated ceiling area.

(3)  Required vents are permitted to be roof type, eave type, gable-end type or any combination thereof, and shall be distributed

(a)	uniformly on opposite sides of the building,

(b)	with not less than 25% of the required openings located at the top of the space, and

(c)	with not less than 25% of the required openings located at the bottom of the space.

(4)  Except where each roof joist space referred to in Sentence (2) is separately vented, roof joist spaces shall be interconnected by installing purlins not less than 38 mm by 38 mm on the top of the roof joists.

(5)  Vents shall be designed to prevent the entry of rain, snow and insects.

(6)  The unobstructed vent area required in Sentences (1) and (2) shall be determined in conformance with CAN3-A93, “Natural Airflow Ventilators for Buildings”.

9.19.1.3.  Clearances

(1)  Where venting is provided to a roof joist space, not less than 63 mm of space shall be provided between the top of the insulation and the underside of the roof sheathing.

(2)  Ceiling insulation shall be installed in a manner which will not restrict a free flow of air through roof vents or through any portion of the attic or roof space.

9.19.1.4.  Mansard or Gambrel Roof

(1)  The lower portion of a mansard or gambrel style roof need not be ventilated.

(2)  The upper portion of roofs described in Sentence (1) shall be ventilated in conformance with the requirements in Articles 9.19.1.1. to 9.19.1.3.

9.19.2. Access

9.19.2.1.  Access

(1)  Every attic or roof space shall be provided with an access hatch where the attic or roof space measures

(a)	not less than 10 m2, in area,

(b)	not less than 1 000 mm in length or width, and

(c)	not less than 600 mm in height over at least the area described in Clauses (a) and (b).

(2)  The hatch required in Sentence (1) shall be not less than 550 mm by 900 mm except that, where the hatch serves not more than one dwelling unit, the hatch is permitted to be reduced to 500 mm by 700 mm.

(3)  Hatchways to attic or roof spaces shall be fitted with doors or covers.

Section 9.20. Above-Grade Masonry

9.20.1. Scope

9.20.1.1.  Application

(1)  Except as provided in Article 9.20.1.2., this Section applies to unreinforced masonry and masonry veneer in which the wall height above the foundation wall does not exceed 11 m, and in which the roof or floor system above the first storey is not of concrete construction.

(2)  For buildings other than described in Sentence (1), or where the masonry is designed on the basis of design loads and allowable stresses, Subsection 4.3.2. shall apply.

9.20.1.2.  Earthquake Reinforcement

(1)  In velocity- or acceleration-related seismic zones, of 4 or greater, loadbearing elements of masonry buildings more than 1 storey in building height shall be reinforced with at least the minimum amount of reinforcement as required in Subsection 9.20.15.

(2)  In velocity- or acceleration-related seismic zones, of 2 and 3, loadbearing elements of masonry buildings 3 storeys in building height shall be reinforced with at least the minimum amount of reinforcement as required in Subsection 9.20.15.

9.20.2. Masonry Units

9.20.2.1.  Masonry Unit Standards

(1)  Masonry units shall comply with

(a)	ASTM C 126, “Ceramic Glazed Structural Clay Facing Tile, Facing Brick, and Solid Masonry Units”,

(b)	ASTM C 212, “Structural Clay Facing Tile”,

(c)	CAN/CSA-A82.1, “Burned Clay Brick (Solid Masonry Units Made from Clay or Shale)”,

(d)	CSA A82.3-M, “Calcium Silicate (Sand-Lime) Building Brick”,

(e)	CSA A82.4-M, “Structural Clay Load-Bearing Wall Tile”,

(f)	CSA A82.5-M, “Structural Clay Non-Load-Bearing Tile”,

(g)	CAN3 A82.8-M, “Hollow Clay Brick”,

(h)	CAN/CSA-A165.1, “Concrete Masonry Units”,

(i)	CAN/CSA-A165.2, “Concrete Brick Masonry Units”,

(j)	CAN/CSA-A165.3, “Prefaced Concrete Masonry Units”, or

(k)	CAN3-A165.4-M, “Autoclaved Cellular Units”.

9.20.2.2.  Used Brick

(1)  Used bricks shall be free of old mortar, soot or other surface coating and shall conform to Article 9.20.2.1.

9.20.2.3.  Glass Blocks

(1)  Glass blocks shall not be used as loadbearing units or in the construction of fireplaces or chimneys.

9.20.2.4.  Cellular Concrete

(1)  Masonry made with cellular concrete shall not be used in contact with the soil or exposed to the weather.

9.20.2.5.  Stone

(1)  Stone shall be sound and durable.

9.20.2.6.  Concrete Units Exposed to the Weather

(1)  Concrete units exposed to the weather shall have weight and water absorption characteristics conforming to Classes A, B or C, described in CAN/CSA-A165.1, “Concrete Masonry Units”.

(2)  Where cellular concrete blocks are used in situations described in Sentence (1), allowance shall be made in the design for the shrinkage characteristics of the units to be used.

9.20.2.7.  Compressive Strength

(1)  The compressive strength of masonry units shall conform to Table 9.20.2.7.

Table 9.20.2.7.

Compressive Strength of Concrete Masonry Units

Forming Part of Sentence 9.20.2.7.(1)

| Type of Unit | Minimum Compressive Strength Over Net Area, Mpa |  |
| --- | --- | --- |
|  | Exposed to Weather | Not Exposed to Weather |
| Solid or hollow concrete units | 15 | 10 |
| Solid loadbearing cellular units | Not permitted | 5 |
| Solid non-loadbearing cellular units | Not permitted | 2 |
| Column 1 | 2 | 3 |

9.20.3. Mortar

9.20.3.1.  Mortar Materials

(1)  Cementitious materials and aggregates for mortar shall comply with

(a)	ASTM C 5, “Quicklime for Structural Purposes”,

(b)	ASTM C 207, “Hydrated Lime for Masonry Purposes”,

(c)	CAN/CSA-A5, “Portland Cement”,

(d)	CAN/CSA-A8, “Masonry Cement”, or

(e)	CSA A82.56-M, “Aggregate for Masonry Mortar”.

(2)  Water and aggregate shall be clean and free of significant amounts of deleterious materials.

(3)  Lime used in mortar shall be hydrated.

(4)  If lime putty is used in mortar, it shall be made by slaking quicklime in water for not less than 24 h or soaking hydrated lime in water for not less than 12 h.

9.20.3.2.  Mortar Mixes

(1)  Except as provided in Sentences (3) and (4), mortar mixes shall conform to Table 9.20.3.2.

(2)  Mortar containing portland cement shall not be used later than 2.5 h after mixing.

(3)  Mortar for sand-lime brick and concrete brick is permitted to consist of 1 part masonry cement to not less than 3 or not more than 3.5 parts of aggregate by volume in addition to those mixes permitted in Table 9.20.3.2.

Table 9.20.3.2.

Mortar Mix Proportions (By Volume)

Forming Part of Sentence 9.20.3.2.(1)

| Permissible Use of Mortar | Portland Cement | Masonry Cement | Lime | Aggregate |
| --- | --- | --- | --- | --- |
| All locations but not for use with sand-lime or concrete brick | 0.5 to 1 | 1 | — | Not less than 2.25 and not more than 3 times the sum of the volumes of the cement and the lime |
|  | 1 | — | 0.25 to 0.5 |  |
| All locations except foundation walls and piers, but not for use with sand-lime or concrete brick | — | 1 | — |  |
|  | 1 | — | 0.5 to 1.25 |  |
| All locations except loadbearing walls of hollow units, parapet walls and chimneys | 1 | — | 1.25 to 2.5 |  |
| All non-loadbearing interior walls and all loadbearing walls of solid units, except foundation walls, parapet walls and chimneys | 1 | — | 2.25 to 4 |  |
|  | — | — | 1 |  |
| Column 1 | 2 | 3 | 4 | 5 |

(4)  Mortar for glass block shall consist of 1 part portland cement and 1 part hydrated lime to not more than 4 parts aggregate by volume.

9.20.4. Mortar Joints

9.20.4.1.  Thickness

(1)  Except as provided in Sentence (2), mortar joint thickness for burned clay brick and concrete masonry units shall be 10 mm.

(2)  Permitted tolerances in head and bed joints shall be −5 mm to +10 mm.

9.20.4.2.  Solid Masonry Units

(1)  Solid masonry units shall be laid with full head and bed joints.

9.20.4.3.  Hollow Masonry Units

(1)  Hollow masonry units shall be laid with mortar applied to head and bed joints of both inner and outer face shells.

9.20.5. Masonry Support

9.20.5.1.  Masonry Support

(1)  All masonry shall be supported on masonry, concrete or steel, except that masonry veneer walls are permitted to be supported on foundations of wood frame constructed in conformance with Sentence 9.15.1.3.(3).

(2)  Every masonry wall shall be at least as thick as the wall it supports, except as otherwise permitted in Article 9.20.12.2.

9.20.5.2.  Lintels or Arches

(1)  Masonry over openings shall be supported by steel, reinforced concrete lintels or masonry arches designed to support the imposed loads.

(2)  Except as permitted in Sentence (3), steel angle lintels supporting masonry above openings shall conform to Table 9.20.5.2.A.

(3)  Steel angle lintels supporting masonry veneer above openings shall conform to Table 9.20.5.2.B.

(4)  Steel lintels described in Sentences (2) and (3) shall have even and level bearing and shall have not less than 150 mm length of bearing at end supports.

(5)  Steel angle lintels supporting masonry shall be prime painted or otherwise protected from corrosion.

Table 9.20.5.2.A.

Loose Steel Lintels for Masonry — No. & Size of Angles Required(7)

Forming Part of Sentence 9.20.5.2.(2)

| Clear Span(1)(3) | Exterior Angles |  | Wall Thickness, Mm | Interior Angles |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | for Brick | for Stone |  | Maximum Floor Loads per Metre of Span in Newtons(2)(4)(5) |  |  |  |  |  |  |
|  | 100 mm | 100 mm + 50 mm stone facing |  |  |  |  |  |  |  |  |
|  | No Floor Load |  |  | None | 3 650 | 7 300 | 10 950 | 14 600 | 18 250 | 21 900 |
| 1 200 mm | L-90 x 90 | L-125 x 90 | 203 | L-90 | L-90 | L-90 | L-100 | L-125 | L-125 | L-125 |
|  |  |  |  | x 90 | x 90 | x 90 | x 90 | x 90 | x 90 | x 90 |
|  |  |  |  | x 6 | x 6 | x 8 | x 8 | x 8 | x 10 | x 13 |
|  |  |  | 305 | 2Ls-90 | 2Ls-90 | 2Ls-90 | 2Ls-90 | 2Ls-90 | 2Ls-100 | 2Ls-100 |
| or less | 6 | 8 |  | x 90 | x 90 | x 90 | x 90 | x 90 | x 90 | x 90 |
|  |  |  |  | x 8 | x 8 | x 8 | x 8 | x 8 | x 8 | x 8 |
| 1 500 mm | L-90 x 90 | L-125 x 90 | 203 | L-90 | L-90 | L-125 | L-125 | L-125 | L-150 | — |
|  |  |  |  | x 90 | x 90 | x 90 | x 90 | x 90 | x 90 | — |
|  |  |  |  | x 8 | x 8 | x 8 | x 10 | x 13 | x 10 | — |
|  |  |  | 305 | 2Ls-90 | 2Ls-90 | 2Ls-90 | 2Ls-125 | 2Ls-125 | 2Ls-125 | 2Ls-125 |
|  | 8 | 8 |  | x 90 | x 90 | x 90 | x 90 | x 90 | x 90 | x 90 |
|  |  |  |  | x 8 | x 8 | x 8 | x 8 | x 8 | x 8 | x 10 |
| 1 800 mm | L-100 x 90 | L-125 x 125 | 203 | L-100 | L-125 | L-125 | L-150 |  |  |  |
|  |  |  |  | x 90 | x 90 | x 90 | x 100 |  |  |  |
|  |  |  |  | x 8 | x 8 | x 8 | x 10 |  |  |  |
|  |  |  | 305 | 2Ls-100 | 2Ls-100 | 2Ls-125 | 2Ls-125 | 2Ls-125 | 2Ls-150 | 2Ls-150 |
|  | 8 | 8 |  | x 90 | x 90 | x 90 | x 90 | x 90 | x 100 | x 100 |
|  |  |  |  | x 8 | x 8 | x 8 | x 8 | x 10 | x 10 | x 10 |
| 2 100 mm | L-100 x 90 | L-125 x 125 | 203 | L-100 | L-125 | L-150 |  |  |  |  |
|  |  |  |  | x 90 | x 90 | x 100 |  |  |  |  |
|  |  |  |  | x 8 | x 10 | x 10 |  |  |  |  |
|  |  |  | 305 | 2Ls-100 | 2Ls-125 | 2Ls-125 | 2Ls-150 | 2Ls-150 |  |  |
|  | 8 | 8 |  | x 90 | x 90 | x 90 | x 100 | x 100 |  |  |
|  |  |  |  | x 8 | x 10 | x 10 | x 10 | x 10 |  |  |
| 2 400 mm | L-125 x 90 | L-125 x 125 | 203 | L-125 | L-150 |  |  |  |  |  |
|  |  |  |  | x 90 | x 100 |  |  |  |  |  |
|  |  |  |  | x 8 | x 10 |  |  |  |  |  |
|  |  |  | 305 | 2Ls-125 | 2Ls-125 | 2Ls-150 |  |  |  |  |
|  | 8 | 8 |  | x 90 | x 90 | x 100 |  |  |  |  |
|  |  |  |  | x 8 | x 13 | x 10 |  |  |  |  |
| 2 700 mm | L-125 x 90 | L-125 x 125 | 203 | L-125 |  |  |  |  |  |  |
|  |  |  |  | x 90 |  |  |  |  |  |  |
|  |  |  |  | x 10 |  |  |  |  |  |  |
|  |  |  | 305 | 2Ls-125 | 2Ls-150 |  |  |  |  |  |
|  | 10 | 10 |  | x 150 | x 100 |  |  |  |  |  |
|  |  |  |  | x 10 | x 10 |  |  |  |  |  |
| 3 000 mm | L-150 | L-125 x 125 | 203 | L-150 |  |  |  |  |  |  |
|  |  |  |  | x 100 |  |  |  |  |  |  |
|  |  |  |  | x 10 |  |  |  |  |  |  |
|  |  |  | 305 | 2Ls-150 |  |  |  |  |  |  |
|  | 100 x 10 | 13 |  | x 100 |  |  |  |  |  |  |
|  |  |  |  | x 10 |  |  |  |  |  |  |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |

Notes to Table 9.20.5.2.A.

(1)	 See Sentence 9.20.5.2.(4)

(2)	 Omit floor load in lintel when distance to bottom of floor construction is greater than width of opening.

(3)	 Interior and exterior angles in 200 mm walls and interior angles in 300 mm walls are bolted together when clear span is over 1 800 mm.

(4)	 When masonry lighter than brick is used over interior angles floor load may be increased by the difference in weight per square metre times the width of the opening.  Not generally available.

(5)	 Interior angles have been designed for floor load plus brick masonry of height equal to width of opening.

(6)	 fs = 138 MPa.

Deflection maximum = 1/700 span.

(7)	 The figures in the Table indicating wall thickness and angle cross-section are in mm.

Table 9.20.5.2.B.

Maximum Allowable Spans for Steel Lintels Supporting Masonry Veneer, m

Forming Part of Sentence 9.20.5.2.(3)

| Minimum Angle Size, mm |  |  | 70 mm Brick | 90 mm Brick | 100 mm Stone |
| --- | --- | --- | --- | --- | --- |
| Vertical Leg | Horizontal Leg | Thickness |  |  |  |
| 90 | 75 | 6 | 2.55 | — | — |
| 90 | 90 | 6 | 2.59 | 2.47 | 2.30 |
| 100 | 90 | 6 | 2.79 | 2.66 | 2.48 |
| 125 | 90 | 8 | 3.47 | 3.31 | 3.08 |
| 125 | 90 | 10 | 3.64 | 3.48 | 3.24 |
| Column 1 | 2 | 3 | 4 | 5 | 6 |

9.20.6. Thickness and Height

9.20.6.1.  Thickness of Exterior Walls

(1)  Masonry exterior walls, other than cavity walls, in 1 storey buildings and the top storeys of 2- and 3-storey buildings shall be not less than 140 mm thick provided the walls are not more than 2 800 mm high at the eaves and 4.6 m high at the peaks of gable ends.

(2)  The exterior walls of the bottom storeys of 2 storey buildings, and exterior walls of the bottom 2 storeys of 3 storey buildings shall be not less than 190 mm thick.

(3)  In exterior walls composed of more than one wythe, each wythe shall be not less than 90 mm thick.

9.20.6.2.  Cavity Walls

(1)  Cavity walls shall be made with not less than 90 mm wide units if the joints are raked and not less than 75 mm wide units if the joints are not raked.

(2)  The width of a cavity in a cavity wall shall be not less than 50 mm nor greater than 150 mm.

(3)  The minimum thickness of cavity walls above the supporting base shall be 230 mm for the top 7.6 m and 330 mm for the remaining portion, except that where 75 mm wide units are used, the wall height above the top of the foundation wall shall not exceed 6 m.

9.20.6.3.  Thickness of Interior Walls

(1)  The thickness of loadbearing interior walls shall be determined on the basis of the maximum lateral support spacing as provided in Sentences 9.20.10.1.(2) and (3).

(2)  The thickness of interior non-loadbearing walls shall be

(a)	determined on the basis of the maximum lateral support spacing as provided in Sentences 9.20.10.1.(2) and (3), and

(b)	in any case not less than 65 mm.

9.20.6.4.  Masonry Veneer Walls

(1)  Except for masonry veneer individually supported by the back-up material, masonry veneer shall be of solid units not less than 70 mm thick.

(2)  Veneer described in Sentence (1) over wood-frame walls shall have not less than a 25 mm air space behind the veneer.

(3)  Masonry veneer less than 90 mm thick shall have unraked joints.

(4)  Masonry veneer individually supported by the back-up material shall conform to Subsection 4.3.2.

9.20.6.5.  Parapet Walls

(1)  The height of parapet walls above the adjacent roof surface shall be not more than 3 times the parapet wall thickness.

(2)  Parapet walls shall be solid from the top of the parapet to not less than 300 mm below the adjacent roof level.

9.20.6.6.  Stone or Concrete Facings

(1)  Limestone slab facings and precast concrete panel facings shall conform to Subsection 4.3.2.

9.20.7. Chases and Recesses

9.20.7.1.  Maximum Dimensions

(1)  Except as permitted in Sentence 9.20.7.2.(2) and Article 9.20.7.4., the depth of any chase or recess shall not exceed one third the thickness of the wall, and the width of the chase or recess shall not exceed 500 mm.

9.20.7.2.  Minimum Wall Thickness

(1)  Except as permitted in Sentence (2) and Article 9.20.7.4., no chase or recess shall be constructed in any wall 190 mm or less in thickness.

(2)  Recesses may be constructed in 190 mm walls provided they do not exceed 100 mm in depth, 750 mm in height and 500 mm in width.

9.20.7.3.  Separation of Chases and Recesses

(1)  Chases and recesses shall be not less than

(a)	4 times the wall thickness apart measured from centre to centre, and

(b)	not less than 600 mm away from any pilaster, cross wall, buttress or other vertical element providing required lateral support for the wall.

9.20.7.4.  Non-Conforming Chases or Recesses

(1)  Chases or recesses that do not conform to the limits specified in Articles 9.20.7.1. to 9.20.7.3. shall be considered as openings, and any masonry supported above such a chase or recess shall be supported by a lintel or arch as provided in Article 9.20.5.2.

9.20.7.5.  Chases or Recesses Cut into Walls

(1)  Chases or recesses shall not be cut into walls made with hollow units after the masonry units are in place.

9.20.8. Support of Loads

9.20.8.1.  Capping of Hollow Masonry Walls

(1)  Except as permitted in Sentence (2), loadbearing walls of hollow masonry units supporting roof or floor framing members shall be capped with not less than 50 mm of solid masonry or have the top course filled with concrete.

(2)  Capping required in Sentence (1) may be omitted where the roof framing is supported on a wood plate not less than 38 mm by 89 mm.

9.20.8.2.  Cavity Walls Supporting Framing Members

(1)  Floor joists supported on cavity walls shall be supported on solid units not less than 57 mm high.

(2)  Floor joists described in Sentence (1) shall not project into the cavity.

(3)  Roof and ceiling framing members bearing on cavity walls shall be supported on

(a)	not less than 57 mm of solid masonry, bridging the full thickness of the wall, or

(b)	a wood plate not less than 38 mm thick, bearing not less than 50 mm on each wythe.

9.20.8.3.  Bearing of Beams and Joists

(1)  The bearing area under beams and joists shall be sufficient to carry the supported load.

(2)  In no case shall the minimum length of end bearing of beams supported on masonry be less than 90 mm.

(3)  The length of end bearing of floor, roof or ceiling joists supported on masonry shall be not less than 40 mm.

9.20.8.4.  Support of Beams and Columns

(1)  Beams and columns supported on masonry walls shall be supported on pilasters where the thickness of the masonry wall or wythe is less than 190 mm.

(2)  Not less than 190 mm depth of solid masonry or concrete shall be provided under the beam or column referred to in Sentence (1).

(3)  Pilasters required in Sentence (1) shall be bonded or tied to masonry walls.

(4)  Concrete pilasters required in Sentence (1) shall be not less than 50 mm by 300 mm.

(5)  Unit masonry pilasters required in Sentence (1) shall be not less than 100 mm by 290 mm.

9.20.8.5.  Distance to Edge of Supporting Members

(1)  Masonry veneer of hollow units resting on bearing support shall not project more than

(a)	30 mm beyond the supporting base where the veneer is not less than 90 mm thick, and

(b)	12 mm beyond the supporting base where the veneer is less than 90 mm thick.

(2)  Masonry veneer of solid units resting on bearing support shall not project more than one third of the width of the veneer.

(3)  Where the masonry veneer described in Sentence (2) is rough stone masonry

(a)	the projection shall be measured as the average projection of the units, and

(b)	the width of the veneer shall be measured as the average width of the veneer.

9.20.9. Bonding and Tying

9.20.9.1.  Joints to be Offset or Reinforced

(1)  Vertical joints in adjacent masonry courses shall be offset unless each wythe of masonry is reinforced with the equivalent of not less than 2 corrosion-resistant steel bars of 3.76 mm diam placed in the horizontal joints at vertical intervals not exceeding 460 mm.

(2)  Where joints in the reinforcing referred to in Sentence (1) occur, the bars shall be lapped not less than 150 mm.

9.20.9.2.  Bonding or Tying of Other than Masonry Veneer

(1)  Masonry walls, other than masonry veneer walls, that consist of 2 or more wythes shall have the wythes bonded or tied together with masonry bonding units as described in Article 9.20.9.3. or with metal ties as described in Articles 9.20.9.4.

9.20.9.3.  Bonding

(1)  Where wythes are bonded together with masonry units, the bonding units shall comprise not less than 4 per cent of the wall surface area.

(2)  Bonding units described in Sentence (1) shall be spaced not more than 600 mm vertically and horizontally in the case of brick masonry and 900 mm o.c. in the case of block or tile.

(3)  Units described in Sentence (1) shall extend not less than 90 mm into adjacent wythes.

9.20.9.4.  Tying

(1)  Where 2 or more wythes are tied together with metal ties of the individual rod type, the ties shall conform to the requirements in Sentences (3) to (6).

(2)  Other ties may be used where it can be shown that such ties provide walls that are at least as strong and as durable as those made with the individual rod type.

(3)  Metal ties of the individual rod type shall

(a)	be corrosion-resistant,

(b)	have a minimum cross-sectional area of not less than 17.8 mm2, and

(c)	have not less than a 50 mm portion bent at right angles at each end.

(4)  Metal ties of the individual rod type shall

(a)	extend from within 25 mm of the outer face of the wall to within 25 mm of the inner face of the wall,

(b)	be completely embedded in mortar except for the portion exposed in cavity walls, and

(c)	be staggered from course to course.

(5)  Where 2 or more wythes in walls other than cavity walls and masonry veneer/masonry back-up walls are tied together with metal ties of the individual rod type, the space between wythes shall be completely filled with mortar.

(6)  Ties described in Sentence (5) shall be

(a)	located within 300 mm of openings and spaced not more than 900 mm apart around openings, and

(b)	spaced not more than 900 mm apart horizontally and 460 mm apart vertically at other locations.

(7)  Except as required in Sentences (8) and (9), where the inner and outer wythes of cavity walls are tied with individual wire ties, the ties shall be spaced not more than 900 mm apart horizontally and 400 mm apart vertically.

(8)  Within 100 mm of the bottom of each floor or roof assembly where the cavity extends below the assemblies, the ties described in Sentence (7) shall be spaced not more than 600 mm apart horizontally.

(9)  Within 300 mm of any openings, the ties described in Sentence (7) shall be spaced not more than 900 mm apart.

9.20.9.5.  Ties for Masonry Veneer

(1)  Masonry veneer 70 mm or more in thickness and resting on a bearing support shall be tied to masonry back-up or to wood framing members with straps that are

(a)	corrosion-resistant,

(b)	not less than 0.76 mm thick,

(c)	not less than 22 mm wide,

(d)	shaped to provide a key with the mortar, and

(e)	spaced in accordance with Table 9.20.9.5.

Table 9.20.9.5.

Veneer Tie Spacing

Forming Part of Sentence 9.20.9.5.(1)

| Maximum Vertical Spacing, mm | Maximum Horizontal Spacing, mm |
| --- | --- |
| 400 | 800 |
| 500 | 600 |
| 600 | 400 |
| Column 1 | 2 |

(2)  The straps described in Sentence (1) which are fastened to the wood framing members shall be

(a)	bent at a right angle within 6 mm from the fastener, and

(b)	fastened with corrosion resistant 3.18 mm diam. screws, or spiral nails having a wood penetration of not less than 30 mm.

(3)  Masonry veneer individually supported by masonry or wood-frame back-up shall be secured to the back-up in conformance with Subsection 4.3.2.

(4)  The straps described in Sentence (1) may be installed against one of the sheathings listed in Table 9.23.16.2.A. provided that

(a)	the tie is in contact with the exterior surface of the sheathing, and

(b)	the sheathing beneath the tie is not compressed.

9.20.9.6.  Reinforcing for Glass Block

(1)  Glass block shall have horizontal joint reinforcement of 2 corrosion-resistant bars of not less than 3.76 mm or expanded metal strips not less than 75 mm wide

(a)	spaced at vertical intervals of not more than 600 mm for units 190 mm or less in height, and

(b)	installed in every horizontal joint for units higher than 190 mm.

(2)  Reinforcement required in Sentence (1) shall be lapped not less than 150 mm.

9.20.10. Lateral Support

9.20.10.1.  Lateral Support Required

(1)  Masonry walls shall be laterally supported by floor or roof construction or by intersecting masonry walls or buttresses.

(2)  The spacing of supports required in Sentence (1) shall be not more than

(a)	20 times the wall thickness for all loadbearing walls and exterior non-loadbearing walls, and

(b)	36 times the wall thickness for interior non-loadbearing walls.

(3)  In applying Sentence (2), the thickness of cavity walls shall be taken as the greater of

(a)	two-thirds of the sum of the thicknesses of the wythes, or

(b)	the thickness of the thicker wythe.

(4)  Floor and roof constructions providing lateral support for walls as required in Sentence (1) shall be constructed to transfer lateral loads to walls or buttresses approximately at right angles to the laterally supported walls.

9.20.11. Anchorage of Roofs, Floors and Intersecting Walls

9.20.11.1.  Anchorage of Floor or Roof Assemblies

(1)  Where required to receive lateral support, masonry walls shall be anchored to each floor or roof assembly at maximum intervals of 2 m, except that anchorage of floor joists not more than 1 m above grade may be omitted.

(2)  Anchors required in Sentence (1) shall be corrosion-resistant and be not less than the equivalent of 40 mm by 4.76 mm thick steel straps.

(3)  Anchors required in Sentence (1) shall be shaped to provide a mechanical key with the masonry and shall be securely fastened to the horizontal support to develop the full strength of the tie.

(4)  When joists are parallel to the wall, anchors required in Sentence (1) shall extend across not less than 3 joists.

9.20.11.2.  Bonding and Tying of Intersecting Walls

(1)  Where required to provide lateral support, intersecting walls shall be bonded or tied together.

(2)  Where bonding is used to satisfy the requirements of Sentence (1), 50% of the adjacent masonry units in the intersecting wall, distributed uniformly over the height of the intersection, shall be imbedded in the laterally supported wall.

(3)  Where tying is used to satisfy the requirements of Sentence (1), the ties shall be

(a)	corrosion-resistant metal,

(b)	equivalent to not less than 4.76 mm by 40 mm steel strapping,

(c)	spaced not more than 800 mm o.c. vertically, and

(d)	shaped at both ends to provide sufficient mechanical key to develop the strength of the ties.

9.20.11.3.  Wood Frame Walls Intersecting Masonry Walls

(1)  Wood-frame walls shall be tied to intersecting masonry walls with not less than 4.76 mm diam corrosion-resistant steel rods spaced not more than 900 mm o.c. vertically.

(2)  Ties required in Sentence (1) shall be anchored to the wood framing at one end and shaped to provide a mechanical key at the other end to develop the strength of the tie.

9.20.11.4.  Wood Frame Roof Systems

(1)  Except as permitted in Sentence (2), roof systems of wood-frame construction shall be tied to exterior walls by not less than 12.7 mm diam anchor bolts

(a)	spaced not more than 2 400 mm apart,

(b)	embedded not less that 90 mm into the masonry, and

(c)	fastened to a rafter plate of not less than 38 mm thick lumber.

(2)  The roof system described in Sentence (1) is permitted to be anchored by nailing the wall furring strips to the side of the rafter plate.

9.20.11.5.  Cornices, Sills and Trim

(1)  Cornices, sills or other trim of masonry material which project beyond the wall face shall have not less than 65% of their mass, but not less than 90 mm, within the wall or shall be adequately anchored to the wall with corrosion-resistant anchors.

9.20.11.6.  Piers

(1)  Where anchor bolts are to be placed in the top of a masonry pier, the pier shall conform to the requirements of Sentence 9.15.2.4.(4) and shall be capped with concrete or reinforced masonry not less than 200 mm thick.

9.20.12. Corbelling

9.20.12.1.  Corbelling

(1)  All corbelling shall consist of solid units.

(2)  The units referred to in Sentence (1) shall be corbelled so that the horizontal projection of any unit does not exceed 25 mm and the total projection does not exceed one-third of the total wall thickness.

9.20.12.2.  Corbelling for Cavity Walls

(1)  Cavity walls of greater thickness than the foundation wall on which they rest shall not be corbelled but may project 25 mm over the outer face of the foundation wall disregarding parging.

(2)  Where the foundation wall referred to in Sentence (1) is unit masonry, it is permitted to be corbelled to meet flush with the inner face of a cavity wall provided

(a)	the projection of each course does not exceed half the height or one-third the width of the corbelled unit, and

(b)	the total corbel does not exceed one-third of the foundation wall thickness.

9.20.12.3.  Corbelling for Masonry Veneer

(1)  Masonry veneer resting on a bearing support shall not project more than 25 mm beyond the supporting base where the veneer is at least 90 mm thick, and 12 mm beyond the supporting base where the veneer is less than 90 mm thick.

(2)  In the case of rough stone veneer, the projection, measured as the average projection of the stone units, shall not exceed one-third the bed width beyond the supporting base.

9.20.13. Control of Rain Water Penetration

9.20.13.1.  Materials for Flashing

(1)  Material used for flashing shall conform to Table 9.20.13.1.

(2)  Aluminum flashing in contact with masonry or concrete shall be effectively coated or separated from the masonry or concrete by an impervious membrane.

Table 9.20.13.1.

Flashing Material

Forming Part of Sentence 9.20.13.1.(1)

| Material | Minimum Thickness, mm |  |
| --- | --- | --- |
|  | Exposed Flashing | Concealed Flashing |
| Aluminum | 0.48 | — |
| Copper | 0.46 | 0.46 |
| Copper or aluminum laminated to felt or kraft paper | — | 0.05 |
| Hot dipped or galvanized steel | 0.33 | 0.33 |
| Lead sheet | 1.73 | 1.73 |
| Polyethylene | — | 0.50 |
| Roll roofing, Type S | — | standard |
| Zinc | 0.46 | 0.46 |
| Column 1 | 2 | 3 |

9.20.13.2.  Fastening of Flashing

(1)  Fastening devices for flashing shall be corrosion-resistant and where metal flashing is used, shall be compatible with the flashing with respect to galvanic action.

9.20.13.3.  Location of Flashing

(1)  Flashing shall be installed in masonry and masonry veneer walls

(a)	beneath jointed masonry window sills,

(b)	over the back and top of parapet walls,

(c)	over the heads of glass block panels, beneath weep holes, and

(d)	over the heads of window and door openings in exterior walls when the vertical distance between the top of a window or door frame and the bottom edge of the eave exceeds one-quarter of the horizontal eave overhang.

(2)  Throughwall flashing shall be provided in a masonry veneer wall such that any moisture which accumulates in the air space will be directed to the exterior of the building.

9.20.13.4.  Extension of Flashing

(1)  A flashing may be deleted when the masonry at the sill of a wall opening or the top of a wall is protected by an impervious non-jointed masonry coping which conforms to Article 9.20.13.12.

(2)  When installed beneath jointed masonry window sills and jointed masonry copings or over the heads of openings, flashing shall extend from the front edge of the masonry up behind the sill or lintel.

9.20.13.5.  Flashing for Weep Holes in Masonry Veneer/Masonry Walls

(1)  Flashing beneath weep holes in cavity walls and masonry veneer/masonry back-up walls shall

(a)	be bedded not less than 25 mm in the inside wythe,

(b)	extend to not less than 5 mm beyond the outer face of the building element below the flashing, and

(c)	be installed with a nominally horizontal slope toward the outside wythe.

9.20.13.6.  Flashing for Weep Holes in Veneer

(1)  Flashing beneath weep holes in masonry veneer over masonry back-up walls shall conform to the flashing requirements for cavity walls and masonry veneer/masonry back-up walls in Article 9.20.13.5.

(2)  Flashing beneath weep holes in masonry veneer over wood-frame walls shall be installed so that it extends from a point not less than 5 mm beyond the outer face of the building element below the flashing to a point 150 mm up the wood frame wall.

(3)  Where the frame wall is sheathed with a sheathing membrane, a non-wood-based rigid exterior insulating sheathing or a semi-rigid insulating sheathing with an integral sheathing membrane, the flashing shall be installed behind the sheathing membrane or insulating sheathing.

(4)  Flashing described in Sentence (2) is permitted to conform to the requirements for concealed flashing in Table 9.20.13.1.

9.20.13.7.  Flashing Joints

(1)  Joints in flashing shall be made watertight.

9.20.13.8.  Required Weep Holes

(1)  Weep holes spaced not more than 800 mm apart shall be provided at the bottom of

(a)	cavities in cavity walls, and

(b)	cavities or air spaces in masonry veneer walls.

(2)  The cavities or air spaces described in Sentence (1) shall include those above lintels over window and door openings required to be flashed in conformance with Article 9.20.13.4.

(3)  The weep holes required in Sentence (1) shall be in a location such that any water that collects in the cavity or space will be directed to the exterior of the building.

9.20.13.9.  Protection of Interior Finish

(1)  Except as provided in Sentence (3), where the interior finish of the exterior walls of a building is a type which may be damaged by moisture, exterior masonry walls, other than cavity walls or walls that are protected for their full height by a roof of a carport or porch, shall be

(a)	parged on the interior surface,

(b)	covered with No. 15 breather-type asphalt-saturated paper conforming to CAN2-51.32, “Sheathing, Membrane, Breather Type”, and

(c)	the paper referred to in Clause (b) shall be lapped not less than 100 mm at the joints

(2)  In situations described in Sentence (1), flashing shall be provided where water will accumulate, to lead it to the exterior.

(3)  Where the insulation effectively limits the passage of water vapour and is applied by a waterproof adhesive or by mortar directly to the masonry, the requirements for sheathing paper do not apply.

9.20.13.10.  Mortar Droppings

(1)  Cavity walls shall be constructed so that mortar droppings are prevented from forming a bridge to allow the passage of rain water across the cavity.

9.20.13.11.  Caulking at Door and Window Frames

(1)  The junction of door and window frames with masonry shall be caulked in conformance with Subsection 9.27.4.

9.20.13.12.  Drips Beneath Window Sills

(1)  Except for wall openings located less than 150 mm above ground level, where a concealed flashing is not installed beneath window and door sills, such sills shall be provided with an outward slope and a drip located not less than 25 mm from the wall surface.

9.20.14. Protection during Work

9.20.14.1.  Laying Temperature of Mortar and Masonry

(1)  Mortar and masonry shall be maintained at a temperature not below 5°C during installation and for not less than 48 h after installation.

(2)  No frozen material shall be used in the mortar mix.

9.20.14.2.  Protection from Weather

(1)  The top surface of uncompleted masonry exposed to the weather shall be completely covered with a waterproofing material when construction is not in progress.

9.20.15. Reinforcement for Earthquake Resistance

9.20.15.1.  Amount of Reinforcement

(1)  Where reinforcement is required in this Section, masonry walls shall be reinforced horizontally and vertically with steel having a total cross-sectional area of not less than 0.002 times the horizontal cross-sectional area of the wall, so that not less than one-third of the required steel area is installed either horizontally or vertically and the remainder in the other direction.

9.20.15.2.  Installation Standard

(1)  Where reinforcement for masonry is required in this Section, it shall be installed in conformance with the requirements for reinforced masonry as contained in CAN3-A371, “Masonry Construction for Buildings”.

9.20.16. Corrosion Resistance

9.20.16.1.  Corrosion Resistance of Connectors

(1)  Carbon steel connectors required to be corrosion-resistant shall be galvanized to at least the minimum standards in Table 9.20.16.1.

Table 9.20.16.1.

Minimum Requirements for Galvanizing

Forming Part of Sentence 9.20.16.1.(1)

| Connector Material | ASTM Standard | Coating Class |
| --- | --- | --- |
| Wire ties and continuous reinforcing (hot-dipped galvanizing) | A153 | Class B2 or 458 g/m2 |
| Hardware and bolts | A153 | See A153 |
| Strip, plate, bars, and rolled sections (not less than 3.18 mm thick) | A123 | 610 g/m2 |
| Sheet (less than 3.18 mm thick) | A123 | 305 g/m2 on material 0.76 mm thick(1) |
| Column 1 | 2 | 3 |

Note to Table 9.20.16.1.:

(1)	 ASTM A123 does not apply to metal less than 3.18 mm thick.  Galvanizing coatings may be interpolated for thicknesses between 3.18 mm and 0.76 mm.

Section 9.21. Chimneys and Flues

9.21.1. General

9.21.1.1.  Application

(1)  Except when otherwise specifically stated herein, this Section applies to

(a)	rectangular chimneys of brick masonry or concrete not more than 12 m in height serving fireplaces or appliances having a combined total rated heat output of 120 kW or less, and

(b)	flue pipes serving appliances regulated by Article 9.33.5.3.

(2)  Chimneys and flue pipes other than those described in Sentence (1) shall conform to Section 6.3.

9.21.1.2.  Factory-Built Chimneys

(1)  Factory-built chimneys serving solid fuel-burning appliances, and their installation, shall conform to CAN/ULC-S629, “650°C Factory-Built Chimneys”.

9.21.1.3.  Chimneys, Gas Vents or Flue Pipes

(1)  Except as provided in Sentence (2), chimneys (other than those described in Sentences 9.21.1.1.(1) and 9.21.1.2.(1)), gas vents and flue pipes serving gas-, oil- or solid fuel-burning appliances and associated equipment shall conform to Subsection 9.33.10.  (Note: vents for gas- or oil-burning appliances are regulated by Standards administered by other agencies.)

(2)  Flue pipes serving solid fuel-burning stoves, ranges and space heaters shall conform to CAN/CSA-B365-M, “Installation Code for Solid-Fuel Burning Appliances and Equipment”.

9.21.1.4.  Chimney or Flue Pipe Walls

(1)  The walls of any chimney or flue pipe shall be constructed to be smoke- and flame-tight.

9.21.2. Chimney Flues

9.21.2.1.  Chimney Flue Limitation

(1)  A chimney flue serving a fireplace or incinerator shall not serve any other appliance.

9.21.2.2.  Connections of More Than One Appliance

(1)  Except as required in Article 9.21.2.1., two or more fuel-burning appliances are permitted to be connected to the same chimney flue provided adequate draft is maintained for the connected appliances and the connections are made as described in Sentences (2) and (3).

(2)  Where 2 or more solid fuel-burning appliances are connected to the same chimney flue, the appliances must be located on the same storey.

(3)  The connection referred to in Sentence (2) for a solid fuel-burning appliance shall be below connections for appliances burning other fuels.

(4)  Solid fuel-burning appliances shall not be connected to a chimney flue serving a gas-burning appliance.

9.21.2.3.  Inclined Chimney Flues

(1)  Chimney flues shall not be inclined more than 45° to the vertical.

9.21.2.4.  Size of Chimney Flues

(1)  Except for chimneys serving fireplaces, the size of a chimney flue shall conform to the requirements of the solid fuel-burning appliance installation standards referenced in Sentence 6.2.1.4.(1) and Article 9.33.1.2.

(2)  Where a chimney flue serves only one solid fuel-burning appliance, the flue area shall be at least equal to that of the flue pipe connected to it.

9.21.2.5.  Fireplace Chimneys

(1)  The size of a chimney flue serving a masonry fireplace shall be within the allowable range specified in Table 9.21.2.5.A. or Table 9.21.2.5.B.

Table 9.21.2.5.A

Diameter of Round Flues for Fireplace Chimneys

Forming Part of Sentence 9.21.2.5.(1)

| Fireplace Opening, m2 | Chimney Height, m |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3.0 to 4.5 |  | > 4.5 to 5.9 |  | > 5.9 to 8.9 |  | > 8.9 to 12 |  |
|  | Flue diameter, mm |  |  |  |  |  |  |  |
|  | Min. | Max. | Min. | Max. | Min. | Max. | Min. | Max. |
| Up to 0.150 | 110 | 170 | 100 | 160 | 90 | 150 | 90 | 150 |
| 0.151 to 0.250 | 150 | 210 | 130 | 190 | 130 | 190 | 120 | 180 |
| 0.251 to 0.350 | 180 | 240 | 160 | 220 | 150 | 210 | 140 | 200 |
| 0.351 to 0.500 | 220 | 280 | 200 | 260 | 190 | 250 | 170 | 230 |
| 0.501 to 0.650 | 260 | 320 | 230 | 290 | 220 | 280 | 200 | 260 |
| 0.651 to 0.800 | 290 | 350 | 260 | 320 | 240 | 300 | 220 | 280 |
| 0.801 to 1.00 | 330 | 390 | 290 | 350 | 270 | 330 | 250 | 310 |
| 1.01 to 1.20 | 360 | 420 | 320 | 380 | 300 | 360 | 270 | 330 |
| 1.21 to 1.40 | 390 | 450 | 350 | 410 | 330 | 390 | 300 | 360 |
| 1.41 to 1.60 | 420 | 480 | 380 | 440 | 350 | 410 | 320 | 380 |
| 1.61 to 1.80 | — | — | 400 | 460 | 370 | 430 | 340 | 400 |
| 1.81 to 2.00 | — | — | — | — | 400 | 460 | 360 | 420 |
| 2.01 to 2.20 | — | — | — | — | — | — | 380 | 440 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |

Table 9.21.2.5.B

Rectangular Flue Sizes for Fireplace Chimneys

Forming Part of Sentence 9.21.2.5.(1)

| Fireplace Opening, m2 | Chimney Height, m |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3.0 to 4.5 |  | > 4.5 to 5.9 |  | > 5.9 to 8.9 |  | > 8.9 to 12 |  |
|  | Flue Size, mm |  |  |  |  |  |  |  |
|  | Min. | Max. | Min. | Max. | Min. | Max. | Min. | Max. |
| Up to 0.150 | 200 x 200 | 200 x 200 | 100 x 200 | 100 x 200 | 100 x 200 | 100 x 200 | 100 x 200 | 100 x 200 |
| 0.151 to 0.250 | 200 x 200 | 200 x 200 | 200 x 200 | 200 x 200 | 200 x 200 | 200 x 200 | 200 x 200 | 200 x 200 |
| 0.251 to 0.350 | 200 x 300 | 200 x 300 | 200 x 200 | 200 x 300 | 200 x 200 | 200 x 200 | 200 x 200 | 200 x 200 |
| 0.351 to 0.500 | 300 x 300 | 300 x 300 | 200 x 300 | 200 x 300 | 200 x 300 | 200 x 300 | 200 x 200 | 200 x 300 |
| 0.501 to 0.650 | 300 x 300 | 300 x 400 | 300 x 300 | 300 x 300 | 300 x 300 | 300 x 300 | 200 x 300 | 200 x 300 |
| 0.651 to 0.800 | 300 x 400 | 300 x 400 | 300 x 300 | 300 x 400 | 300 x 300 | 300 x 300 | 300 x 300 | 300 x 300 |
| 0.801 to 1.00 | 400 x 400 | 400 x 400 | 300 x 400 | 300 x 400 | 300 x 400 | 300 x 400 | 300 x 300 | 300 x 300 |
| 1.01 to 1.20 | 400 x 400 | 400 x 400 | 400 x 400 | 400 x 400 | 300 x 400 | 300 x 400 | 300 x 400 | 300 x 400 |
| 1.21 to 1.40 | — | — | 400 x 400 | 400 x 400 | 400 x 400 | 400 x 400 | 300 x 400 | 300 x 400 |
| 1.41 to 1.60 | — | — | — | — | 400 x 400 | 400 x 400 | 400 x 400 | 400 x 400 |
| 1.61 to 1.80 | — | — | — | — | — | — | 400 x 400 | 400 x 400 |
| 1.81 to 2.00 | — | — | — | — | — | — | 400 x 400 | 400 x 400 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |

9.21.2.6.  Oval Chimney Flues

(1)  The width of an oval chimney flue shall be not less than two-thirds its breadth.

9.21.3. Chimney Lining

9.21.3.1.  Lining Materials

(1)  Every masonry or concrete chimney shall have a lining of clay, concrete, firebrick or metal.

9.21.3.2.  Joints in Chimney Liners

(1)  Joints of chimney liners shall be sealed to provide a barrier to the passage of flue gases and condensate into the cavity between the liner and the surrounding masonry.

(2)  Joints of clay, concrete or firebrick chimney liners shall be struck flush to provide a straight, smooth, aligned chimney flue.

9.21.3.3.  Clay Liners

(1)  Clay liners shall conform to CAN/CSA-A324-M, “Clay Flue Linings”.

(2)  Liners referred to in Sentence (1) shall be not less than 15.9 mm thick and shall be capable of resisting, without softening or cracking, a temperature of 1 100°C.

9.21.3.4.  Firebrick Liners

(1)  Firebrick liners shall conform to ASTM C27, “Classification of Fireclay and High Alumina Refractory Brick”.

(2)  Firebrick liners shall be laid with high temperature cement mortar conforming to CAN/CGSB-10.3, “Air Setting Refractory Mortar”.

9.21.3.5.  Concrete Liners

(1)  Concrete flue liners shall conform to Clause 4.2.6.4. of CAN/CSA-A405, “Design and Construction of Masonry Chimneys and Fireplaces”.

9.21.3.6.  Metal Liners

(1)  Metal liners shall be constructed of at least 0.3 mm thick stainless steel.

(2)  Except as permitted in Sentence 9.22.10.1.(3), metal liners referred to in Sentence (1) shall only be used in chimneys serving gas- or oil-burning appliances.

9.21.3.7.  Installation of Chimney Liners

(1)  Chimney liners shall be installed when the surrounding masonry or concrete is placed.

9.21.3.8.  Spaces between Liners and Surrounding Masonry

(1)  A space not less than 10 mm wide shall be left between a chimney liner and the surrounding masonry.

(2)  The space required in Sentence (1) shall not be filled with mortar.

9.21.3.9.  Mortar for Chimney Liners

(1)  Chimney liners used in chimneys for solid fuel-burning appliances shall be laid in a full bed of

(a)	high temperature cement mortar conforming to CAN/CGSB 10.3, “Air Setting Refractory Mortar”, or

(b)	mortar consisting of 1 part portland cement to 3 parts sand by volume.

(2)  Chimney liners used in chimneys for oil- or gas-burning appliances shall be laid in a full bed of mortar consisting of 1 part portland cement to 3 parts sand by volume.

9.21.3.10.  Extension of Chimney Liners

(1)  Chimney liners shall extend from a point not less than 200 mm below the lowest flue pipe connection to a point not less than 50 mm or more than 100 mm above the chimney cap.

9.21.4. Masonry and Concrete Chimney Construction

9.21.4.1.  Unit Masonry

(1)  Unit masonry shall conform to Section 9.20.

9.21.4.2.  Concrete

(1)  Concrete shall conform to Section 9.3.

9.21.4.3.  Footings

(1)  Footings for masonry chimneys and concrete chimneys shall conform to the requirements in Section 9.15.

9.21.4.4.  Height of Chimney Flues

(1)  A chimney flue shall extend not less than

(a)	900 mm above the highest point at which the chimney comes in contact with the roof, and

(b)	not less than 600 mm above the highest roof surface or structure within 3 m of the chimney.

9.21.4.5.  Lateral Stability

(1)  Except as provided in Sentence (2), chimneys shall be braced to provide lateral stability for wind loads in accordance with CAN3-S304-M, “Masonry Design for Buildings”.

(2)  A chimney need not be laterally braced provided

(a)	no horizontal outside dimension is less than 400 mm, and

(b)	the chimney extends not more than 3.6 m above a roof or the masonry wall of which it forms a part.

9.21.4.6.  Chimney Caps

(1)  The top of a chimney shall have a waterproof cap of reinforced concrete, masonry or metal.

(2)  The cap required in Sentence (1) shall slope from the lining and be provided with a drip not less than 25 mm from the chimney wall.

(3)  Cast-in-place concrete caps shall be separated from the chimney liner by a bond break and be sealed at that location.

(4)  Jointed precast concrete or masonry chimney caps shall have flashing installed beneath the cap extending from the liner to the drip edge.

9.21.4.7.  Cleanout

(1)  Except for a chimney flue constructed to serve a masonry fireplace, a cleanout opening with a metal frame and tight-fitting metal door shall be installed near the base of the chimney flue.

9.21.4.8.  Wall Thickness

(1)  The walls of a masonry chimney shall be built of solid units not less than 70 mm thick.

9.21.4.9.  Separation of Flue Liners

(1)  Flue liners in the same chimney shall be separated by not less than 70 mm of masonry or concrete exclusive of liners where clay liners are used, or 90 mm of firebrick where firebrick liners are used.

(2)  Flue liners referred to in Sentence (1) shall be installed to prevent significant lateral movement.

9.21.4.10.  Flashing

(1)  Junctions with adjacent materials shall be adequately flashed to shed water.

9.21.5. Clearance from Combustible Construction

9.21.5.1.  Clearance from Combustible Materials

(1)  The clearance between masonry or concrete chimneys and combustible framing material shall be not less than

(a)	50 mm for interior chimneys, and

(b)	12 mm for exterior chimneys.

(2)  A clearance of not less than 150 mm shall be provided between a cleanout opening and combustible material.

(3)  Combustible flooring, subflooring and ceiling finishes shall have not less than a 12 mm clearance from masonry or concrete chimneys.

9.21.5.2.  Sealing of Spaces

(1)  All spaces between masonry or concrete chimneys and combustible material shall be sealed top or bottom with noncombustible material.

9.21.5.3.  Support of Joists or Beams

(1)  Joists or beams may be supported on masonry walls which enclose chimney flues provided the combustible members are separated from the flue by a minimum of 290 mm of solid masonry.

Section 9.22. Fireplaces

9.22.1. General

9.22.1.1.  Application

(1)  Except as otherwise specifically stated herein, this Section applies to masonry fireplaces constructed on site.

9.22.1.2.  Masonry and Concrete

(1)  Except as otherwise stated in this Section, unit masonry shall conform to Section 9.20 and concrete to Section 9.3.

(2)  Masonry above openings shall be supported by steel lintels conforming to Sentence 9.20.5.2.(2), reinforced concrete or a masonry arch.

9.22.1.3.  Footings

(1)  Footings for masonry and concrete fireplaces shall conform to Section 9.15.

9.22.1.4.  Combustion Air

(1)  Every solid fuel-fired fireplace, including a factory-built fireplace, shall have a supply of combustion air from outdoors in accordance with Sentences (2) to (7).

(2)  The combustion air shall be supplied by a noncombustible and corrosion-resistant supply duct.

(3)  The supply duct shall have

(a)	a diameter of not less than 100 mm or equivalent area, and

(b)	an exterior intake for entry of air from the outdoors.

(4)  The supply duct shall contain a tight-fitting damper that shall be located close to the interior outlet and be operable from the room containing the fireplace.

(5)  The operating mechanism shall clearly indicate the actual position of the damper.

(6)  The interior outlet shall

(a)	be located as close as possible to the opening in the face of the fireplace, and

(b)	be designed to prevent embers from entering the supply duct.

(7)  Where a supply of combustion air is provided directly to the fire chamber of a fireplace, including a factory-built fireplace or a steel fireplace liner, the installation shall comply with the “Outdoor Air Supply” requirements provided in CAN/CSA-A405-M, “Design and Construction of Masonry Chimneys and Fireplaces”.

9.22.2. Fireplace Liners

9.22.2.1.  Brick or Steel Liners

(1)  Except where a fireplace is equipped with a steel liner, every fireplace shall have a firebrick liner.

9.22.2.2.  Firebrick Liners

(1)  Fireplace liners shall be not less than

(a)	50 mm thick for the sides and back, and

(b)	25 mm thick for the floor.

(2)  Firebrick liners shall be laid with high temperature cement mortar conforming to CAN/CGSB 10.3, “Air Setting Refractory Mortar”.

(3)  Joints between a firebrick liner and the adjacent back-up masonry shall be offset.

9.22.2.3.  Steel Liners

(1)  Steel liners for fireplaces shall conform to CAN/ULC-S639M, “Standard for Steel Liner Assemblies for Solid-Fuel Burning Masonry Fireplaces”, and shall be installed in accordance with the installation instructions in that Standard.

9.22.3. Fireplace Walls

9.22.3.1.  Thickness of Walls

(1)  Except as provided in Sentence (2), the thickness of the back and sides of a fireplace, including the thickness of any firebrick liner, shall consist of not less than 190 mm thick where a metal liner or a firebrick liner less than 50 mm is used.

(2)  When a steel fireplace liner is used with an air circulating chamber surrounding the firebox, the back and sides of the fireplace shall consist of

(a)	solid masonry units not less than 90 mm thick, or

(b)	hollow masonry units not less than 190 mm thick.

9.22.4. Fire Chamber

9.22.4.1.  Fire Chamber Dimensions

(1)  The distance from the back of the fire chamber to the plane of the fireplace opening shall be not less than 300 mm.

9.22.5. Hearth

9.22.5.1.  Hearth Extension

(1)  Except as required in Sentence (2), fireplaces shall have a noncombustible hearth extending not less than 400 mm in front of the fireplace opening measured from the facing, and not less than 200 mm beyond each side of the fireplace opening.

(2)  Where the fire chamber floor is elevated more than 150 mm above the hearth, the dimension of the hearth measured perpendicular to the plane of the fireplace opening shall be increased by not less than

(a)	50 mm for an elevation above 150 mm and not more than 300 mm, and

(b)	an additional 25 mm for every 50 mm in elevation above 300 mm.

9.22.5.2.  Support of Hearth

(1)  Except as permitted in Sentence (2), the fire chamber floor and hearth shall be supported on a reinforced concrete slab not less than a 100 mm thick at its supports and, if cantilevered, not less than 50 mm thick at its unsupported edge.

(2)  A hearth for a fireplace with an opening raised not less than 200 mm from a combustible floor is permitted to be supported on that floor provided the requirements of Clauses 5.3.6.5. to 5.3.6.7. of CAN/CSA-A405-M, “Design and Construction of Masonry Chimneys and Fireplaces” are followed.

9.22.6. Damper

9.22.6.1.  Required Damper and Size

(1)  The throat of every fireplace shall be equipped with a metal damper sufficiently large to cover the full area of the throat opening.

9.22.7. Smoke Chamber

9.22.7.1.  Slope of Smoke Chamber

(1)  The sides of the smoke chamber connecting a fireplace throat with a flue shall not be sloped at an angle greater than 45° to the vertical.

9.22.7.2.  Wall Thickness

(1)  The thickness of masonry walls surrounding the smoke chamber shall be not less than 190 mm at the sides, front and back, except that the portions of the back exposed to the outside may be 140 mm thick.

9.22.8. Factory-Built Fireplaces

9.22.8.1.  Conformance to Standard

(1)  Factory-built fireplaces and their installation shall conform to CAN/ULC S610-M, “Factory-Built Fireplaces”.

9.22.9. Clearance of Combustible Material

9.22.9.1.  Clearance to the Fireplace Opening

(1)  Combustible material shall not be placed on or near the face of a fireplace within 150 mm of the fireplace opening, except that where the combustible material projects more than 38 mm out from the face of the fireplace above the opening, such material shall be at least 300 mm above the top of the opening.

9.22.9.2.  Metal Exposed to the Interior

(1)  Metal exposed to the interior of a fireplace such as the damper control mechanism shall have at least a 50 mm clearance from any combustible material on the face of the fireplace where such metal penetrates through the face of the fireplace.

9.22.9.3.  Clearance to Combustible Framing

(1)  Not less than a 100 mm clearance shall be provided between the back and sides of a solid fuel burning fireplace and combustible framing, except that a 50 mm clearance is permitted where the fireplace is located in an exterior wall.

(2)  Not less than a 50 mm clearance shall be provided between the back and sides of the smoke chamber of a solid fuel burning fireplace and combustible framing, except that a 25 mm clearance is permitted where the fireplace is located in an exterior wall.

9.22.9.4.  Heat Circulating Duct Openings

(1)  The clearance of combustible material above heat circulating duct openings from those openings shall be not less than

(a)	300 mm where the combustible material projects more than 38 mm from the face, and

(b)	150 mm where the projection is less than 38 mm.

9.22.10. Fireplace Inserts

9.22.10.1.  Installation Standard

(1)  Fireplace inserts and hearth mounted stoves vented through the throat of a fireplace shall conform to ULC S628, “Standard for Fireplace Inserts”.

9.22.10.2.  Installation

(1)  The installation of fireplace inserts and hearth mounted stoves vented through the throat of a fireplace shall conform to CAN/CSA-B365-M, “Installation Code for Solid-Fuel Burning Appliances and Equipment”.

(2)  Fireplace inserts and hearth mounted stoves vented through the throat of a fireplace described in Sentence (1) may be installed in existing fireplaces only if a minimum thickness of 190 mm of solid masonry is provided between the smoke chamber and any existing combustible materials, unless the insert is listed for lesser clearances.

(3)  A fireplace insert installed in a masonry fireplace shall have

(a)	a listed metal chimney liner installed from the insert collar to the top of the chimney,

(b)	a direct sealed connection to the chimney flue where such provision is part of an insert conforming to Sentence 9.22.10.1.(1), or

(c)	a direct sealed connection to the smoke chamber and a cleanout provided to any inaccessible part of the smoke chamber.

Section 9.23. Wood-Frame Construction

9.23.1. Scope

9.23.1.1.  Application

(1)  This Section applies to conventional wood-frame construction in which the framing members are spaced not more than 600 mm o.c.

(2)  The requirements in this Section with regard to floor framing, subflooring and their fastenings apply to floors for which the design live load does not exceed 2.4 kPa.

(3)  The requirements in this Section with regard to wall framing and its fastenings apply to walls which support floors for which the design live load does not exceed 2.4 kPa on any floor.

(4)  Where the conditions in Sentences (2) or (3) are exceeded, the design of the framing and fastening shall conform to Subsection 4.3.1.

9.23.1.2.  Post, Beam and Plank Construction

(1)  Post, beam and plank construction and plank frame wall construction shall conform to Article 9.4.1.2.

9.23.2. General

9.23.2.1.  Strength and Rigidity

(1)  All members shall be so framed, anchored, fastened, tied and braced to provide the necessary strength and rigidity.

9.23.2.2.  Protection from Decay

(1)  Ends of wood joists, beams and other members framing into masonry or concrete shall be treated to prevent decay where the bottom of the member is at or below ground level, or a 12 mm air space shall be provided at the end and sides of the member.

(2)  Air spaces required in Sentence (1) shall not be blocked by insulation, vapour barriers or air tight materials.

9.23.2.3.  Protection from Dampness

(1)  Except as permitted in Sentence (2), wood framing members that are not pressure treated with a wood preservative and which are supported on concrete in contact with the ground or fill shall be separated from the concrete by not less than 0.05 mm polyethylene film or Type S roll roofing.

(2)  Dampproofing material referred to in Sentence (1) is not required where the wood member is at least 150 mm above the ground.

9.23.2.4.  Lumber

(1)  Lumber shall conform to the appropriate requirements in Subsection 9.3.2.

9.23.2.5.  Termite Protection

(1)  Where termites are known to exist, unless pressure treated with a chemical that is toxic to such termites in accordance with Article 9.3.2.9., wood steps shall rest on a non-cellulosic base or apron extending at least 150 mm above grade.

(2)  Wood lattice or skirting around porches shall be separated from piers and soil by at least 50 mm.

9.23.3. Fasteners

9.23.3.1.  Standards for Nails and Screws

(1)  Unless otherwise indicated, nails specified in this Section shall be common steel wire nails or common spiral nails, conforming to CSA B111, “Wire Nails, Spikes and Staples”.

(2)  Wood screws specified in this Section shall conform to ANSI B18.6.1., “Slotted and Recessed Wood Screws (Inch Series)”.

9.23.3.2.  Length of Nails

(1)  All nails shall be long enough so that not less than half their required length penetrates into the second member.

9.23.3.3.  Prevention of Splitting

(1)  Splitting of wood members shall be minimized by staggering the nails in the direction of the grain and by keeping nails well in from the edges.

9.23.3.4.  Nailing of Framing

(1)  Except as provided in Sentence (2), nailing of framing shall conform to Table 9.23.3.4.

(2)  Where the bottom wall plate or sole plate of an exterior wall is not nailed to joists or blocking in conformance with Table 9.23.3.4., the exterior wall may be fastened to the floor framing by

(a)	having plywood, OSB or waferboard sheathing extend down over floor framing and fastened to the floor framing by nails or staples conforming to Article 9.23.3.5., or

(b)	tying the wall framing to the floor framing by 50 mm wide galvanized-metal strips

(i)	not less than 0.41 mm in thickness,

(ii)	spaced not more than 1 200 mm apart, and

(iii)	fastened at each end with at least two 63 mm nails.

Table 9.23.3.4.

Nailing for Framing

Forming Part of Sentence 9.23.3.4.(1)

| Construction Detail | Minimum Length of Nails, mm | Minimum Number or Maximum Spacing of Nails |
| --- | --- | --- |
| Floor joist to plate — toe nail | 82 | 2 |
| Wood or metal strapping to underside of floor joists | 57 | 2 |
| Cross bridging to joists | 57 | 2 at each end |
| Double header or trimmer joists | 76 | 300 mm (o.c.) |
| Floor joist to stud (balloon construction) | 76 | 2 |
| Ledger strip to wood beam | 82 | 2 per joist |
| Joist to joist splice (See also Table 9.23.13.8.) | 76 | 2 at each end |
| Tail joist to adjacent header joist | 82 | 5 |
| (end nailed) around openings | 101 | 3 |
| Each header joist to adjacent trimmer joist | 82 | 5 |
| (end nailed) around openings | 101 | 3 |
| Stud to wall plate (each end) toe nail | 63 | 4 |
| or end nail | 82 | 2 |
| Doubled studs at openings, or studs at walls or wall intersections and corners | 76 | 750 mm (o.c.) |
| Doubled top wall plates | 76 | 600 mm (o.c.) |
| Bottom wall plate or sole plate to joists or blocking (exterior walls)(1) | 82 | 400 mm (o.c.) |
| Interior walls to framing or subflooring | 82 | 600 mm (o.c.) |
| Horizontal member over openings in non-loadbearing walls — each end | 82 | 2 |
| Lintels to studs | 82 | 2 at each end |
| Ceiling joist to plate — toe nail each end | 82 | 2 |
| Roof rafter, roof truss or roof joist to plate — toe nail | 82 | 3 |
| Rafter plate to each ceiling joist | 101 | 2 |
| Rafter to joist (with ridge supported) | 76 | 3 |
| Rafter to joist (with ridge unsupported) | 76 | See Table 9.23.13.8. |
| Gusset plate to each rafter at peak | 57 | 4 |
| Rafter to ridge board — toe nail — end nail | 82 | 3 |
| Collar tie to rafter — each end | 76 | 3 |
| Collar tie lateral support to each collar tie | 57 | 2 |
| Jack rafter to hip or valley rafter | 82 | 2 |
| Roof strut to rafter | 76 | 3 |
| Roof strut to loadbearing wall — toe nail | 82 | 2 |
| 38 mm x 140 mm or less plank decking to support | 82 | 2 |
| Plank decking wider than 38 mm x 140 mm to support | 82 | 3 |
| 38 mm edge laid plank decking to support (toe nail) | 76 | 1 |
| 38 mm edge laid plank to each other | 76 | 450 mm (o.c.) |
| Column 1 | 2 | 3 |

Note to Table 9.23.3.4.:

(1)	 See Sentence 9.23.3.4.(2).

9.23.3.5. Fastening for Sheathing or Subflooring

(1)  Fastening of sheathing and subflooring shall conform to Table 9.23.3.5.

Table 9.23.3.5.

Fasteners for Sheathing and Subflooring

Forming Part of Sentence 9.23.3.5.(1)

| Element | Minimum Length of Fasteners, mm |  |  |  | Minimum Number or Maximum Spacing of Fastener |
| --- | --- | --- | --- | --- | --- |
|  | Common or Spiral Nails | Ring Thread Nails or Screws | Roofing Nails | Staples |  |
| Board lumber 184 mm or less wide | 51 | 45 | N/A | 51 | 2 per support |
| Board Lumber more than 184 mm wide | 51 | 45 | N/A | 51 | 3 per support |
| Fibreboard sheathing up to 13 mm thick | N/A | N/A | 44 | 28 |  |
| Gypsum sheathing up to 13 mm thick | N/A | N/A | 44 | N/A |  |
| Plywood, OSB or waferboard up to 10 mm thick | 51 | 45 | N/A | 38 |  |
| Plywood, OSB or waferboard from 10 mm to 20 mm thick | 51 | 45 | N/A | 51 |  |
| Plywood, OSB or waferboard over 20 mm Thick | 57 | 51 | N/A | N/A | 150 mm (o.c.) along edges and 300 mm (o.c.) along intermediate supports |
| Column 1 | 2 | 3 | 4 | 5 | 6 |

(2)  Staples shall not be less than 1.6 mm in diameter or thickness, with not less than a 9.5 mm crown driven with the crown parallel to framing.

(3)  Roofing nails for the attachment of fibreboard or gypsum sheathing shall not be less than 3.2 mm in diameter with a minimum head diameter of 11.1 mm.

(4)  Flooring screws shall not be less than 3.2 mm in diameter.

9.23.4. Maximum Spans

9.23.4.1.  Application

(1)  Spans provided in this Subsection for joists, beams and lintels supporting floors shall apply only where

(a)	the floors serve residential areas as described in Table 4.1.6.3., or

(b)	the uniformly distributed live load on the floors do not exceed that specified for residential areas as described in Table 4.1.6.3.

(2)  Spans for joists, beams and lintels supporting floors shall be determined according to Subsection 4.1.3. where the supported floors

(a)	serve other than residential areas, or

(b)	support a uniform live load in excess of that specified for residential areas.

9.23.4.2  Spans for Joists, Rafters and Beams

(1)  Except as required in Sentence (2), the spans for wood joists, rafters and beams shall conform to the spans shown in Tables A-1 to A-7 for the uniform live loads shown in the tables.

(2)  Spans for floor joists which are not selected from Tables A-1 and A-2 and which are required to be designed for the same loading conditions, shall not exceed the design requirements for uniform loading and vibration criteria.

(3)  Spans for built-up wood and glued-laminated timber floor beams shall conform to the spans in Tables A-8 to A-11.

(4)  Spans for roof ridge beams shall conform to the spans in Table A-12 for the uniform snow load shown.

9.23.4.3.  Steel Beams

(1)  The spans for steel floor beams with laterally supported top flanges shall conform to Table 9.23.4.3.

(2)  Beams described in Sentence (1) shall at least meet the requirements for Grade 300 W steel in CAN/CSA-G40.21-M, “Structural Quality Steels”.

(3)  A beam may be considered to be laterally supported if

(a)	the wood joists bear on its top flange at intervals of 610 mm or less over its entire length,

(b)	the load being applied to this beam is transmitted through the joists, and

(c)	19 mm by 38 mm wood strips in contact with the top flange are nailed on both sides of the beam to the bottom of the joist supported.

Table 9.23.4.3.

Maximum Spans for Steel Beams Supporting Floors in Dwelling Units(1)

Forming Part of Sentence 9.23.4.3.(1)

| Section | Supported Joist Length, m (Half the sum of joist spans on both sides of the beam) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 2.4 | 3.0 | 3.6 | 4.2 | 4.8 | 5.4 | 6.0 |
| One Storey Supported |  |  |  |  |  |  |  |
| W150 x 22 | 5.5 | 5.2 | 4.9 | 4.8 | 4.5 | 4.3 | 4.1 |
| W200 x 21 | 6.5 | 6.2 | 5.7 | 5.3 | 5.0 | 4.7 | 4.5 |
| W200 x 27 | 7.3 | 6.9 | 6.6 | 6.3 | 6.1 | 5.8 | 5.5 |
| W200 x 31 | 7.8 | 7.4 | 7.1 | 6.8 | 6.6 | 6.4 | 6.1 |
| W250 x 24 | 8.1 | 7.5 | 6.9 | 6.4 | 6.0 | 5.7 | 5.4 |
| W250 x 33 | 9.2 | 8.7 | 8.3 | 8.0 | 7.6 | 7.2 | 6.9 |
| W250 x 39 | 10.0 | 9.4 | 9.0 | 8.6 | 8.3 | 8.9 | 7.6 |
| W310 x 31 | 10.4 | 9.6 | 8.8 | 8.2 | 7.7 | 7.3 | 7.0 |
| W310 x 39 | 11.3 | 10.7 | 10.2 | 9.8 | 9.2 | 8.7 | 8.3 |
| Two Storeys Supported |  |  |  |  |  |  |  |
| W150 x 22 | 4.7 | 4.2 | 3.9 | 3.6 | 3.4 | 3.2 | 3.0 |
| W200 x 21 | 5.2 | 4.7 | 4.3 | 4.0 | 3.7 | 3.5 | 3.4 |
| W200 x 27 | 6.3 | 5.7 | 5.2 | 4.8 | 4.5 | 4.3 | 4.1 |
| W200 x 31 | 6.9 | 6.2 | 5.7 | 5.3 | 5.0 | 4.7 | 4.5 |
| W250 x 24 | 6.2 | 5.6 | 5.1 | 4.8 | 4.5 | 4.2 | 4.0 |
| W250 x 33 | 7.9 | 7.1 | 6.5 | 6.0 | 5.7 | 5.4 | 5.1 |
| W250 x 39 | 8.7 | 7.8 | 7.2 | 6.7 | 6.3 | 5.9 | 5.6 |
| W310 x 31 | 8.0 | 7.2 | 6.6 | 6.1 | 5.8 | 5.4 | 5.2 |
| W310 x 39 | 9.5 | 8.6 | 7.9 | 7.3 | 6.9 | 6.5 | 6.2 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |

9.23.4.4.  Concrete Topping

(1)  Except as permitted in Sentence (2), where a floor is required to support a concrete topping, the joist spans shown in Table A-1 or the spacing of the members shall be reduced to allow for the loads due to the topping.

(2)  Where a floor is required to support a concrete topping, joist spans are permitted to be selected from Table A-2 provided the concrete

(a)	is 38 to 51 mm thick,

(b)	is normal weight,

(c)	is placed directly on the subflooring, and

(d)	has not less than 20 MPa compressive strength after 28 days.

(3)  Where a floor is required to support a concrete topping, the beam spans shown in Tables A-8 to A-11 or the supported length of the floor joists shall be reduced to allow for the loads due to the topping.

9.23.4.5.  Heavy Roofing Materials

(1)  Where a roof is required to support an additional uniform dead load from roofing materials such as concrete roofing tile, or materials other than as specified in Section 9.26., such as clay roofing tiles, the additional load shall be allowed for by reducing

(a)	the spans for roof joists and rafters in Tables A-4 to A-7, or the spacing of the members, and

(b)	the spans for ridge beams and lintels in Tables A-12 to A-20.

9.23.5. Notching and Drilling

9.23.5.1.  Holes Drilled in Framing Members

(1)  Holes drilled in roof, floor or ceiling framing members shall be not larger than one-quarter the depth of the member and shall be located not less than 50 mm from the edges, unless the depth of the member is increased by the size of the hole.

9.23.5.2.  Notching of Framing Members

(1)  Floor, roof and ceiling framing members are permitted to be notched provided the notch is located on the top of the member within half the joist depth from the edge of bearing and is not deeper than one-third the joist depth, unless the depth of the member is increased by the size of the notch.

9.23.5.3.  Wall Studs

(1)  Wall studs shall not be notched, drilled or otherwise damaged so that the undamaged portion of the stud is less than two-thirds the depth of the stud if the stud is loadbearing or 40 mm if the stud is non-loadbearing, unless the weakened studs are suitably reinforced.

9.23.5.4.  Top Plates

(1)  Top plates in walls shall not be notched, drilled or otherwise weakened to reduce the undamaged width to less than 50 mm unless the weakened plates are suitably reinforced.

9.23.5.5.  Roof Trusses

(1)  Roof truss members shall not be notched, drilled or otherwise weakened unless such notching or drilling is allowed for in the design of the truss.

9.23.6. Anchorage

9.23.6.1.  Anchorage of Building Frames

(1)  Building frames shall be anchored to the foundation unless a structural analysis of wind and earth pressures shows anchorage is not required.

(2)  Except as provided in Article 9.23.6.3., anchorage shall be provided by embedding the ends of the first floor joists in concrete, or fastening the sill plate to the foundation with not less than 12.7 mm diam anchor bolts spaced not more than 2 400 mm o.c.

(3)  Anchor bolts referred to in Sentence (2) shall be fastened to the sill plate with nuts and washers and shall be embedded not less than 100 mm in the foundation and so designed that they may be tightened without withdrawing them from the foundation.

9.23.6.2.  Anchorage of Columns and Posts

(1)  Exterior columns and posts shall be anchored to resist uplift and lateral movement.

9.23.6.3.  Anchorage of Smaller Buildings

(1)  Buildings not more than 4.3 m wide and not more than 1 storey in building height are permitted to be anchored in conformance with the requirements of CAN/CSA-Z240.10.1., “Site Preparation, Foundation and Anchorage of Mobile Homes”.

9.23.7. Sill Plates

9.23.7.1.  Size of Sill Plates

(1)  Where sill plates provide bearing for the floor system they shall be not less than 38 mm by 89 mm material.

9.23.7.2.  Levelling of Sill Plates

(1)  Sill plates shall be levelled by setting them on a full bed of mortar, except that where the top of the foundation is level, they may be laid directly on the foundation provided the junction between the foundation and the sill plate is caulked or the sill plate is placed on a layer of mineral wool not less than 25 mm thick before being compressed.

9.23.8. Beams to Support Floors

9.23.8.1.  Bearing for Beams

(1)  Beams shall have even and level bearing and shall have not less than 89 mm length of bearing at end supports.

9.23.8.2.  Priming of Steel Beams

(1)  Steel beams shall be shop primed.

9.23.8.3.  Built-up Wood Beams

(1)  Where a beam is made up of individual pieces of lumber that are nailed together, the individual members shall be 38 mm or greater in thickness and installed on edge.

(2)  Except as permitted in Sentence (3), where individual members of a built-up beam are butted together to form a joint, the joint shall occur over a support.

(3)  Where a beam is continuous over more than 1 span, individual members are permitted to be butted together to form a joint at or within 150 mm of the end quarter points of the clear spans, provided the quarter points are not those closest to the ends of the beam.

(4)  Members joined at quarter points shall be continuous over adjacent supports.

(5)  Joints in individual members of a beam that are located at or near the end quarter points shall not occur in adjacent members at the same quarter point and shall not reduce the effective beam width by more than half.

(6)  Not more than 1 butt joint shall occur in any individual member of a built-up beam within any one span.

(7)  Except as provided in Sentence (8), where 38 mm members are laid on edge to form a built-up beam, individual members shall be nailed together with a double row of nails not less than 89 mm in length, spaced not more than 450 mm apart in each row with the end nails located 100 mm to 150 mm from the end of each piece.

(8)  Where 38 mm members in built-up wood beams are not nailed together as provided in Sentence (7), they shall be bolted together with not less than 12.7 mm diam bolts equipped with washers and spaced not more than 1 200 mm o.c., with the end bolts located not more than 600 mm from the ends of the members.

9.23.9. Floor Joists

9.23.9.1.  End Bearing for Joists

(1)  Except when supported on ribbon boards, floor joists shall have not less than 38 mm length of end bearing.

(2)  Ribbon boards referred to in Sentence (1) shall be not less than 19 mm by 89 mm lumber let into the studs.

9.23.9.2.  Joists Supported by Beams

(1)  Floor joists may be supported on the tops of beams or may be framed into the sides of beams.

(2)  When framed into the side of a wood beam, joists referred to in Sentence (1) shall be supported on

(a)	joist hangers or other acceptable mechanical connectors, or

(b)	not less than 38 mm by 64 mm ledger strips nailed to the side of the beam, except that 38 mm by 38 mm ledger strips may be used provided each joist is nailed to the beam by at least four 89 mm nails, in addition to the nailing for the ledger strip required in Table 9.23.3.4.

(3)  When framed into the side of a steel beam, joists referred to in Sentence (1) shall be supported on the bottom flange of the beam or on not less than 38 mm by 38 mm lumber bolted to the web with not less than 6.3 mm diam bolts spaced not more than 600 mm apart.

(4)  Joists referred to in Sentence (3) shall be spliced above the beam with not less than 38 mm by 38 mm lumber at least 600 mm long to support the flooring.

(5)  Not less than a 12 mm space shall be provided between the splice required in Sentence (4) and the beam to allow for shrinkage of the wood joists.

9.23.9.3.  Restraint of Joist Bottoms

(1)  Except as provided in Sentence 9.23.9.4.(5), bottoms of floor joists shall be restrained from twisting at each end by toe-nailing to the supports, end-nailing to the header joists or by providing continuous strapping, blocking between the joists or cross-bridging near the supports.

9.23.9.4.  Strapping and Bridging in Tables A-1 and A-2

(1)  Where a panel-type ceiling finish is attached to wood furring, the provisions of Article 9.23.9.5. shall apply.

(2)  Except as permitted in Sentence (5), where strapping is specified, it shall be

(a)	not less than 19 mm by 64 mm, nailed to the underside of floor joists

(b)	located not more than 2 100 mm from each support or other rows of strapping, and

(c)	fastened at each end to a sill or header.

(3)  Where bridging is specified in Table A-1, it shall consist of not less than 19 mm by 64 mm or 38 mm by 38 mm cross-bridging located not more than 2 100 mm from each support or other rows of bridging.

(4)  Where bridging and strapping are specified in Tables A-1 and A-2, they shall consist of

(a)	bridging as described in Sentence (3), together with, wood strapping as described in Sentence (2), or

(b)	38 mm solid blocking located not more than 2 100 mm from each support or other rows of bridging and securely fastened between the joists, together with wood strapping as defined in Sentence (2).

(5)  Strapping is not required if furring strips or a panel-type ceiling finish is attached directly to the joists.

9.23.9.5.  Ceiling in Table A2

(1)  Where a ceiling is specified in Table A-2, it shall consist of gypsum board, plywood or OSB not less than 12.7 mm thick attached to

(a)	19 mm by 89 mm wood furring spaced at not more than 600 mm o.c., or

(b)	19 mm by 64 mm wood furring spaced at not more than 400 mm o.c.

9.23.9.6.  Header Joists

(1)  Header joists around floor openings shall be doubled when they exceed 1 200 mm in length.

(2)  The size of header joists exceeding 3.2 m in length shall be determined by calculations.

9.23.9.7.  Trimmer Joists

(1)  Trimmer joists around floor openings shall be doubled when the length of the header joist exceeds 800 mm.

(2)  When the header joist exceeds 2 000 mm in length the size of the trimmer joists shall be determined by calculations.

9.23.9.8.  Support of Tail and Header Joists

(1)  When tail joists and header joists are supported by the floor framing, they shall be supported by suitable joist hangers or nailing in accordance with Table 9.23.3.4.

9.23.9.9.  Support of Walls

(1)  Non-loadbearing walls parallel to the floor joists shall be supported by joists beneath the wall or on blocking between the joists.

(2)  Blocking referred to in Sentence (1) for the support of non-loadbearing walls shall be not less than 38 mm by 89 mm lumber, spaced not more than 1 200 mm apart.

(3)  Non-loadbearing interior walls at right angles to the floor joists are not restricted as to location.

(4)  Loadbearing interior walls parallel to floor joists shall be supported by beams or walls of sufficient strength to transfer safely the design loads to vertical supports.

(5)  Loadbearing interior walls at right angles to floor joists shall be located not more than 900 mm from the joist support when the wall does not support a floor, and not more than 600 mm from the joist support when the wall supports one or more floors, unless the joist size is designed to support such loads.

9.23.9.10.  Cantilevered Floor Joists

(1)  Floor joists supporting roof loads shall not be cantilevered more than 400 mm beyond their supports where 38 mm by 184 mm joists are used and not more than 600 mm beyond their supports where 38 mm by 235 mm or larger joists are used.

(2)  The cantilevered portions referred to in Sentence (1) shall not support floor loads from other storeys unless calculations are provided to show that the design resistances of the cantilevered joists are not exceeded.

(3)  Where cantilevered floor joists described in Sentences (1) and (2) are at right angles to the main floor joists, the tail joists in the cantilevered portion shall

(a)	extend inward away from the cantilever support a distance equal to not less than 6 times the length of the cantilever, and

(b)	shall be end nailed to an interior doubled header joist in conformance with Table 9.23.3.4.

9.23.10. Wall Stud

9.23.10.1.  Stud Size and Spacing

(1)  The size and spacing of studs shall conform to Table 9.23.10.1.

Table 9.23.10.1.

Size and Spacing of Studs

Forming Part of Sentence 9.23.10.1.(1)

| Type of Wall | Supported Loads (including dead loads) | Minimum Stud Size, mm | Maximum Stud Spacing, mm | Maximum Unsupported Height, m |
| --- | --- | --- | --- | --- |
| Interior | No load | 38 x 38 | 400 | 2.4 |
|  |  | 38 x 89 flat(1) | 400 | 3.6 |
|  |  | 38 x 64 | 600 | 3.0 |
|  |  | 38 x 64 flat(1) | 400 | 2.4 |
|  | Attic not accessible by a stairway | 38 x 89 | 600 | 3.6 |
|  |  | 38 x 89 flat(1) | 400 | 2.4 |
|  | Attic accessible by a stairway plus one floor |  |  |  |
|  | Roof load plus one floor | 38 x 89 | 400 | 3.6 |
|  | Attic not accessible by stairway plus 2 floors |  |  |  |
|  | Roof load | 38 x 64 | 400 | 2.4 |
|  | Attic accessible by a stairway | 38 x 89 | 600 | 3.6 |
|  | Attic not accessible by a stairway plus one floor |  |  |  |
|  | Attic accessible by a stairway plus 2 floors | 38 x 89 | 300 | 3.6 |
|  | Roof load plus 2 floors | 64 x 89 | 400 | 3.6 |
|  |  | 38 x 140 | 400 | 4.2 |
|  | Attic accessible by a stairway plus 3 floors | 38 x 140 | 300 | 4.2 |
|  | Roof load plus 3 floors |  |  |  |
| Exterior | Roof with or without attic storage | 38 x 64 | 400 | 2.4 |
|  |  | 38 x 89 | 600 | 3.0 |
|  | Roof with or without attic storage plus one floor | 38 x 89 | 400 | 3.0 |
|  |  | 38 x 140 | 600 | 3.0 |
|  |  | 38 x 89 | 300 | 3.0 |
|  | Roof with or without attic storage plus 2 floors | 64 x 89 | 400 | 3.0 |
|  |  | 38 x 140 | 400 | 3.6 |
|  | Roof with or without attic storage plus 3 floors | 38 x 140 | 300 | 1.8 |
| Column 1 | 2 | 3 | 4 | 5 |

Note to Table 9.23.10.1.:

(1)	 See Article 9.23.10.3.

9.23.10.2.  Bracing and Lateral Support

(1)  Except as provided in Sentence (2), each exterior wall in each storey shall be braced with at least one diagonal brace conforming to Sentence (3).

(2)  Bracing is not required where the walls

(a)	have an interior finish conforming to the requirements of Section 9.29, or

(b)	where the walls are

(i)	clad with panel type siding,

(ii)	diagonally sheathed with lumber, or

(iii)	sheathed with plywood, OSB, waferboard, gypsum or fibreboard sheathing.

(3)  Where bracing is required, it shall

(a)	consist of not less than 19 mm x 89 mm wood members,

(b)	be applied to the studs at an angle of approximately 45o to the horizontal, and

(c)	extend the full height of the wall on each storey.

(4)  Bracing described in Sentence (3) shall be nailed to each stud and wall plate by at least two 63 mm nails.

(5)  Where loadbearing interior walls are not finished in accordance with Sentence (2), blocking or strapping shall be fastened to the studs at mid-height to prevent sideways buckling.

9.23.10.3.  Orientation of Studs

(1)  Except as permitted in Sentences (2) and (3), all studs shall be placed at right angles to the wall face.

(2)  Studs on the flat are permitted to be used in gable ends of roofs that contain only unfinished space or in non-loadbearing interior walls within the limits described in Article 9.23.10.1.

(3)  Wall studs that support only a load from an attic not accessible by a stairway are permitted to be placed on the flat within the limits permitted in Article 9.23.10.1. provided

(a)	the studs are clad on not less than 1 side with plywood, OSB or waferboard sheathing fastened to the face of the studs with a structural adhesive, and

(b)	the portion of the roof supported by the studs does not exceed 2 100 mm in width.

9.23.10.4.  Continuity of Studs

(1)  Wall studs shall be continuous for the full storey height except at openings and shall not be spliced except by finger-jointing with a structural adhesive.

9.23.10.5.  Support for Cladding Materials

(1)  Corners and intersections shall be designed to provide adequate support for the vertical edges of interior finishes, sheathing and cladding materials, and in no instance shall exterior corners be framed with less than the equivalent of 2 studs.

(2)  Where the vertical edges of interior finishes at wall intersections are supported at vertical intervals by blocking or furring, the vertical distance between such supports shall not exceed the maximum distance between supports specified in Section 9.29.

9.23.10.6.  Studs at Sides of Openings

(1)  Except as provided in Sentence (2), studs shall be doubled on each side of openings so that the inner studs extend from the lintel to the bottom wall plate and the outer studs extend from the top wall plates to the bottom wall plate.

(2)  Single studs are permitted to be used on either side of openings

(a)	in non-loadbearing interior walls not required to have fire-resistance ratings provided the studs extend from the top wall plate to the bottom wall plate, or

(b)	in loadbearing or non-loadbearing interior or exterior walls, provided

(i)	the opening is less than and within the required stud spacing, and

(ii)	no 2 such openings of full stud space width are located in adjacent stud spaces.

9.23.11. Wall Plates

9.23.11.1.  Size of Wall Plates

(1)  Except as provided in Sentence (2), wall plates shall be

(a)	not less than 38 mm thick, and

(b)	not less than the required width of the wall studs.

(2)  In non-loadbearing walls and in loadbearing walls where the studs are located directly over framing members, the bottom wall plate may be 19 mm thick.

9.23.11.2.  Bottom Wall Plates

(1)  A bottom wall plate shall be provided in all cases.

(2)  The bottom plate in exterior walls shall not project more than one third the plate width over the support.

9.23.11.3.  Top Plates

(1)  Except as permitted in Sentences (2) to (4), no fewer than 2 top plates shall be provided in loadbearing walls.

(2)  A single top plate is permitted to be used in a section of a loadbearing wall containing a lintel provided the top plate forms a tie across the lintel.

(3)  A single top plate is permitted to be used in loadbearing walls where the concentrated loads from ceilings, floors and roofs are not more than 50 mm to one side of the supporting studs and in all non-loadbearing walls.

(4)  The top plates need not be provided in a section of loadbearing wall containing a lintel provided the lintel is tied to the adjacent wall section with

(a)	not less than 75 mm by 150 mm by 0.91 mm thick galvanized steel, or

(b)	19 mm by 89 mm by 300 mm wood splice nailed to each wall section with at least three 63 mm nails.

9.23.11.4.  Joints in Top Plates

(1)  Joints in the top plates of loadbearing walls shall be staggered not less than one stud spacing.

(2)  The top plates in loadbearing walls shall be lapped or otherwise suitably tied at corners and intersecting walls in accordance with Sentence (4).

(3)  Joints in single top plates used with loadbearing walls shall be tied in accordance with Sentence (4).

(4)  Ties referred to in Sentences (2) and (3) shall be the equivalent of not less than 75 mm by 150 mm by 0.91 mm thick galvanized steel nailed to each wall with at least three 63 mm nails.

9.23.12. Framing Over Openings

9.23.12.1.  Openings in Non-Loadbearing Walls

(1)  Except as provided in Sentence (2), openings in non-loadbearing walls shall be framed with not less than 38 mm material the same width as the studs securely nailed to adjacent studs.

(2)  Openings for doors in non-loadbearing walls required to be fire separations with a fire-resistance rating shall be framed with the equivalent of at least two 38 mm thick members that are the same width as the wall plates.

9.23.12.2.  Openings in Loadbearing Walls

(1)  Openings in loadbearing walls greater than the required stud spacing shall be framed with lintels designed to carry the superimposed loads to adjacent studs.

(2)  Except as provided in Sentence 9.23.12.3.(3), where 2 or more members are used in lintels, they shall be fastened together with not less than 82 mm nails in a double row, with nails not more than 450 mm apart in each row.

(3)  Lintel members may be separated by filler pieces.

9.23.12.3.  Lintel Spans and Sizes

(1)  Spans and sizes of wood lintels shall conform to the spans shown in Tables A-13 to A-20

(a)	for buildings of residential occupancy,

(b)	where the wall studs exceed 38 mm by 64 mm in size,

(c)	where the spans of supported joists do not exceed 4.9 m, and

(d)	where the spans of trusses do not exceed 9.8 m.

(2)  In loadbearing exterior and interior walls of 38 x 64 mm framing members, lintels shall consist of

(a)	solid 64 mm thick members on edge, or

(b)	38 mm thick and 19 mm thick members fastened together with a double row of nails not less than 63 mm long and spaced not more than 450 mm apart.

(3)  Lintels referred to in Sentence (2)

(a)	shall be not less than 50 mm greater in depth than those shown in Tables A-13 to A-20 for the maximum spans shown, and

(b)	shall not exceed 2 240 mm in length.

9.23.13. Roof and Ceiling Framing

9.23.13.1.  Continuity of Rafters and Joists

(1)  Roof rafters and joists and ceiling joists shall be continuous or shall be spliced over vertical supports that extend to suitable bearing.

9.23.13.2.  Framing around Openings

(1)  Roof and ceiling framing members shall be doubled on each side of openings greater than 2 rafter or joist spacings wide.

9.23.13.3.  End Bearing Length

(1)  The length of end bearing of joists and rafters shall be not less than 38 mm.

9.23.13.4.  Location and Attachment of Rafters

(1)  Rafters shall be located directly opposite each other and tied together at the peak, or may be offset by their own thickness if nailed to a ridge board not less than 17.5 mm thick.

(2)  Except as permitted in Sentence (3), framing members shall be connected by gusset plates or nailing at the peak in conformance with Table 9.23.3.4.

(3)  Where the roof framing on opposite sides of the peak is assembled separately, such as in the case of factory-built houses, the roof framing on opposite sides is permitted to be fastened together with galvanized-steel strips not less than 200 mm by 75 mm by 0.41 mm thick spaced not more than 1 200 mm apart and nailed at each end to the framing by at least two 63 mm nails.

9.23.13.5.  Shaping of Rafters

(1)  Rafters shall be shaped at supports to provide even bearing surfaces and supported directly above the exterior walls.

9.23.13.6.  Hip and Valley Rafters

(1)  Hip and valley rafters shall be not less than 50 mm greater in depth than the common rafters and not less than 38 mm thick, actual dimension.

9.23.13.7.  Intermediate Support for Rafters and Joists

(1)  Ceiling joists and collar ties of not less than 38 mm by 89 mm lumber are permitted to be assumed to provide intermediate support to reduce the span for rafters and joists where the roof slope is 1 in 3 or greater.

(2)  Collar ties referred to in Sentence (1) more than 2 400 mm long shall be laterally supported near their centres by not less than 19 mm by 89 mm continuous members at right angles to the collar ties.

(3)  Dwarf walls and struts may be used to provide intermediate support to reduce the span for rafters and joists.

(4)  When struts are used to provide intermediate support they shall be not less than 38 mm by 89 mm material extending from each rafter to a loadbearing wall at an angle of not less than 45° to the horizontal.

(5)  When dwarf walls are used for rafter support, they shall be framed in the same manner as loadbearing walls and securely fastened top and bottom to the roof and ceiling framing to prevent over-all movement.

(6)  Solid blocking shall be installed between floor joists beneath dwarf walls referred to in Sentence (5) that enclose finished rooms.

9.23.13.8.  Ridge Support

(1)  Except as provided in Sentence (4), roof rafters and joists shall be supported at the ridge of the roof by

(a)	a loadbearing wall extending from the ridge to suitable bearing, or

(b)	a ridge beam supported by not less than 89 mm length of bearing.

(2)  Except as provided in Sentence (3), the ridge beam referred to in Sentence (1) shall conform to the sizes and spans shown in Table A-12, provided

(a)	the supported rafter or joist length does not exceed 4.9 m, and

(b)	the roof does not support any concentrated loads.

(3)  The ridge beam referred to in Sentence (1) need not comply with Sentence (2) where

(a)	the beam is of not less than 38 mm x 140 mm material, and

(b)	the beam is supported at intervals not exceeding 1 200 mm by not less than 38 mm by 89 mm members extending vertically from the ridge to suitable bearing.

(4)  When the roof slope is 1 in 3 or more, ridge support need not be provided when the lower ends of the rafters are adequately tied to prevent outward movement.

(5)  Ties required in Sentence (4) are permitted to consist of tie rods or ceiling joists forming a continuous tie for opposing rafters and nailed in accordance with Table 9.23.13.8.

(6)  Ceiling joists referred to in Sentence (5) shall be fastened together with at least one more nail per joist splice than required for the rafter to joist connection shown in the Table 9.23.13.8.

(7)  Members referred to in Sentence (6) are permitted to be fastened together either directly or through a gusset plate.

Table 9.23.13.8.

Rafter-to-Joist Nailing (Unsupported Ridge)

Forming Part of Sentences 9.23.13.8.(5) and (6)

| Roof Slope | Rafter Spacing, mm | Minimum Number of Nails not less than 75 mm Long |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Rafter Tied to every Joist |  |  |  |  |  | Rafter tied to Joist every 1.2 m |  |  |  |  |  |
|  |  | Building Width |  |  | Building Width |  |  | Building Width |  |  | Building Width |  |  |
|  |  | up to 8 m |  |  | up to 9.8 m |  |  | up to 8 m |  |  | up to 9.8 m |  |  |
|  |  | Roof Snow Load, kPa |  |  | Roof Snow Load, kPa |  |  | Roof Snow Load, kPa |  |  | Roof Snow Load, kPa |  |  |
|  |  | 1.0 or less | 1.5 | 2.0 or more | 1.0 or less | 1.5 | 2.0 or more | 1.0 or less | 1.5 | 2.0 or more | 1.0 or less | 1.5 | 2.0 or more |
| 1 in 3 | 400 | 4 | 5 | 6 | 5 | 7 | 8 | 11 | — | — | — | — | — |
|  | 600 | 6 | 8 | 9 | 8 | — | — | 11 | — | — | — | — | — |
| 1 in 2.4 | 400 | 4 | 4 | 5 | 5 | 6 | 7 | 7 | 10 | — | 9 | — | — |
|  | 600 | 5 | 7 | 8 | 7 | 9 | 11 | 7 | 10 | — | — | — | — |
| 1 in 2 | 400 | 4 | 4 | 4 | 4 | 4 | 5 | 6 | 8 | 9 | 8 | — | — |
|  | 600 | 4 | 5 | 6 | 5 | 7 | 8 | 6 | 8 | 9 | 8 | — | — |
| 1 in 1.71 | 400 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 7 | 8 | 7 | 9 | 11 |
|  | 600 | 4 | 4 | 5 | 5 | 6 | 7 | 5 | 7 | 8 | 7 | 9 | 11 |
| 1 in 1.33 | 400 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 6 | 5 | 6 | 7 |
|  | 600 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 5 | 6 | 5 | 6 | 7 |
| 1 in 1 | 400 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 |
|  | 600 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |

9.23.13.9.  Restraint of Joist Bottoms

(1)  Roof joists supporting a finished ceiling, other than plywood, OSB or waferboard, shall be restrained from twisting along the bottom edges by means of furring, blocking, cross bridging or strapping conforming to Article 9.23.9.3.

9.23.13.10.  Ceiling Loads Supporting Roof Loads

(1)  Except as permitted in Sentence (2), ceiling joists supporting part of the roof load from the rafters shall be not less than 25 mm greater in depth than required for ceiling joists not supporting part of the roof load.

(2)  When the roof slope is 1 in 4 or less, the ceiling joist sizes referred to in Sentence (1) shall be determined from the span tables for roof joists.

9.23.13.11.  Wood Roof Trusses

(1)  Roof trusses which are not designed in accordance with Part 4 shall

(a)	be capable of supporting a total ceiling load (dead load plus live load) of 0.5 kPa plus two and two-thirds times the specified live roof load for 24 h, and

(b)	not exceed the deflections shown in Table 9.23.13.11. when loaded with the ceiling load plus one and one-third times the specified roof snow load for 1 h.

Table 9.23.13.11.

Maximum Roof Truss Deflections

Forming Part of Sentence 9.23.13.11.(1)

| Truss Span | Type of Ceiling | Maximum Deflection |
| --- | --- | --- |
| 4.3 m or less | Plaster or gypsum board | 1/360 of the span |
|  | Other than plaster or gypsum board | 1/180 of the span |
| Over 4.3 m | Plaster or gypsum board | 1/360 of the span |
|  | Other than plaster or gypsum board | 1/240 of the span |
| Column 1 | 2 | 3 |

(2)  The joint connections used in trusses described in Sentence (1) shall be designed in conformance with the requirements in Subsection 4.3.1.

(3)  Where the length of compression web members in roof trusses described in Sentence (1) exceeds 1 830 mm, such web members shall be provided with continuous bracing to prevent buckling.

(4)  Bracing required in Sentence (3) shall consist of not less than 19 mm by 89 mm lumber nailed at right angles to the web members near their centres with at least two 63 mm nails for each member.

(5)  Where the ability of a truss design to satisfy the requirements of Sentence (1) is demonstrated by testing, it shall consist of a full scale load test carried out in conformance with CSA S307-M, “Load Test Procedure for Wood Trusses for Houses and Small Buildings”.

(6)  Where the ability of a truss design to satisfy the requirements of Sentence (1) is demonstrated by analysis, it shall be carried out in accordance with good engineering practice such as described in “Truss Design Procedures and Specifications for Light Metal Plate Connected Wood Trusses,” published by the Truss Plate Institute of Canada.

9.23.14. Subflooring

9.23.14.1.  Subflooring Required

(1)  Subflooring shall be provided beneath finish flooring where the finish flooring does not have adequate strength to support the design loads.

9.23.14.2.  Material Standards

(1)  Wood-based panels for subfloors shall conform to

(a)	CSA O121, “Douglas Fir Plywood”,

(b)	CSA O151, “Canadian Softwood Plywood”,

(c)	CSA O153, “Poplar Plywood”,

(d)	CAN/CSA-O325.0, “Construction Sheathing”, or

(e)	CSA-O437.0, “OSB and Waferboard”.

(2)  Particleboard subflooring may be used only where a building is constructed in a factory so that the subfloor will not be exposed to the weather.

(3)  Subflooring described in Sentence (2) shall conform to grade N-1 or N-2 in CAN3-O188.1, “Interior Mat-Formed Wood Particleboard”.

(4)  Subflooring described in Sentence (2) shall have its upper surface and all edges treated to restrict water absorption where the subfloor is used in bathrooms, kitchens, laundry rooms and other areas subject to periodic wetting.

9.23.14.3.  Edge Support

(1)  Where the edges of panel-type subflooring are required to be supported, such support shall consist of tongue-and-groove panel edges or not less than 38 mm by 38 mm blocking securely nailed between framing members.

9.23.14.4.  Direction of Installation

(1)  Plywood subflooring shall be installed with the surface grain at right angles to the joists and with joints parallel to floor joists staggered.

(2)  OSB subflooring conforming to O-1 and O-2 grades in CSA-O437.0 and waferboard subflooring conforming to R-1 grade in CSA O437.0 shall be installed with the direction of face orientation at right angles to the joists and with the joints parallel to floor joists staggered.

9.23.14.5.  Subfloor Thickness or Rating

(1)  Except as provided in Sentences (2) and (3), subfloors shall conform to Table 9.23.14.5.A. or Table 9.23.14.5.B.

Table 9.23.14.5.A.

Thickness of Subflooring

Forming Part of Sentences 9.23.14.5.(1) and 9.23.15.6.(1)

| Maximum Spacing of Supports, mm | Minimum Thickness, mm |  |  |  |
| --- | --- | --- | --- | --- |
|  | Plywood and OSB, O-2 Grade | OSB, O-1 Grade, and Waferboard, R-1 Grade | Particleboard | Lumber |
| 400 | 15.5 | 15.9 | 15.9 | 17.0 |
| 500 | 15.5 | 15.9 | 19.0 | 19.0 |
| 600 | 18.5 | 19.0 | 25.4 | 19.0 |
| Column 1 | 2 | 3 | 4 | 5 |

Table 9.23.14.5.B.

Rating for Subfloor when Applying CSA O325.0

Forming Part of Sentences 9.23.14.5.(1) and 9.23.15.6.(1)

| Maximum Spacing of Supports, mm | Panel Mark |  |
| --- | --- | --- |
|  | Subfloor | Used with Panel-Type Underlay |
| 400 | 1F16 | 2F16 |
| 500 | 1F20 | 2F20 |
| 600 | 1F24 | 2F24 |
| Column 1 | 2 | 3 |

(2)  Where the finished flooring consists of not less than 19 mm matched wood strip flooring laid at right angles to joists, spaced not more than 600 mm o.c., subflooring shall be permitted to consist of not less than

(a)	12.5 mm thick plywood,

(b)	12.5 mm thick OSB conforming to O-2 grade,

(c)	12.7 mm thick OSB conforming to O-1 grade, or

(d)	12.7 mm thick waferboard conforming to R-1 grade.

(3)  Except where the flooring consists of ceramic tiles applied with adhesive, where a separate panel-type underlay or concrete topping is applied to a subfloor on joists spaced not more than 400 mm o.c., the subfloor may consist of not less than

(a)	12.5 mm thick plywood,

(b)	12.5 mm thick OSB conforming to O-2 grade,

(c)	12.7 mm thick OSB conforming to O-1 grade, or

(d)	12.7 mm thick waferboard conforming to R-1 grade.

9.23.14.6.  Annular Grooved Nails

(1)  When resilient flooring is applied directly to an OSB, waferboard, particleboard or plywood subfloor, the subfloor shall be fastened to the supports with annular grooved nails.

9.23.14.7.  Lumber Subflooring

(1)  Lumber subflooring shall be laid at an angle of not less than 45° to the joists.

(2)  Lumber subflooring shall be fully supported at the ends on solid bearing.

(3)  Lumber for subflooring shall be of uniform thickness and not more than 184 mm wide.

9.23.15. Roof Sheathing

9.23.15.1.  Material Standards

(1)  Wood-based panels used for roof sheathing shall conform to the requirements of

(a)	CSA O121, “Douglas Fir Plywood”,

(b)	CSA O151, “Canadian Softwood Plywood”,

(c)	CSA O153, “Poplar Plywood”,

(d)	CAN/CSA-O325.0, “Construction Sheathing”, or

(e)	CAN3-O437.0, “OSB and Waferboard”.

9.23.15.2.  Direction of Installation

(1)  Plywood roof sheathing shall be installed with the surface grain at right angles to the roof framing.

(2)  OSB roof sheathing conforming to O-1 and O-2 grades as specified in CSA-O437.0, “OSB and Waferboard”, shall be installed with the direction of face orientation at right angles to the roof framing members.

9.23.15.3.  Joints in Panel Type Sheathing

(1)  Panel-type sheathing board shall be applied so that joints perpendicular to the roof ridge are staggered where

(a)	the sheathing is applied with the surface grain parallel to the roof ridge, and

(b)	the thickness of the sheathing is such that the edges are required to be supported.

(2)  A gap of not less than 2 mm shall be left between sheets of plywood, OSB or waferboard.

9.23.15.4.  Lumber Roof Sheathing

(1)  Lumber roof sheathing shall not be more than 286 mm wide and shall be applied so that all ends are supported with end joints staggered.

9.23.15.5.  Edge Support

(1)  Except as permitted in Sentence (2), where panel-type roof sheathing requires edge support, the support shall consist of

(a)	metal H clips, or

(b)	not less than 38 mm by 38 mm blocking securely nailed between framing members.

(2)  The supports referred to in Sentence (1) are not required when tongued-and-grooved edged panel-type sheathing board is used.

9.23.15.6.  Thickness or Rating

(1)  The thickness or rating of roof sheathing on a flat roof used as a walking deck shall conform to either Table 9.23.14.5.A. or Table 9.23.14.5.B. for subfloors.

(2)  The thickness or rating of roof sheathing on a roof not used as a walking deck shall conform to either Table 9.23.15.6.A. or Table 9.23.15.6.B.

Table 9.23.15.6.A.

Thickness of Roof Sheathing

Forming Part of Sentence 9.23.15.6.(2)

| Maximum Spacing of Supports, mm | Minimum Thickness, mm |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Plywood and OSB, O-2 Grade |  | OSB, O-1 Grade and Waferboard, |  | Lumber |
|  |  |  | R-1 Grade |  |  |
|  | Edges | Edges | Edges | Edges |  |
|  | Supported | Unsupported | Supported | Unsupported |  |
| 300 | 7.5 | 7.5 | 9.5 | 9.5 | 17.0 |
| 400 | 7.5 | 9.5 | 9.5 | 11.1 | 17.0 |
| 600 | 9.5 | 12.5 | 11.1 | 12.7 | 19.0 |
| Column 1 | 2 | 3 | 4 | 5 | 6 |

Table 9.23.15.6.B.

Rating for Roof Sheathing When Applying CSA O325.0

Forming Part of Sentence 9.23.15.6.(2)

| Maximum Spacing of Supports, mm | Panel Mark |  |
| --- | --- | --- |
|  | Edges Supported | Edges Unsupported |
| 400 | 2R16 | 1R16 |
| 500 | 2R20 | 1R20 |
| 600 | 2R24 | 1R24 |
| Column 1 | 2 | 3 |

(3)  Asphalt-coated or asphalt-impregnated fibreboard not less than 11.1 mm thick conforming to CSA A247-M, “Insulating Fibreboard” is permitted to be used as a roof sheathing over supports spaced not more than 400 mm o.c. provided the roofing consists of

(a)	a continuous sheet of galvanized steel not less than 0.33 mm in thickness, or

(b)	a continuous sheet of aluminum not less than 0.61 mm in thickness.

(4)  All edges of sheathing described in Sentence (3) shall be supported by blocking or framing.

9.23.16. Wall Sheathing

9.23.16.1.  Required Sheathing

(1)  Exterior walls and gable ends shall be sheathed when the exterior cladding requires intermediate fastening between supports or if the exterior cladding requires solid backing.

9.23.16.2.  Thickness, Rating and Material Standards

(1)  Where wall sheathing is required, it shall conform to Table 9.23.16.2.A. or Table 9.23.16.2.B.

Table 9.23.16.2.A.

Wall Sheathing Thickness and Specifications

Forming Part of Article 9.23.16.2.(1)

| Type of Sheathing | Minimum Thickness, mm |  | Material Standards |
| --- | --- | --- | --- |
|  | With Supports 400 mm o.c. | With Supports 600 mm o.c. |  |
| Fibreboard (insulating) | 9.5 | 11.1 | CAN/CSA-A247 |
|  |  |  | CSA/CSA-A82.27-M |
| Gypsum sheathing | 9.5 | 12.7 | ASTM C 97 |
| Lumber | 17.0 | 17.0 | See Table 9.3.2.1. |
| Mineral Fibre, Rigid Board, Type 2 | 25 | 25 | CSA A101-M |
| OSB. O-2 Grade | 6.0 | 7.5 | CSA O437 |
| OSB, O-1 Grade, and waferboard, R-1 Grade | 6.35 | 7.9 | CSA O437 |
| Phenolic, faced | 25 | 25 | CAN/CGSB-51.25-M |
| Plywood (exterior type) | 6.0 | 7.5 | CSA O121-M |
|  |  |  | CSA O151-M |
|  |  |  | CSA O153-M |
| Polystyrene expanded Types 1 and 2 | 38 | 38 | CAN/CGSB-51.20-M |
| Polystyrene expanded Types 3 and 4 | 25 | 25 | CAN/CGSB-51.20-M |
| Urethane and Isocycanurate Types 1, 2 and 4 | 38 | 38 | CGSB 51-GP-21M |
| Urethane and Isocycanurate, Type 3 | 25 | 25 | CGSB 51-GP-21M |
| Urethane and Isocycanurate Types 1 and 2 faced | 25 | 25 | CAN/CGSB-51.26-M |
| Column 1 | 2 | 3 | 4 |

Note to Table 9.23.16.2.A.:

(1)  See also Sentences 9.27.5.1.(2) to (4).

Table 9.23.16.2.B.

Rating For Wall Sheathing When Applying CSA O325.0

Forming Part of Article 9.23.16.2.

| Maximum Spacing of Supports, mm | Panel Mark |
| --- | --- |
| 400 | W16 |
| 500 | W20 |
| 600 | W24 |
| Column 1 | 2 |

9.23.16.3.  Attachment of Cladding to Sheathing

(1)  Gypsum sheathing, rigid insulation and fibreboard shall not be used for the attachment of siding materials.

(2)  Nails used in attaching the materials listed in Sentence (1) shall be not less than 3.2 mm diam with a minimum head diameter of 11 mm.

9.23.16.4.  Lumber Sheathing

(1)  Lumber wall sheathing shall be applied so that all ends are supported.

(2)  Where lumber wall sheathing is required to provide bracing according to Article 9.23.10.2., it shall be applied with end joints staggered.

9.23.16.5.  Joints in Panel-Type Sheathing

(1)  A gap of not less than 2 mm shall be left between sheets of plywood, OSB, waferboard or fibreboard.

9.23.16.6.  Mansard Style Roofs

(1)  Where the bottom portions of mansard style roofs are vented, the vertical framing members behind the sloping portions shall be considered on the same basis as exterior wall studs and shall conform to the appropriate requirements in Subsection 9.23.17.

9.23.17. Wall Sheathing Membrane

9.23.17.1.  Material Standard

(1)  Sheathing paper shall conform to the performance requirements of CAN2-51.32-M, “Sheathing, Membrane, Breather Type”.

9.23.17.2.  Sheathing Paper Beneath Stucco

(1)  Tar-saturated felts or papers shall not be used as a sheathing paper beneath stucco.

9.23.17.3.  Sheathing Membrane and Installation

(1)  Except as provided in Articles 9.23.17.4., 9.23.17.5. and 9.23.17.6., at least one layer of sheathing membrane shall be applied beneath siding, stucco or masonry veneer.

(2)  Sheathing membrane required in Sentence (1) shall be applied so that joints are lapped not less than 100 mm.

(3)  Where sheathing membrane required in Sentence (1) is applied horizontally, the upper sheets shall overlap the lower sheets.

9.23.17.4.  Insulating Sheathing in Lieu of Sheathing Membrane

(1)  Where non-wood based rigid exterior insulating sheathing, or exterior insulating sheathing with an integral sheathing membrane is installed, a separate sheathing membrane is not required.

(2)  Where insulating sheathing is installed as provided in Sentence (1)

(a)	sheathing panels subject to moisture deterioration shall be sealed at all joints, and

(b)	the joints of sheathing panels not subject to moisture deterioration shall be

(i)	sealed at all joints, or

(ii)	lapped or tongue and groove, and detailed to ensure drainage of water to the exterior.

9.23.17.5.  Sheathing Membranes in Lieu of Sheathing

(1)  Except as provided in Article 9.23.17.6., where no sheathing is used, at least 2 layers of sheathing membrane shall be applied beneath the cladding.

(2)  All joints in the sheathing membrane required in Sentence (1) shall occur over framing, and the membrane shall be fastened to the framing with roofing nails or staples spaced not more than 150 mm along the edges of the outer layer of sheathing paper.

(3)  Wall sheathing is permitted to be used in lieu of 1 layer of sheathing membrane required in Sentence (1), and the thickness need not conform to Table 9.23.16.2.A.

9.23.17.6.  Face Sealed Cladding

(1)  Sheathing membrane is permitted to be omitted beneath cladding when the joints in the cladding are formed to effectively prevent the passage of wind and rain in conformance with Sentence (2) or (4) as applicable.

(2)  Cladding consisting of sheets of plywood, hardboard, OSB, waferboard or asbestos cement is considered to meet the requirements of Sentence (1) provided the cladding is applied so that

(a)	all edges are directly supported by framing, and

(b)	the vertical joints between adjacent sheets are

(i)	covered with battens,

(ii)	shiplapped, or

(iii)	otherwise matched to provide weathertight joints.

(3)  Joints between sheets described in Sentence (2) shall be caulked.

(4)  Metal siding consisting of sheets of metal is considered to meet the requirements of Sentence (1) where the joints between sheets are of the locked seam type.

Section 9.24. Sheet Steel Stud Wall Framing

9.24.1. General

9.24.1.1.  Application

(1)  This Section applies to sheet steel studs for use in non-loadbearing exterior and interior walls.

(2)  Where loadbearing steel studs are used, they shall be designed in conformance with Part 4.

9.24.1.2.  Material Standards

(1)  Steel studs and runners shall conform to CAN/CGSB-7.1-M, “Cold Formed Steel Framing Components”.

9.24.1.3.  Metal Thickness

(1)  Metal thickness specified in this Section shall be the minimum base steel thickness exclusive of coatings.

9.24.1.4.  Screws

(1)  Screws for the application of cladding, sheathing or interior finish materials to steel studs, runners and furring channels shall conform to ASTM C1002, “Steel Drill Screws for the Application of Gypsum Board or Metal Plaster Bases”.

9.24.1.5.  Cladding, Sheathing and Interior Finish Required

(1)  Cladding or sheathing, and interior finish shall be installed on steel stud framing and shall be fastened with screws

(a)	spaced at the appropriate spacing described in Section 9.29., and

(b)	penetrating not less than 10 mm through the metal.

9.24.2. Size of Framing

9.24.2.1.  Size and Spacing of Studs in Interior Walls

(1)  Except as required in Articles 9.24.2.3. and 9.24.2.4., the size and spacing of steel studs for non-loadbearing interior walls shall conform to Table 9.24.2.1.

Table 9.24.2.1.

Steel Studs for Non-Loadbearing Interior Walls

Forming Part of Sentence 9.24.2.1.(1)

| Minimum Stud Size, mm | Maximum Stud Spacing, mm | Maximum Wall Height, m |
| --- | --- | --- |
| 30 x 40 | 400 | 3.0 |
|  | 600 | 2.7 |
| 30 x 63 | 400 | 4.0 |
|  | 600 | 3.6 |
| 30 x 91 | 400 | 5.2 |
|  | 600 | 4.9 |
| Column 1 | 2 | 3 |

9.24.2.2.  Thickness of Studs

(1)  Except as required in Article 9.24.2.4., steel studs in non-loadbearing interior walls shall have a metal thickness of not less than 0.46 mm.

9.24.2.3.  Runners

(1)  Runners for interior and exterior non-loadbearing walls shall have a thickness of not less than the thickness of the corresponding studs and shall have not less than 30 mm flanges.

9.24.2.4.  Openings in Fire Separations

(1)  Where openings for doors in non-loadbearing fire separations required to have a fire-resistance rating do not exceed 1 200 mm in width

(a)	the width of steel studs shall be not less than 63 mm, and

(b)	the steel thickness shall be not less than 0.46 mm.

(2)  Where openings described in Sentence (1) exceed 1 200 mm in width

(a)	the width of steel studs shall be not less than 91 mm, and

(b)	the metal thickness shall be not less than 0.85 mm.

(3)  The distance to the first stud beyond the jamb of any door opening in a fire separation required to have a fire-resistance rating shall not exceed 400 mm.

(4)  Where the distance between the framing over the opening referred to in Sentence (1) and the top runner exceeds 400 mm in such walls, intermediate support shall be installed at intervals of not more than 400 mm above the opening.

9.24.2.5.  Size and Spacing of Studs in Exterior Walls

(1)  The size and spacing of non-loadbearing steel studs for exterior walls shall conform to Table 9.24.2.5.

Table 9.24.2.5.

Size and Spacing of Steel Studs for Non-Loadbearing Exterior Walls

Forming Part of Sentence 9.24.2.5.(1)

| Minimum Stud Size, mm | Minimum Metal Thickness, mm | Maximum Stud Length, m |  |  |
| --- | --- | --- | --- | --- |
|  |  | Spacing of Studs |  |  |
|  |  | 300 mm (o.c.) | 400 mm (o.c.) | 600 mm (o.c.) |
| 30 x 91 | 0.53 | 3.0 | 2.4 | — |
| 30 x 91 | 0.69 | 3.3 | 2.7 | 2.4 |
| 30 x 91 | 0.85 | 3.6 | 3.0 | 2.7 |
| 30 x 91 | 1.0 | 4.0 | 3.3 | 3.0 |
| Column 1 | 2 | 3 | 4 | 5 |

9.24.3.  Installation

9.24.3.1.  Installation of Runners

(1)  Runners shall be provided at the tops and bottoms of walls.

(2)  Runners required in Sentence (1) shall be securely attached to the building at approximately 50 mm from the ends, and at intervals of not more than 600 mm o.c. for interior walls and 300 mm o.c. for exterior walls.

(3)  Fasteners used for attachment described in Sentence (2) shall consist of the equivalent of 63 mm nails or 25 mm screws.

(4)  Studs at openings and which are not full wall height shall be supported by a runner at the ends of the studs, securely fastened to the full length studs at the sides of the opening.

9.24.3.2.  Fire-Rated Walls

(1)  Steel studs used in walls required to have a fire-resistance rating shall be installed so that there is not less than a 12 mm clearance between the top of the stud and the top of the runner to allow for expansion in the event of fire.

(2)  Except as provided in Article 9.24.3.6., studs in walls referred to in Sentence (1) shall not be attached to the runners in a manner that will prevent such expansion.

(3)  Framing above doors with steel door frames in non-loadbearing fire separations required to have a fire-resistance rating shall consist of 2 runners on the flat fastened back to back.

(4)  The lower runner required in Sentence (3) shall be cut through the flanges and be bent at each end to extend upwards at least 150 mm and fastened to the adjacent studs.

9.24.3.3.  Orientation of Studs

(1)  Steel studs shall be installed with webs at right angles to the wall face and, except at openings, shall be continuous for the full wall height.

9.24.3.4.  Support for Cladding Materials

(1)  Corners and intersections of walls shall be constructed to provide support for the cladding materials.

9.24.3.5.  Framing around Openings

(1)  Studs shall be doubled on each side of every opening where such openings involve more than 1 stud space, and shall be tripled where the openings in exterior walls exceed 2.4 m in width.

(2)  Studs described in Sentence (1) shall be fastened together by screws, crimping or welding to act as a single structural unit in resisting transverse loads.

9.24.3.6.  Attachment of Studs to Runners

(1)  Studs shall be attached to runners by screws, crimping or welding around wall openings, and elsewhere where necessary to keep the studs in alignment during construction.

(2)  Where clearance for expansion is required in Article 9.24.3.2., attachment required in Sentence (1) shall be applied between studs and bottom runners only.

9.24.3.7.  Openings for Fire Dampers

(1)  Openings for fire dampers in non-loadbearing fire separations required to have a fire-resistance rating shall be framed with double studs on each side of the opening.

(2)  The sill and header for openings described in Sentence (1) shall consist of a runner track with right angle bends made on each end so as to extend 300 mm above the header or below the sill and fastened to the studs.

(3)  The openings described in Sentence (1) shall be lined with a layer of gypsum board at least 12.7 mm thick fastened to stud and runner webs.

Section 9.25. Heat Transfer, Air Leakage and Condensation Control

9.25.1. Scope

9.25.1.1.  Application

(1)  This Section applies to the application of thermal insulation and measures to control condensation, heat transfer and air leakage for buildings of residential occupancy intended for use on a continuing basis during the winter months.

(2)  Insulation and sealing of heating and ventilating ducts shall conform to Sections 9.32. and 9.33.

9.25.1.2.  General

(1)  Except as provided in Sentence (2), any sheet or panel type material with an air leakage characteristic less than 0.1 l/(sm2) at 75 Pa and water vapour permeance less than 60 ng/(Pasm2) and incorporated in a building assembly required by Article 9.25.2.1. to be insulated shall be installed

(a)	on the warm face of the assembly,

(b)	at a location where the ratio between the total thermal resistance of all materials outboard of its innermost impermeable surface and the total thermal resistance of all materials inboard of that surface is not less than required in Table 9.25.1.2., or

(c)	outboard of an air space that is vented to the outdoors and, for walls, drained.

Table 9.25.1.2.

Ratio of Outboard to Inboard Thermal Resistance

Forming Part of Sentence 9.25.1.2.(1)

| Heating Degree Days of Building Location(1), Celsius degree-days | Minimum Ratio, Total Thermal Resistance Outboard of material’s Inner Surface to Total Thermal Resistance Inboard of Material’s Inner Surface |
| --- | --- |
| up to 4999 | 0.20 |
| 5000 to 5999 | 0.30 |
| 6000 to 6999 | 0.35 |
| 7000 to 7999 | 0.40 |
| 8000 to 8999 | 0.50 |
| 9000 to 9999 | 0.55 |
| 10000 to 10999 | 0.60 |
| 11000 to 11999 | 0.65 |
| 12000 or higher | 0.75 |
| Column 1 | 2 |

Note to Table 9.25.1.2.:

(1) See Sentence 2.5.1.1.(1).

(2)  Sheathing materials installed so that, in each framing space, at least one of the gaps required by Article 9.23.15.3. and Sentence 9.23.16.5.(1) does not occur over framing need not comply with Sentence (1).

9.25.1.3.  Thermal Design

(1)  The requirements for thermal insulation in this Section need not be met where thermal design is provided in accordance with Section 9.38.

9.25.2. Thermal Insulation

9.25.2.1.  Required Insulation

(1)  All walls, ceilings and floors separating heated space from unheated space, the exterior air or the exterior soil shall be provided with sufficient thermal insulation to prevent moisture condensation on their room side during the winter and to ensure comfortable conditions for the occupants.

(2)  Insulation shall be provided between heated and unheated spaces and between heated spaces and the exterior, and around the perimeter of concrete slabs-on-ground.

(3)  Reflective surfaces of insulating materials shall not be considered in calculating the thermal resistance of building assemblies.

(4)  Except as permitted in Sentences (5), (6), (7), (8), (13) and (14) the minimum thermal resistance of insulation shall conform to Table 9.25.2.1.

Table 9.25.2.1.

Minimum Thermal Resistance of Insulation to be Installed based on Degree Day Zones(1)

Forming Part of Sentence 9.25.2.1.(4)

| Building Element Exposed to the Exterior or to Unheated Space | RSI Value Required |  |  |
| --- | --- | --- | --- |
|  | Zone 1 Less than 5000 | Zone 2 5000 or more | Electric Space Heating Zone 1 & 2 |
| Ceiling below attic or roof space | 5.40 | 6.70 | 7.00 |
| Roof assembly without attic or roof space | 3.52 | 3.52 | 3.87 |
| Wall other than foundation wall | 3.00 | 3.87 | 4.70 |
| Foundation walls enclosing heated space | 1.41 | 2.11 | 3.25 |
| Floor, other than slab-on-ground | 4.40 | 4.40 | 4.40 |
| Slab-on ground containing pipes or heating ducts | 1.76 | 1.76 | 1.76 |
| Slab-on-ground not containing pipes or heating ducts | 1.41 | 1.41 | 1.41 |
| Column 1 | 2 | 3 | 4 |

Note to Table 9.25.2.1.:

(1) Number of degree days for individual locations are contained in Table 2.5.1.1.

(5)  Except for doors on enclosed unheated vestibules and cold cellars, and except for glazed portions of doors, all doors separating heated space from unheated space shall have a thermal resistance of not less than RSI 0.7 where a storm door is not provided.

(6)  All sliding glass doors separating heated space from unheated space shall have a thermal resistance of not less than 0.30 m2°C/W.

(7)  All glazing that separates heated space from unheated space shall have a thermal resistance of not less than 0.30 m2°C/W.

(8)  The thermal resistance values in Table 9.25.2.1. for exposed roofs or ceilings may be reduced near eaves to the extent made necessary by the roof slope and required ventilation clearances, except that the thermal resistance of insulation at the location directly above the inner surface of the exterior wall shall be at least RSI 2.1.

(9)  Where an enclosed unheated space is separated from a heated space by glazing, the unheated enclosure may be considered to provide a thermal resistance of 0.16 m2°C/W.

(10)  When electric space heating is used in a category TIL3 dwelling unit, all sliding glass doors separating heated space from unheated space or the outdoors shall have an energy rating of not less than -13 ER.

(11)  When electric space heating is used in a category TIL3 dwelling unit, all glazing that separates heated space from unheated space or the outdoors shall have an energy rating of not less than -13 ER for openable windows and 0 ER for fixed glazing.

(12)  The energy rating required in Sentences (10) and (11) shall be determined in conformance with CAN/CSA-A440.2-M, “Energy Performance Evaluation of Windows and Sliding Glass Doors”.

(13)  Except as provided in Sentences (14) and (15), log wall construction and post, beam and plank construction shall have a minimum thermal resistance of RSI 2.1 for the total assembly.

(14)  The thermal resistance value in Sentence (13) for the total wall assembly may be reduced to not less than RSI 1.61 if

(a)	the thermal resistance of insulation for the exposed roof or ceiling required in Table 9.25.2.1. is increased by an amount equivalent to the reduction permitted in this Sentence, and

(b)	for log walls, the logs have tongue-and-groove or splined joints.

(15)  Where milled log walls are installed, the thermal resistance value in Sentence (13) for the total wall assembly does not apply if

(a)	the mean thickness of each log is not less than 150 mm,

(b)	the thermal resistance of insulation for the exposed roof or ceiling required in Table 9.25.2.1. is increased by RSI 0.53, and

(c)	the logs have tongue-and-groove or splined joints.

9.25.2.2.  Reserved

9.25.2.3.  Insulation Materials

(1)  Except as required in Sentence (2), thermal insulation shall conform to the requirements of

(a)	CAN/CGSB-51.20-M, “Thermal Insulation, Polystyrene, Boards and Pipe Covering”,

(b)	CGSB 51-GP-21M, “Thermal Insulation, Urethane and Isocyanurate, Unfaced”,

(c)	CAN/CGSB-51.23,“Spray Applied Rigid Polyurethane Cellular Plastic Thermal insulation”,

(d)	CAN/CGSB-51.25-M, “Thermal Insulation, Phenolic, Faced”,

(e)	CAN/CGSB-51.26-M, “Thermal Insulation, Urethane and Isocyanurate, Board, Faced”,

(f)	CAN/CGSB-51-GP-27M, “Thermal Insulation, Polystyrene, Loose Fill”,

(g)	CGSB 51-GP-60M, “Thermal Insulation, Cellulose Fibre, Loose Fill”,

(h)	CSA A101, “Thermal Insulation, Mineral Fibre, for Buildings”, or

(i)	CAN/CSA-A247-M, “Insulating Fibreboard”.

(2)  The flame-spread ratings requirements contained in the standards listed in Sentence (1) shall not apply.

(3)  Insulation in contact with the ground shall be inert to the action of soil and water and be such that its insulative properties are not significantly reduced by moisture.

(4)  Type 1 expanded polystyrene insulation as described in CAN/CGSB-51.20-M, “Thermal Insulation, Polystyrene, Boards and Pipe Covering” shall not be used in contact with the ground or as roof insulation applied above the roofing membrane.

9.25.2.4.  Installation of Thermal Insulation

(1)  Insulation shall be installed so that there is a reasonably uniform insulating value over the entire face of the insulated area.

(2)  Insulation shall be applied to the full width and length of the space between furring or framing.

(3)  Except where the insulation provides the principal resistance to air leakage, thermal insulation shall be installed so that at least 1 face is in full and continuous contact with an element with low air permeance.

(4)  Insulation on the interior of foundation walls enclosing a crawl space shall be applied so that there is not less than a 50 mm clearance above the crawl space floor if the insulation is of a type that may be damaged by water.

(5)  Insulation around concrete slabs-on-ground shall be located so that heat from the building is not restricted from reaching the ground beneath the perimeter, where exterior walls are not supported by footings extending below frost level.

(6)  Where insulation is exposed to the weather and subject to mechanical damage, it shall be protected with not less than

(a)	6 mm asbestos-cement board,

(b)	6 mm preservative-treated plywood, or

(c)	12 mm cement parging on wire lath applied to the exposed face and edge.

(7)  Except as permitted in Sentence (9) insulation and vapour barrier shall be protected from mechanical damage by a covering of gypsum board, plywood, particleboard, waferboard or hardboard.

(8)  In unfinished basements, the protection required in Sentence (7) need not be provided for mineral fibre insulation provided it is covered with polyethylene vapour barrier of at least 0.15 mm in thickness.

(9)  Insulation in factory-built buildings shall be installed so that it will not become dislodged during transportation.

(10)  Insulation applied to the interior of foundation walls enclosing heated space shall extend from the underside of the subfloor to not less than 600 mm below the adjacent exterior ground level.

(11)  The insulation required by Sentence (10) may be provided by a system installed

(a)	on the interior of the foundation wall,

(b)	on the exterior face of the foundation wall, or

(c)	partially on the interior and partially on the exterior, provided the thermal performance of the system is equivalent to that permitted in Clauses (a) or (b).

(13)  If a foundation wall is constructed of hollow masonry units, one or more of the following shall be used to control convection currents in the core spaces

(a)	filling the core spaces,

(b)	at least one row of semi-solid blocks at or below grade, or

(c)	other similar methods.

(14)  Masonry walls of hollow units which penetrate the ceiling shall be sealed at or near the ceiling adjacent to the roof space to prevent air within the voids from entering the attic or roof space by

(a)	capping with masonry units without voids, or

(b)	installation of flashing material extending across the full width of the masonry.

9.25.2.5.  Installation of Loose-Fill Insulation

(1)  Except as provided in Sentences (2) to (6), loose-fill insulation shall be used on horizontal surfaces only.

(2)  Loose-fill insulation is permitted to be installed in attic spaces over ceilings sloped not more than 2.5 in 12.

(3)  Loose-fill insulation may be used in wood-frame walls of existing buildings.

(4)  Water repellent loose-fill insulation may be used between the outer and inner wythes of masonry cavity walls.

(5)  Where soffit venting is used, measures shall be taken

(a)	to prevent loose-fill insulation from blocking the soffit vents and to maintain an open path for circulation of air from the vents into the attic or roof space, and

(b)	to minimize air flow into the loose-fill insulation near the soffit vents to maintain the thermal performance of the material.

9.25.2.6.  Installation of Spray-applied Polyurethane

(1)  Spray-applied polyurethane insulation shall be installed in accordance with CAN/CGSB-51.39, “Sprayed Application of Rigid Polyurethane Cellular Plastic Thermal Insulation for Building Construction”.

9.25.3. Air Barrier Systems

9.25.3.1.  Required Barrier to Air Leakage

(1)  Thermally insulated wall, ceiling and floor assemblies shall be constructed so as to include an air barrier system which will provide a continuous barrier to air leakage

(a)	from the interior of the building into wall, floor, attic or roof spaces sufficient to prevent excessive moisture condensation in such spaces during the winter, and

(b)	from the exterior inward sufficient to prevent moisture condensation on the room side during winter.

9.25.3.2.  Air Barrier System Properties

(1)  Sheet and panel type materials intended to provide the principal resistance to air leakage shall have an air leakage characteristic not greater than 0.02 L/(s•m2) measured at an air pressure differential of 75 Pa.

(2)  Where polyethylene sheet used to provide the air-tightness in the air barrier system shall conform to CAN/CGSB-51.34-M, “Vapour Barrier, Polyethylene Sheet for Use in Building Construction”.

9.25.3.3.  Continuity of the Air Barrier System

(1)  Where the air barrier system consists of an air-impermeable panel-type material, all joints shall be sealed to prevent air leakage.

(2)  Where the air barrier system consists of flexible sheet material, all joints shall be

(a)	sealed, or

(b)	lapped not less than 100 mm and clamped, such as between framing members, furring or blocking and rigid panels.

(3)  Where an interior wall meets an exterior wall, ceiling, floor or roof required to be provided with an air barrier protection, the air barrier system shall extend across the intersection.

(4)  Where an interior wall projects through a ceiling or extends to become an exterior wall, spaces in the wall shall be blocked to provide continuity across those spaces with the air barrier system in the abutting walls or ceiling.

(5)  Where an interior floor projects through an exterior wall or extends to become an exterior floor, continuity of the air barrier system shall be maintained from the abutting walls across the floor assembly.

(6)  Penetrations of the air barrier system, such as those created by the installation of doors, windows, electrical wiring, electrical boxes, piping or ductwork, shall be sealed to maintain the integrity of the air barrier system over the entire surface.

(7)  Access hatches installed through assemblies constructed with an air barrier system shall be weatherstripped around their perimeters to prevent air leakage.

(8)  Clearances between chimneys or gas vents and the surrounding construction which would permit air leakage from within the building into a wall or attic or roof space shall be sealed by noncombustible material to prevent such leakage.

9.25.4. Vapour Barriers

9.25.4.1.  Required Barrier to Vapour Diffusion

(1)  Thermally insulated wall, ceiling and floor assemblies shall be constructed with a vapour barrier sufficient to prevent condensation in the wall spaces, floor spaces or attic or roof spaces.

9.25.4.2.  Vapour Barrier Materials

(1)  Except as required in Sentence (2), vapour barriers shall have an initial permeance not greater than 45 ng/(Pa•s•m2).

(2)  When used where a high resistance to vapour movement is required, such as in wall constructions that incorporate exterior cladding or sheathing having a low water vapour permeance, vapour barriers shall have a permeance not greater than 15 ng/(Pa•s•m2).

(3)  Where polyethylene is installed as the vapour barrier required in Sentence (2), it shall conform to CAN/CGSB-51.34-M, “Vapour Barrier, Polyethylene Sheet for Use in Building Construction”.

(4)  Membrane-type vapour barriers other than polyethylene shall conform to CAN/CSA-51.33-M, “Vapour Barrier, Sheet, Excluding Polyethylene, for Use in Building Construction”.

(5)  Where a coating is applied to gypsum board to function as the vapour barrier, the permeance of the coating shall be determined in accordance with CAN/CGSB-1.501-M, “Method for Permeance of Coated Wallboard”.

9.25.4.3.  Installation of Vapour Barriers

(1)  Vapour barriers shall be installed to protect the entire surfaces of thermally insulated wall, ceiling and floor assemblies.

(2)  Vapour barriers shall be installed sufficiently close to the warm side of insulation to prevent condensation at design conditions.

Section 9.26. Roofing

9.26.1. General

9.26.1.1.  Purpose of Roofing

(1)  Roofs shall be protected with roofing, including flashing, installed to shed rain effectively and prevent water due to ice damming from entering the roof.

9.26.1.2.  Alternate Installation Methods

(1)  Methods described in CAN3-A123.51, “Asphalt Shingle Application on Roof Slopes 1:3 and Steeper”, or CAN3-A123.52, “Asphalt Shingle Application on Roof Slopes 1:6 to Less than 1:3” are permitted to be used for asphalt shingle applications not described in this Section.

9.26.1.3.  Solar Collector Systems

(1)  A solar collector system is permitted to be installed above roofing materials conforming to Sentence 9.26.2.1.(1).

9.26.2. Roofing Materials

9.26.2.1.  Material Standards

(1)  Roofing materials shall conform to

(a)	CAN/CGSB-37.4-M, “Fibrated, Cutback Asphalt, Lap Cement for Asphalt Roofing”,

(b)	CAN/CGSB-37.5-M, “Cutback Asphalt Plastic, Cement”,

(c)	CSA/CGSB 37.8M, “Asphalt, Cutback, Filled, for Roof Coating”,

(d)	CGSB 37-GP-9Ma, “Primer, Asphalt for Asphalt Roofing, Dampproofing and Waterproofing”,

(e)	CGSB 37-GP-21M, “Tar, Cutback, Fibrated, for Roof Coating”,

(f)	CAN/CGSB 37.50-M, “Asphalt, Rubberized, Hot Applied for Roofing and Waterproofing”,

(g)	CGSB 37-GP-52M, “Roofing and Waterproofing Membrane, Sheet Applied, Elastomeric”,

(h)	CGSB 37-GP-54M, “Roofing and Waterproofing Membrane, Sheet Applied, Flexible, Polyvinyl Chloride”,

(i)	CGSB 37-GP-56M, “Membrane, Modified, Bituminous, Prefabricated, and Reinforced for Roofing”,

(j)	CGSB 41-GP-6M, “Sheets, Thermosetting Polyester Plastics, Glass Fiber Reinforced”,

(k)	CAN2-51.32-M, “Sheathing, Membrane, Breather Type”,

(l)	CSA A123.1-M, “Asphalt Shingles Surfaced with Mineral Granules”,

(m)	CSA A123.2-M, “Asphalt Coated Roofing Sheets”,

(n)	CSA A123.3-M, “Asphalt or Tar Saturated Roofing Felt”,

(o)	CSA A123.4-M, “Bitumen for Use in Construction of Built-Up Roof Coverings and Dampproofing and Waterproofing Systems”,

(p)	CAN/CSA A123.5-M, “Asphalt Shingles Made from Glass Felt and Saturated with Mineral Granules”,

(q)	CAN/CSA A123.17, “Asphalt-Saturated Felted Glass-Fibre Mat for Use in Construction of Built-Up Roofs”,

(r)	CAN/CSA-A220.0, “Performance of Concrete Roof Tiles”,

(s)	CSA O118.1-M, “Western Red Cedar Shingles and Shakes”, or

(t)	CSA O118.2-M, “Eastern White Cedar Shingles”.

9.26.2.2.  Nails

(1)  Nails used for roofing shall be corrosion-resistant roofing or shingle nails conforming to CSA B111, “Wire Nails, Spikes and Staples”.

(2)  Nails shall have sufficient length to penetrate through or 12 mm into roof sheathing.

(3)  Nails used with asphalt roofing shall have a head diameter of not less than 9.5 mm and a shank thickness of not less than 2.95 mm.

(4)  Nails used with wood shingles or shakes shall have a head diameter of not less than 4.8 mm and a shank thickness of not less than 2.0 mm and shall be stainless steel, aluminum or hot-dipped galvanized.

9.26.2.3.  Staples

(1)  Staples used to apply asphalt or wood shingles shall be corrosion-resistant and shall be driven with the crown parallel to the eaves.

(2)  Staples used with asphalt shingles shall be not less than 19 mm long, 1.6 mm diam or thickness, with not less than a 25 mm crown, except that an 11 mm crown may be used as provided in Sentence 9.26.7.4.(2).

(3)  Staples used with wood shingles shall be not less than 29 mm long, 1.6 mm diam or thickness, with not less than a 9.5 mm crown and shall be stainless steel or aluminum.

9.26.3. Roof Slope

9.26.3.1.  Slope

(1)  Except as provided in Sentences (2) and (3), the roof slopes on which roof coverings may be applied shall conform to Table 9.26.3.1.

Table 9.26.3.1.

Roofing Types and Slope Limits

Forming Part of Sentence 9.26.3.1.(1)

| Type of Roofing | Minimum Slope | Maximum Slope |
| --- | --- | --- |
| Built-up Roofing |  |  |
| Asphalt base (gravelled) | 1 in 50(1) | 1 in 4 |
| Asphalt base (without gravel) | 1 in 25 | 1 in 2 |
| Coal-tar base (gravelled) | 1 in 50(1) | 1 in 25 |
| Cold process | 1 in 25 | 1 in 1.33 |
| Asphalt Shingles |  |  |
| Normal application | 1 in 3 | no limit |
| Low slope application | 1 in 6 | no limit |
| Roll Roofing |  |  |
| Smooth and mineral surfaced | 1 in 4 | no limit |
| 480 mm wide selvage asphalt roofing | 1 in 6 | no limit |
| Cold application felt | 1 in 50 | 1 in 1.33 |
| Wood Shingles | 1 in 4 | no limit |
| Handsplit Shakes | 1 in 3 | no limit |
| Asbestos-Cement Corrugated sheets | 1 in 4 | no limit |
| Corrugated Metal roofing | 1 in 4 | no limit |
| Sheet Metal shingles | 1 in 4 | no limit |
| Slate shingles | 1 in 2 | no limit |
| Clay Tile | 1 in 2 | no limit |
| Glass Fibre Reinforced polyester |  |  |
| Roofing Panels | 1 in 4 | no limit |
| Column 1 | 2 | 3 |

Note to Table 9.26.3.1.:

(1)	 See Sentences 9.26.3.1.(2) and (3).

(2)  Asphalt and gravel or coal tar and gravel roofs may be constructed with lower slopes than required in Sentence (1) when effective drainage is provided by roof drains located at the lowest points on the roofs.

(3)  Sheet metal roof cladding systems specifically designed for low-slope applications are permitted to be installed with lower slopes than required in Sentence (1).

9.26.4. Flashing at Intersections

9.26.4.1.  Materials

(1)  Sheet metal flashing shall consist of not less than

(a)	1.73 mm thick sheet lead,

(b)	0.33 mm thick galvanized steel,

(c)	0.46 mm thick copper,

(d)	0.46 mm thick zinc, or

(e)	0.48 mm thick aluminum.

9.26.4.2.  Valley Flashing

(1)  Where sloping surfaces of shingled roofs intersect to form a valley, the valley shall be flashed.

(2)  Closed valleys shall not be used with rigid shingles on slopes of less than 1 in 1.2.

(3)  Closed valley flashing shall consist of sheet metal, self sealing composite membranes consisting of polyethylene and bituminous material or one layer of either Type S smooth surface roll roofing or Type M mineral surface roll roofing (mineral surface down) not less than 600 mm wide, and nails shall not penetrate the flashing within 75 mm of its edge or 124 mm of the bottom of the valley centreline.

(4)  Open valleys shall be flashed with not less than

(a)	one layer of sheet metal not less than 600 mm wide, or

(b)	2 layers of roll roofing.

(5)  The bottom layer of roofing required in Sentence (4) shall consist of not less than Type S smooth roll roofing or Type M mineral surface roll roofing (mineral surface down) not less than 457 mm wide, centred in the valley and fastened with nails spaced not more than 450 mm o.c. located 25 mm away from the edges.

(6)  The top layer of roofing required in Sentence (4) shall consist of not less than Type M mineral surface roll roofing (mineral surface up), 914 mm wide, centred in the valley, applied over a 100 mm wide strip of cement along each edge of the bottom layer, and fastened with a sufficient number of nails to hold it in place until the shingles are applied.

9.26.4.3.  Intersection of Shingle Roofs and Masonry

(1)  The intersection of shingle roofs and masonry walls or chimneys shall be protected with flashing.

(2)  Counter flashing required in Sentence (1) shall be embedded not less than 25 mm in the masonry and shall extend not less than 150 mm down the masonry and lap the lower flashing not less than 100 mm.

(3)  Flashing along the slopes of a roof described in Sentence (1) shall be stepped so that there is not less than a 75 mm head lap in both the lower flashing and counter flashing.

(4)  Where the roof described in Sentence (1) slopes upwards from the masonry, the flashing shall extend up the roof slope to a point equal in height to the flashing on the masonry, but not less than 1.5 times the shingle exposure.

9.26.4.4.  Intersection of Shingle Roofs and Walls Other Than Masonry

(1)  The intersection of shingle roofs and walls clad with other than masonry shall be protected with flashing.

(2)  Flashing required in Sentence (1) shall be installed so that it extends up the wall not less than 75 mm behind the sheathing paper, and extends not less than 75 mm horizontally.

(3)  Along the slope of the roof, the flashing required in Sentence (1) shall be stepped with not less than a 75 mm head lap.

9.26.4.5.  Intersection of Built-Up Roofs and Masonry

(1)  The intersection of built-up roofs with masonry walls or chimneys shall have a cant strip at the intersection and a roofing membrane shall be mopped over the cant strip and not less than 150 mm up the wall.

(2)  Counter flashing installed over the intersection referred to in Sentence (1) shall be embedded not less than 25 mm in the masonry, and shall be of sufficient length to extend down not less than 150 mm, lapping the membrane on the masonry not less than 100 mm.

9.26.4.6.  Intersection of Built-Up Roofs and Walls other than Masonry

(1)  The intersection of built-up roofs with walls clad with other than masonry shall have a cant strip at the intersection.

(2)  The roofing membrane shall be mopped over the cant strip referred to in Sentence (1).

(3)  Flashing plies shall extend not less than 150 mm up the wall referred to in Sentence (1) behind the sheathing paper.

9.26.4.7.  Chimney Saddles

(1)  Except as otherwise permitted in Sentence (5), chimney saddles shall be installed where the upper side of a chimney on a sloping roof is more than 750 mm wide.

(2)  Chimney saddles shall be covered with sheet metal or roofing material of equivalent weight and quality equivalent to the roofing.

(3)  Saddles shall be flashed where they intersect the roof.

(4)  The intersection of the saddle and the chimney shall be flashed and counterflashed as in Article 9.26.4.3.

(5)  A chimney saddle need not be installed if the intersection between the chimney and roof is protected by sheet metal flashing that extends up the chimney to a height equal to at least one sixth the width of the chimney, but not less than 150 mm, and up the roof slope to a point equal in height to the flashing on the chimney, but not less than 1.5 times the shingle exposure.

(6)  Flashing described in Sentence (5) at the chimney shall be counterflashed as required by Article 9.26.4.3.

9.26.5. Eave Protection for Shingles and Shakes

9.26.5.1.  Required Eave Protection

(1)  Except as provided in Sentence (2), eave protection shall be provided on shingle, shake or tile roofs, extending from the edge of the roof a minimum of 900 mm up the roof slope to a line not less than 300 mm inside the inner face of the exterior wall.

(2)  Eave protection is not required

(a)	over unheated garages, carports and porches,

(b)	where the roof overhang exceeds 900 mm measured along the roof slope from the edge of the roof to the inner face of the exterior wall,

(c)	on roofs of asphalt shingles installed in accordance with Subsection 9.26.8.,

(d)	on roofs with slopes of 1 in 1.5 or greater, or

(e)	in regions with 3 500 or fewer degree-days.

9.26.5.2.  Materials

(1)  Eave protection shall be laid beneath the starter strip and shall consist of

(a)	No. 15 asphalt-saturated felt laid in two plies lapped 480 mm and cemented together with lap cement,

(b)	Type M or S roll roofing laid with not less than 100 mm head and end laps cemented together with lap cement,

(c)	glass fibre or polyester fibre coated base sheets, or

(d)	self-sealing composite membranes consisting of modified bituminous coated material.

9.26.6. Underlay Beneath Shingles

9.26.6.1.  Materials

(1)  Except as required in Sentence (2), when underlay is used beneath shingles, it shall be

(a)	asphalt-saturated sheathing paper weighing not less than 0.195 kg/m2, or

(b)	No. 15 plain or perforated asphalt-saturated felt.

(2)  Underlay used beneath wood shingles shall be breather type.

9.26.6.2.  Installation

(1)  When used with shingles, underlay shall be installed parallel to the eaves with head and end lap of not less than 50 mm.

(2)  The top edge of each strip referred to in Sentence (1) shall be fastened with sufficient roofing nails to hold it in place until the shingles are applied.

(3)  The underlay referred to in Sentence (1) shall overlap the eave protection by not less than 100 mm.

9.26.7. Asphalt Shingles on Slopes of 1 in 3 or Greater

9.26.7.1.  Coverage

(1)  Coverage shall be not less than 2 thicknesses of shingle over the entire roof, disregarding cutouts.

9.26.7.2.  Starter Strip

(1)  A starter strip shall be installed along the lower edge of the roof so that it extends approximately 12 mm beyond the eaves and rake of the roof and fastened along the bottom edge with nails spaced not more than 300 mm o.c.

(2)  Starter strips shall be at least Type M mineral-surfaced roll roofing not less than 300 mm wide, or shingles of the same weight and quality as those used as a roof covering with tabs facing up the roof slope.

(3)  Starter strips need not be provided where eave protection of not less than Type M mineral-surfaced roll roofing is provided or self-sealing composite membranes consisting of polyethylene and bituminous material is provided.

9.26.7.3.  Head Lap

(1)  Shingles shall have a head lap of not less than 50 mm.

9.26.7.4.  Fasteners

(1)  Except as provided in Sentence (2), shingles shall be fastened with at least 4 nails or staples for 1 000 mm wide shingles so that no nails or staples are exposed.

(2)  Where staples with an 11 mm crown are used, shingles shall be fastened with at least 6 staples.

(3)  Fasteners may be reduced for narrower shingles in proportion to the width of the shingle or when shingles incorporating interlocking devices are used.

(4)  Fasteners referred to in Sentences (1) and (2) shall be located 25 mm to 40 mm from each end of each strip shingle with other fasteners equally spaced between them.

(5)  Fasteners referred to in Sentences (1) and (2) shall be located not less than 12 mm above the tops of the cutouts.

9.26.7.5.  Securing of Tabs

(1)  Shingle tabs shall be secured by a spot of plastic cement not exceeding 25 mm diam under the centre of each tab or by interlocking devices or self-sealing strips.

9.26.7.6.  Hips and Ridges

(1)  Shingles on hips and ridges shall be applied so they extend not less than 100 mm on either side of the hip or ridge, and shall be lapped not less than 150 mm.

(2)  Shingles referred to in Sentence (1) shall be fastened with nails or staples on each side located not more than 25 mm from the edge and 25 mm above the butt of the overlying shingle.

9.26.7.7.  Eave Protection

(1)  Eave protection shall conform to Subsection 9.26.5.

9.26.7.8.  Flashing

(1)  Flashing shall conform to Subsection 9.26.4.

9.26.8. Asphalt Shingles on Slopes of Less Than 1 in 3

9.26.8.1.  Coverage

(1)  Except for the first 2 courses, coverage shall be not less than 3 thicknesses of shingle over the entire roof, disregarding cutouts.

9.26.8.2.  Starter Strip

(1)  A starter strip shall be installed as in Article 9.26.7.2.

(2)  Starter strips required in Sentence (1) shall be laid in a continuous band of cement not less than 200 mm wide.

9.26.8.3.  Securing of Tabs

(1)  Shingle tabs shall be secured with cold application cement applied at the rate of not less than 0.5 L/m2 of cemented area, or hot application asphalt applied at the rate of 1 kg/m2 of cemented area.

9.26.8.4.  Securing of Shingle Courses

(1)  The first course of shingles shall be secured by a continuous band of cement along the eaves applied so that the width of the band equals the shingle exposure plus 100 mm and the band is located not less than 50 mm above the lower edge of the starter strip.

(2)  The succeeding courses of shingles shall be secured by a continuous band of cement applied so that the width of the band equals the shingle exposure plus 50 mm.

(3)  The band required in Sentence (2) shall be located not less than 25 mm nor more than 50 mm above the butt of the overlying course of shingles.

9.26.8.5.  Hips and Ridges

(1)  Shingles on hips and ridges shall be not less than 300 mm wide applied to provide triple coverage.

(2)  Shingles referred to in Sentence (1) shall be cemented to the roof shingles and to each other with a coat of cement 25 mm from the edges of the shingles and fastened with nails or staples located 40 mm above the butt of the overlying shingle and 50 mm from each edge.

9.26.8.6.  Flashing

(1)  Flashing shall conform to Subsection 9.26.4.

9.26.8.7.  Fastening

(1)  Shingles shall be fastened in accordance with Article 9.26.7.4.

9.26.9. Wood Roof Shingles

9.26.9.1.  Decking

(1)  Decking for wood shingled roofs may be continuous or spaced.

9.26.9.2.  Grade

(1)  Western red cedar shingles shall be not less than No. 2 grade.

(2)  Eastern white cedar shingles shall be not less than B (clear) grade.

9.26.9.3.  Size

(1)  Wood shingles shall be not less than 400 mm long and not less than 75 mm nor more than 350 mm wide.

9.26.9.4.  Spacing and Joints

(1)  Shingles shall be spaced approximately 6 mm apart and offset at the joints in adjacent courses not less than 40 mm so that joints in alternate courses are staggered.

9.26.9.5.  Fastening

(1)  Shingles shall be fastened with 2 nails or staples located approximately 20 mm from the sides of the shingle and 40 mm above the exposure line.

9.26.9.6.  Exposure

(1)  The exposure of wood roof shingles shall conform to Table 9.26.9.6.

Table 9.26.9.6.

Exposure of Wood Shingles

Forming Part of Sentence 9.26.9.6.(1)

| Roof Slope | Maximum Exposure, mm |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | No. 1 or A Grade Length of Shingle, mm |  |  | No. 2 or B Grade Length of Shingle, mm |  |  |
|  | 400 | 450 | 600 | 400 | 450 | 600 |
| < 1 in 3 | 100 | 115 | 165 | 90 | 100 | 140 |
| ≥ 1 in 3 | 125 | 140 | 190 | 100 | 115 | 165 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 |

9.26.9.7.  Flashing

(1)  Flashing shall conform to Subsection 9.26.4.

9.26.9.8.  Eave Protection

(1)  Eave protection shall conform to Subsection 9.26.5.

9.26.10. Handsplit Roof Shakes

9.26.10.1.  Size and Thickness

(1)  Shakes shall be not less than 450 mm long and not less than 100 mm nor more than 350 mm wide with a butt thickness of not more than 32 mm and not less than 9 mm.

9.26.10.2.  Underlay

(1)  Where eave protection is not provided, an underlay conforming to the requirements in Article 9.26.6.1. for wood shingles shall be laid as a strip not less than 900 mm wide along the eaves.

(2)  A strip of material similar to that described in Sentence (1) not less than 450 mm wide shall be interlayed between each course of shakes with the bottom edge of the strip positioned above the butt line at a distance equal to double the exposure of the shakes.

(3)  Interlayed strips in Sentence (2) shall be lapped at least 150 mm at hips and ridges in a manner that will prevent water from reaching the roof sheathing.

9.26.10.3.  Spacing and Joints

(1)  Shakes shall be spaced 6 mm to 9 mm apart and the joints in one course shall be separated not less than 40 mm from joints in adjacent courses.

9.26.10.4.  Fastening

(1)  Shakes shall be fastened with nails located approximately 20 mm from the sides of the shakes and 40 mm above the exposure line.

9.26.10.5.  Exposure

(1)  The exposure of wood shakes shall not exceed

(a)	190 mm for shakes not less than 450 mm long, and

(b)	240 mm for shakes not less than 600 mm long.

9.26.10.6.  Flashing

(1)  Flashing shall conform to Subsection 9.26.4.

9.26.10.7.  Eave Protection

(1)  Eave protection shall conform to Subsection 9.26.5.

9.26.11. Built-Up Roofs

9.26.11.1.  Quantity of Materials

(1)  The quantities of bituminous materials used on built-up roofs shall conform to Table 9.26.11.1.

Table 9.26.11.1.

Quantities of Bitumen for Built-Up Roofs

Forming Part of Sentence 9.26.11.1.(1)

| Type of Roof | Amount of Bitumen per Square Metre of Roof Surface |  |
| --- | --- | --- |
|  | Mopping Coats Between Layers | Flood Coat |
| Asphalt and aggregate | 1 kg | 3 kg |
| Coal-tar and aggregate | 1.2 kg | 3.6 |
| Cold process roofing | 0.75 L cold process cement | 2 L cold process top coating |
| Column 1 | 2 | 3 |

9.26.11.2.  Coal-Tar and Asphalt Products

(1)  Coal-tar products and asphalt products shall not be used together in built-up roof construction.

9.26.11.3.  Roof Felts

(1)  Bitumen roofing felts shall be not less than No. 15 felt.

9.26.11.4.  Aggregate Surfacing

(1)  Aggregate used for surfacing built-up roofs shall be clean, dry and durable and shall consist of particles of gravel, crushed stone or air-cooled blast furnace slag having a size of from 6 mm to 15 mm.

(2)  The minimum amount of aggregate surfacing per square metre of roof surface shall be 15 kg gravel or crushed stone or 10 kg crushed slag.

9.26.11.5.  Flashing

(1)  Flashing shall conform to Subsection 9.26.4.

9.26.11.6.  Number of Layers

(1)  Built-up roofing shall consist of at least 3 mopped-down layers of roofing felt flood coated with bitumen.

9.26.11.7.  Installation of Layers

(1)  In hot process applications each layer of bitumen-saturated felt shall be laid while the bitumen is hot, with each layer overlapping the previous one.

(2)  The full width under each lap referred to in Sentence (1) shall be coated with bitumen so that in no place does felt touch felt.

(3)  Felt shall be laid free of wrinkles and shall be rolled directly into the hot bitumen and broomed forward and outward from the centre to ensure complete adhesion.

9.26.11.8.  Roofing over Wood-Based Sheathing

(1)  Except as permitted in Sentence (2), built-up roofing applied over wood, plywood, OSB or waferboard roof sheathing shall be laid over an additional base layer of felt laid dry over the entire roof deck with at least a 50 mm headlap and a 50 mm sidelap between each sheet.

(2)  Where plywood, OSB or waferboard roof sheathing is used, the dry layer of felt required in Sentence (1) may be omitted when the joints are taped and the sheathing is primed with asphalt.

9.26.11.9.  Attachment to Decking

(1)  Roofing shall be securely attached to the decking or where insulation is applied above the deck, the insulation shall be securely attached to the deck before the first layer of felt is fastened to the insulation.

9.26.11.10.  Cant Strips

(1)  Except as permitted in Sentence (4), a cant strip shall be provided at the edges of roofs.

(2)  No fewer than 2 plies of the roofing membrane shall be carried over the top of the cant strip.

(3)  Flashing shall extend over the top of the cant strip and be shaped to form a drip.

(4)  The cant strip required in Sentence (1) may be omitted where a gravel stop is provided at the edge of roofs.

(5)  The roofing membranes shall be carried over the edge of the roof before the gravel stop is fastened and 2 plies of roofing membrane mopped to the top surface of the gravel stop referred to in Sentence (4) before the flood coat is applied.

(6)  The gravel stop referred to in Sentence (4) shall extend over the edge of the roof to form a drip or shall be flashed so that the flashing extends over the edge to form a drip.

9.26.12. Selvage Roofing

9.26.12.1.  Double Coverage

(1)  Wide selvage asphalt roofing shall provide double coverage over the entire roof surface.

9.26.12.2.  Joints

(1)  Plies of selvage roofing shall be cemented together to ensure a water-tight joint.

9.26.13. Sheet Metal Roofing

9.26.13.1.  Thickness

(1)  Sheet metal roofing shall be not less than

(a)	0.33 mm thick galvanized steel,

(b)	0.46 mm thick copper,

(c)	0.46 mm thick zinc, or

(d)	0.48 mm thick aluminum.

9.26.14. Glass Reinforced Polyester Roofing

9.26.14.1.  Support

(1)  Where glass reinforced polyester roofing panels are not supported by roof decking but span between spaced supports, the panels shall be designed to support the specified roof loads.

9.26.15. Hot Applied Rubberized Asphalt Roofing

9.26.15.1.  Installation

(1)  Hot applied rubberized asphalt roofing shall be installed in accordance with CGSB 37-GP-51M, “Application or Rubberized Asphalt, Hot Applied, for Roofing and Waterproofing”.

9.26.16. Polyvinyl Chloride Sheet Roofing

9.26.16.1.  Installation

(1)  Polyvinyl chloride sheet applied roofing membrane shall be installed in accordance with CGSB 37-GP-55M, “Application of Sheet Applied Flexible Polyvinyl Chloride Roofing Membrane”.

9.26.17. Concrete Roof Tiles

9.26.17.1.  Coverage

(1)  Concrete roof tiles shall be installed according to CAN/CSA-A220.1, “Installation of Concrete Roof Tiles.”

9.26.18. Downspouts and Roof Drains

9.26.18.1  Roof Drains

(1)  When roof drains are provided they shall conform to Part 7.

9.26.18.2.  Downspouts

(1)  Where downspouts are provided and are not connected to a sewer, extensions shall be provided to carry rainwater away from the building in a manner which will prevent soil erosion.

Section 9.27. Cladding

9.27.1. Scope

9.27.1.1.  Application

(1)  This Section applies to exterior wall coverings of lumber, wood shingles, shakes, asbestos-cement shingles and sheets, plywood, OSB, waferboard, hardboard, asphalt shingles, vinyl, aluminum and steel including trim, soffits and flashing.

9.27.1.2.  Stucco and Masonry Veneer

(1)  Requirements for stucco shall conform to Section 9.28 and requirements for masonry veneer shall conform to Section 9.20.

9.27.1.3.  Asphalt Shingles

(1)  Where asphalt shingles are used as siding, they shall conform to the requirements in Section 9.26 for asphalt roof shingles.

9.27.2. General

9.27.2.1.  Required Cladding

(1)  Exterior walls shall be protected with cladding, including flashing, trim and other special purpose accessory pieces required for the cladding system being used, to restrict the entry of rain and snow into the wall assembly.

9.27.2.2.  Clearance from Ground

(1)  Not less than a 200 mm clearance shall be provided between the finished ground level and siding that is adversely affected by moisture such as wood, plywood, OSB, waferboard and hardboard.

9.27.2.3.  Clearance from Roof Surface

(1)  Not less than a 50 mm clearance shall be provided between a roof surface and cladding that is adversely affected by moisture such as wood, plywood, OSB, waferboard and hardboard.

9.27.2.4.  Insulating Asphalt Siding

(1)  Insulating asphalt cladding shall be ventilated by not less than a 10 mm air space behind the cladding.

9.27.3. Flashing

9.27.3.1.  Materials

(1)  Flashing shall consist of not less than

(a)	1.73 mm thick sheet lead,

(b)	0.33 mm thick galvanized steel,

(c)	0.46 mm thick copper,

(d)	0.46 mm thick zinc,

(e)	0.48 mm thick aluminum, or

(f)	1.02 mm thick vinyl.

9.27.3.2.  Installation

(1)  Flashing shall be installed at every horizontal junction between 2 different exterior finishes, except where the upper finish overlaps the lower finish.

(2)  Except as provided in Sentence (4), flashing shall be applied over exterior wall openings where the vertical distance from the bottom of the eave to the top of the trim is more than one-quarter of the horizontal overhang of the eave.

(3)  Flashing shall be installed so that it extends upwards not less than 50 mm behind the sheathing paper and forms a drip on the outside edge.

(4)  Where a window or exterior door is designed to be installed without head flashing, the exterior flange of the window or door frame shall be bedded into a non-hardening type caulking material and the exterior flange screwed down over the caulking material to the wall framing to form a waterproof joint.

9.27.4. Caulking

9.27.4.1.  Required Caulking

(1)  Caulking shall be provided where required to prevent the entry of water into the structure.

(2)  Caulking shall be provided between masonry, siding or stucco and the adjacent door and window frames or trim, including sills unless such locations are completely protected from the entry of rain.

(3)  Caulking shall be provided at vertical joints between different cladding materials unless the joint is suitably lapped or flashed to prevent the entry of rain.

9.27.4.2.  Materials

(1)  Caulking shall be

(a)	a non-hardening type suitable for exterior use,

(b)	selected for its ability to resist the effects of weathering, and

(c)	compatible with and adhere to the substrate to which it is applied.

(2)  Caulking shall conform to

(a)	CGSB 19-GP-5M, “Sealing Compound, One Component, Acrylic Base, Solvent Curing”,

(b)	CAN/CGSB-19.13-M, “Sealing Compound, One Component, Elastomeric, Chemical Curing”,

(c)	CGSB 19-GP-14M, “Sealing Compound, One Component, Butyl-Polyisobutylene Polymer Base, Solvent Curing”, or

(d)	CAN/CGSB-19.24-M, “Multi-Component, Chemical Curing Sealing Compound”.

9.27.5. Attachment of Cladding

9.27.5.1.  Attachment

(1)  Except as permitted in Sentences (2) to (7), cladding shall be nailed to the framing members, furring members or to blocking between the framing members.

(2)  Vertical lumber and stucco lath or reinforcing are permitted to be attached to sheathing only where the sheathing consists of not less than

(a)	14.3 mm lumber,

(b)	12.5 mm plywood, or

(c)	12.5 mm OSB or waferboard.

(3)  Vertically applied metal siding and wood shingles and shakes are permitted to be attached to the sheathing only where the sheathing consists of not less than

(a)	14.3 mm lumber,

(b)	7.5 mm plywood, or

(c)	7.5 mm OSB or waferboard.

(4)  Asbestos-cement shingles are permitted to be attached to the sheathing only when the sheathing consists of not less than

(a)	14.3 mm lumber,

(b)	9.5 mm plywood, or

(c)	9.5 mm OSB or waferboard.

(5)  Where wood shingles or shakes are applied to sheathing which is not suitable for attaching the shingles or shakes, the shingles or shakes may be attached to a wood lath not less than 38 mm by 9.5 mm thick securely nailed to the framing and applied as described in Article 9.27.7.5.

(6)  Where asbestos-cement shingles are applied to sheathing that is not suitable for attaching the shingles, the shingles may be fastened to a wood lath not less than 89 mm by 9.5 mm thick securely nailed to the framing.

(7)  Lath referred to in Sentence (6) shall be applied so that it overlaps the preceding shingle course by not less than 20 mm.

9.27.5.2.  Blocking

(1)  Blocking for the attachment of cladding shall be not less than 38 mm by 38 mm lumber securely nailed to the framing and spaced not more than 600 mm o.c.

9.27.5.3.  Furring

(1)  Except as permitted in Sentences 9.27.5.1.(5) and (6), furring for the attachment of cladding shall be not less than 19 mm by 38 mm lumber when applied over sheathing.

(2)  When applied without sheathing, furring referred to in Sentence (1) shall be not less than

(a)	19 mm by 64 mm lumber on supports spaced not more than 400 mm o.c., or

(b)	19 mm by 89 mm on supports spaced not more than 600 mm o.c.

(3)  Furring referred to in Sentence (1) shall be

(a)	securely fastened to the framing, and

(b)	spaced not more than 600 mm o.c.

9.27.5.4.  Size and Spacing of Fasteners

(1)  Nail or staple size and spacing for the attachment of cladding and trim shall conform to Table 9.27.5.4.

Table 9.27.5.4.

Attachment of Cladding

Forming Part of Sentence 9.27.5.4.(1)

| Type of Cladding | Minimum Nail or Staple Length, mm | Minimum Number of Nails or Staples | Maximum Nail or Staple Spacing |
| --- | --- | --- | --- |
| Wood trim | 51 | — | 600 mm (o.c.) |
| Lumber siding or horizontal siding made from sheet metal | 51 | — | 600 mm (o.c.) |
| Metal siding | 38 | — | 600 mm (o.c.) (nailed to framing) |
| Handsplit wood shakes |  |  |  |
| up to 200 mm in width | 51 | 2 | — |
| over 200 mm in width | 51 | 3 | — |
| Wood shingles and machine grooved shakes |  |  |  |
| 200 mm in width | 32 | 2 | — |
| over 200 mm in width | 32 | 3 | — |
| Asbestos-cement shingles | 32 | 2 | — |
| Panel or sheet type cladding |  |  | 150 mm along edges |
| up to 7 mm thick | 38 | — | 300 mm |
| more than 7 mm thick | 51 | — | along intermediate supports |
| Column 1 | 2 | 3 | 4 |

9.27.5.5.  Fastener Materials

(1)  Nails or staples for the attachment of cladding and wood trim shall be corrosion-resistant and shall be compatible with the cladding material.

9.27.5.6.  Expansion and Contraction

(1)  Fasteners for metal or vinyl cladding shall be positioned to permit expansion and contraction of the siding.

9.27.5.7.  Penetration of Fasteners

(1)  Fasteners for shakes and shingles shall penetrate through the nail-holding base or not less than 19 mm into the framing.

(2)  Fasteners for cladding other than that described in Sentence (1) shall penetrate through the nail-holding base or not less than 25 mm into the framing.

9.27.6. Lumber Siding

9.27.6.1.  Materials

(1)  Lumber siding shall be sound, free of knot holes, loose knots, through checks or splits.

9.27.6.2.  Thickness and Width

(1)  Drop, rustic, novelty, lapped board and vertical wood siding shall be not less than 14.3 mm thick and not more than 286 mm wide.

(2)  Bevel siding shall be

(a)	not less than 5 mm thick at the top, and

(b)	not less than

(i)	12 mm thick at the butt for sidings 184 mm or less in width, and

(ii)	14.3 mm thick at the butt for sidings wider than 184 mm.

(3)  Bevel siding shall be not more than 286 mm wide.

9.27.6.3.  Joints

(1)  Lumber siding shall prevent water from entering at the joints by the use of lapped or matched joints or by vertical wood battens.

(2)  Siding shall overlap not less than 1 mm per 16 mm width of lumber, but not less than

(a)	9.5 mm for matched siding,

(b)	25 mm for lapped bevel siding, or

(c)	12 mm for vertical battens.

9.27.7. Wood Shingles and Machine Grooved Shakes

9.27.7.1.  Materials

(1)  Shingles and shakes shall conform to

(a)	CSA O118.1-M, “Western Red Cedar Shingles and Shakes,” or

(b)	CSA O118.2-M, “Eastern White Cedar Shingles”.

(2)  Western red cedar shakes shall be at least No. 1 grade and shingles at least No. 2 grade, except that No. 3 grade may be used for the lower course of double course applications.

(3)  Eastern white cedar shakes shall be at least B (clear) grade, except that C grade may be used for the lower course of double course applications.

9.27.7.2.  Width

(1)  Shingles and shakes shall be not less than 65 mm nor more than 350 mm wide.

9.27.7.3.  Fasteners

(1)  Shingles or shakes shall be fastened with nails located approximately 20 mm from each edge and not less than 25 mm above the exposure line for single-course applications, or approximately 50 mm above the butt for double-course applications.

9.27.7.4.  Offsetting of Joints

(1)  In single-course application, joints in succeeding courses shall be offset at least 40 mm so that joints in any 2 of 3 consecutive courses are staggered.

(2)  In double-course application, joints in the outer course shall be offset from joints in the under-course by not less than 40 mm, and joints in succeeding courses shall be offset not less than 40 mm.

9.27.7.5.  Fastening to Lath

(1)  When lath is used with double-course application, it shall be spaced according to the exposure and securely fastened to the framing.

(2)  The butts of the under-course of the application referred to in Sentence (1) shall rest on the top edge of the lath.

(3)  The outer course of the application referred to in Sentence (1) shall be fastened to the lath with nails of sufficient length to penetrate through the lath.

(4)  The butts of the shingles or shakes shall be so located that they project not less than 12 mm below the bottom edge of the lath referred to in Sentence (1).

(5)  If wood lath is not used, the butts of the under-course shingles or shakes of the application referred to in Sentence (1) shall be located 12 mm above the butts of the outer course.

9.27.7.6.  Exposure and Thickness

(1)  The exposure and butt thickness of shingles shall conform to Table 9.27.7.6.

Table 9.27.7.6.

Exposure and Thickness of Wood Shingles and Machine Grooved Shakes

Forming Part of Sentence 9.27.7.6.(1)

| Shake or Shingle Length, mm | Maximum Exposure, mm |  | Minimum Butt Thickness, mm |
| --- | --- | --- | --- |
|  | Single Coursing | Double Coursing |  |
| 400 | 190 | 305 | 10 |
| 450 | 216 | 356 | 11 |
| 600 | 292 | 406 | 13 |
| Column 1 | 2 | 3 | 4 |

9.27.8. Asbestos-Cement Shingles and Sheets

9.27.8.1.  Material Standards

(1)  Asbestos-cement shingles and sheets shall conform to

(a)	CAN/CGSB-34.4-M, “Siding, Asbestos Cement, Shingles and Clapboards”,

(b)	CAN/CGSB-34.5-M, “Sheets, Asbestos Cement, Corrugated”,

(c)	CAN/CGSB-34.14-M, “Sheets, Asbestos Cement, Decorative”,

(d)	CAN/CGSB-34.16, “Sheets, Asbestos Cement, Flat, Fully Compressed”,

(e)	CAN/CGSB-34.17-M, “Sheets, Asbestos Cement, Flat, Semi-compressed”, or

(f)	CAN/CGSB-34.21-M, “Panels, Sandwich Asbestos, Cement and Insulating Cores”.

9.27.8.2.  Weight and Thickness

(1)  Asbestos-cement shingles shall weigh not less than 8.06 kg/m2.

(2)  Asbestos-cement sheet shall be not less than

(a)	4.75 mm thick where applied to studs spaced not more than 400 mm o.c., and,

(b)	6 mm thick where applied to studs spaced not more than 600 mm o.c.

(3)  Where applied over sheathing, the thickness of asbestos-cement sheet shall be not less than 3.15 mm.

9.27.8.3.  Fastening of Shingles

(1)  Asbestos-cement shingles shall be fastened with nails located not less than 25 mm above the exposure line.

9.27.8.4.  Joints of Shingles

(1)  Asbestos-cement shingles shall be installed so that vertical joints in succeeding courses are staggered.

(2)  Asphalt-coated backer strips shall be installed behind each vertical joint.

(3)  Shingles referred to in Sentence (1) shall have not less than a 25 mm head lap.

9.27.8.5.  Joints in Panels

(1)  Vertical joints of asbestos-cement panels shall be protected with batten strips, caulking or other suitable method.

(2)  Horizontal joints of asbestos-cement panels shall be lapped, flashed, caulked or otherwise suitably protected.

9.27.9. Plywood

9.27.9.1.  Material Standards

(1)  Plywood cladding shall be exterior type conforming to

(a)	CSA O115-M, “Hardwood and Decorative Plywood”,

(b)	CSA O121-M, “Douglas Fir Plywood”,

(c)	CSA O151-M, “Canadian Softwood Plywood”, or

(d)	CSA O153-M, “Poplar Plywood”.

9.27.9.2.  Thickness

(1)  Plywood cladding shall be not less than 6 mm thick when applied directly to sheathing.

(2)  When applied directly to framing or over furring strips, plywood cladding thickness shall conform to Table 9.27.9.2.

Table 9.27.9.2.

Minimum Plywood Cladding Thickness

Forming Part of Sentence 9.27.9.2.(2)

| Spacing of Supports, mm | Minimum Thickness, mm |  |
| --- | --- | --- |
|  | Face Grain Parallel to Supports | Face Grain Right Angles to Supports |
| 400 | 8 | 6 |
| 600 | 11 | 8 |
| Column 1 | 2 | 3 |

(3)  The thickness of grooved or textured plywood shall be measured at the point of least thickness.

9.27.9.3.  Edge Treatment

(1)  The edges of plywood cladding shall be treated with a suitable paint or sealer.

9.27.9.4.  Panel Siding

(1)  Plywood applied in panels shall have all edges supported.

(2)  Not less than a 2 mm gap shall be provided between panels referred to in Sentence (1).

(3)  Vertical joints in cladding referred to in Sentence (1) shall be protected with batten strips or caulking when the plywood joints are not matched.

(4)  Horizontal joints in cladding referred to in Sentence (1) shall be lapped not less than 25 mm or shall be suitably flashed.

9.27.9.5.  Lapped Strip Siding

(1)  Plywood applied in horizontal lapped strips shall have not less than a 2 mm gap provided at the butted ends, which shall be caulked.

(2)  The horizontal joints of siding described in Sentence (1) shall be lapped not less than 25 mm.

(3)  Wedges shall be inserted under all vertical butt joints and at all corners when horizontal lapped plywood is applied without sheathing.

9.27.10. Hardboard

9.27.10.1.  Material Standards

(1)  Factory-finished hardboard cladding shall conform to CAN/CGSB-11.5M, “Hardboard, Precoated, Factory-Finished, for Exterior Cladding”.

(2)  Hardboard cladding which is not factory finished shall conform to Types 1, 2 or 5 in CAN/CGSB-11.3-M, “Hardboard”.

9.27.10.2.  Thickness

(1)  Type 1 or 2 hardboard cladding shall be not less than

(a)	6.0 mm thick when applied over sheathing that provides continuous support, and

(b)	7.5 mm thick when applied to furring or framing members not more than 400 mm o.c.

(2)  Type 5 hardboard cladding shall be not less than 9.0 mm thick when applied over sheathing that provides continuous support or over furring or framing members spaced not more than 400 mm o.c.

(3)  Where hardboard cladding is grooved, the grooves shall not extend more than 1 500 mm into the required thickness.

9.27.10.3.  Panel Siding

(1)  Hardboard cladding applied in panels shall have all edges supported with not less than a 5 mm gap provided between sheets.

(2)  Vertical joints in cladding described in Sentence (1) shall be protected with batten strips or caulking when the joints are not matched.

(3)  Horizontal joints in cladding described in Sentence (1) shall be lapped not less than 25 mm or shall be suitably flashed.

9.27.10.4.  Lapped Strip Siding

(1)  Hardboard applied in horizontal lapped strips shall have not less than a 5 mm gap provided at the butted ends, which shall be caulked or otherwise protected with suitable mouldings.

(2)  The horizontal joints of siding described in Sentence (1) shall overlap not less than 1 mm per 16 mm width of siding board but not less than 9.5 mm for matched joint siding or 25 mm for lapped siding.

9.27.10.5.  Clearance

(1)  Not less than 3 mm clearance shall be provided between hardboard siding and door or window frames.

9.27.11. OSB and Waferboard

9.27.11.1.  Material Standard

(1)  OSB and waferboard cladding shall conform to CAN3-O437.0, “OSB and Waferboard”.

9.27.11.2.  Thickness

(1)  OSB conforming to O-2 grade shall be not less than 6.0 mm thick where applied directly to sheathing.

(2)  OSB conforming to O-2 grade applied directly to framing or over furring strips, shall conform to the thickness shown for plywood in Table 9.27.9.2.

(3)  OSB conforming to O-1 grade and waferboard conforming to R-1 grade shall be not less than 7.9 mm thick where applied directly to sheathing.

(4)  Where applied directly to framing or over furring strips, OSB conforming to O-1 grade and waferboard conforming to R-1 grade shall be not less than

(a)	9.5 mm thick on supports spaced not more than 400 mm o.c., and

(b)	12.7 mm thick on supports spaced not more than 600 mm o.c.

9.27.11.3.  Panel Cladding

(1)  OSB and waferboard applied in panels shall have all edges supported and treated with a primer or sealer.

(2)  Not less than a 3 mm gap shall be provided between sheets in cladding described in Sentence (1).

(3)  Vertical joints in cladding described in Sentence (1) shall be protected with batten strips or caulking when the OSB and waferboard joints are not matched.

(4)  Horizontal joints in cladding described in Sentence (1) shall be lapped not less than 25 mm or shall be suitably flashed.

9.27.11.4.  Clearance

(1)  At least a 3 mm clearance shall be provided between OSB and waferboard cladding and door or window frames.

9.27.12. Metal Siding

9.27.12.1.  Material Standards

(1)  Horizontal and vertical strip steel siding, including flashing and trim accessories, shall conform to CAN/CGSB-93.4-M, “Galvanized Steel and Aluminum-Zinc Coated Steel Siding, Soffits and Fascia, Prefinished, Residential”.

(2)  Steel sheet cladding shall have a minimum thickness of 0.3 mm and conform to CAN/CGSB-93.3-M, “Prefinished Galvanized and Aluminum-Zinc Alloy Sheet, for Residential Use”.

(3)  Horizontal and vertical strip aluminum siding, including flashing and trim accessories, shall conform to CAN/CGSB-93.2-M, “Prefinished Aluminum Siding, Soffits and Fascia, for Residential Use”.

(4)  Aluminum sheet cladding shall conform to CAN/CGSB-93.1-M, “Sheet, Aluminum Alloy, Prefinished, Residential” and shall have a thickness of not less than 0.58 mm, except that siding supported by backing or sheathing shall have a thickness of not less than 0.46 mm.

9.27.13. Vinyl Siding

9.27.13.1.  Material Standard

(1)  Vinyl siding, including flashing and trim accessories, shall conform to CGSB 41-GP-24Ma, “Siding, Soffits and Fascia, Rigid Vinyl”.

9.27.13.2.  Attachment

(1)  The attachment of vinyl siding shall conform to the requirements in Subsection 9.27.5. for metal siding.

Section 9.28. Stucco

9.28.1. General

9.28.1.1.  Sheathing Beneath Stucco

(1)  Sheathing shall be provided beneath stucco applied over wood-frame walls except as permitted in Article 9.28.4.2.

(2)  Where applied beneath stucco, sheathing shall conform to Subsection 9.23.16.

9.28.1.2.  Lath and Reinforcing

(1)  Stucco lath or reinforcing shall be used to attach stucco to any substrate other than masonry.

(2)  Stucco lath or reinforcing shall be used to attach stucco to masonry where

(a)	the masonry is soft-burned tile or brick of less strength than the stucco, or

(b)	the masonry surface is not sound, clean and sufficiently rough to provide a good key.

(3)  Stucco applied over masonry chimneys shall be reinforced.

9.28.1.3.  Concrete Masonry Units

(1)  Stucco finish shall not be applied over concrete masonry units less than one month old unless the units have been cured by the autoclave process.

9.28.1.4.  Clearance over Ground Level

(1)  Stucco shall be not less than 200 mm above finished ground level except when it is applied over concrete or masonry.

9.28.1.5.  Flashing and Caulking

(1)  Flashing and caulking used with stucco shall conform to Subsections 9.27.3. and 9.27.4., except that if aluminum flashing is used, it shall be separated from the stucco by an impervious membrane or coating.

9.28.2. Stucco Materials

9.28.2.1.  Portland Cement

(1)  Portland cement shall conform to CAN/CSA-A5, “Portland Cement”.

9.28.2.2.  Aggregate

(1)  Aggregate shall be clean, well-graded natural sand or sand manufactured from crushed stone, gravel or air-cooled blast furnace slag and shall contain no significant amounts of deleterious material.

(2)  Aggregate grading shall conform to Table 9.28.2.2.

Table 9.28.2.2.

Aggregate Grading for Stucco

Forming Part of Sentence 9.28.2.2.(2)

| Sieve Sizes, mm | % Passing |  |
| --- | --- | --- |
|  | Maximum | Minimum |
| 4 | — | 100 |
| 2 | — | 90 |
| 1 | 90 | 60 |
| 0.5 | 60 | 45 |
| 0.25 | 30 | 10 |
| 0.125 | 5 | — |
| Column 1 | 2 | 3 |

9.28.2.3.  Water

(1)  Water shall be clean and free of significant amounts of deleterious material.

9.28.3. Fasteners

9.28.3.1.  Materials

(1)  Fasteners for stucco lath or reinforcing shall be corrosion-resistant and of a material other than aluminum.

9.28.3.2.  Nails and Staples

(1)  Nails for stucco lath or reinforcing shall be not less than 3.2 mm diam with a head diameter of not less than 11.1 mm.

(2)  Staples for stucco lath reinforcing shall be not less than 1.98 mm diam or thickness.

(3)  Staples and nails for attaching stucco lath or reinforcing to vertical surfaces shall be of sufficient length to penetrate 25 mm into framing members or to the full depth of the sheathing where the sheathing is used for attachment.

(4)  On horizontal surfaces nails for stucco lath or reinforcing shall be not less than 38 mm long.

9.28.4. Stucco Lath

9.28.4.1.  Materials

(1)  Rib lath or expanded metal stucco mesh shall be

(a)	copper-alloy steel coated with rust-inhibitive paint after fabrication, or

(b)	galvanized.

(2)  Woven or welded wire mesh shall be galvanized.

9.28.4.2.  No Sheathing Required

(1)  Sheathing need not be provided beneath stucco where not less than 1.19 mm diam galvanized wire is applied horizontally to the framing at vertical intervals not exceeding 150 mm, or where paper-backed welded wire metal lath is used.

9.28.4.3.  Stucco Lath Specifications

(1)  Stucco lath shall conform to Table 9.28.4.3.

Table 9.28.4.3.

Stucco Lath

Forming Part of Sentence 9.28.4.3.(1)

| Location | Type of Lath | Minimum Diam. of Wire, mm | Maximum Mesh Opening | Minimum Mass, kg/m2 |
| --- | --- | --- | --- | --- |
| Vertical surfaces | Welded or | 1.19 | 25 mm | — |
|  | woven | 1.35 | 38 mm | — |
|  | wire | 1.60 | 51 mm | — |
|  | Stucco mesh reinforcing (expanded metal) | — | 25.8 cm2 | 0.98 |
| Horizontal surfaces(1) | 9.5 mm rib lath | — | — | 1.84 |
|  | Cedar lath | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 |

9.28.4.4.  Self-Furring Devices

(1)  Stucco lath shall be held not less than 6 mm away from the backing by means of suitable self-furring devices.

9.28.4.5.  Application of Stucco Lath

(1)  Stucco lath shall be applied with the long dimension horizontal.

(2)  Horizontal and vertical joints shall be lapped not less than 50 mm.

(3)  End joints of stucco lath shall be staggered and shall occur over framing members.

(4)  External corners of stucco lath shall be reinforced with a vertical strip of lath or reinforcing extending not less than 150 mm on both sides of the corner, or the lath or reinforcing shall extend around corners not less than 150 mm.

9.28.4.6.  Fastening

(1)  Stucco lath shall be fastened in conformance with Subsection 9.27.5.

(2)  Fasteners on vertical surfaces shall be spaced not more than

(a)	150 mm o.c. vertically and 400 mm o.c. horizontally, or

(b)	100 mm o.c. vertically and 600 mm o.c. horizontally.

(3)  Nailing patterns other than those required in Sentence (2) are permitted to be used provided there are not fewer than 20 fasteners per square metre of wall surface.

(4)  Fasteners on horizontal surfaces shall be spaced not more than

(a)	150 mm o.c. along the framing members when members are spaced not more than 400 mm o.c., and

(b)	100 mm o.c. along members when members are spaced not more than 600 mm o.c.

9.28.5. Stucco Mixes

9.28.5.1.  Mixes

(1)  Stucco mixes shall conform to Table 9.28.5.1.

Table 9.28.5.1.

Stucco Mixes

Forming Part of Sentence 9.28.5.1.(1)

| Materials, volume |  |  |  |
| --- | --- | --- | --- |
| Portland Cement | Masonry Cement | Lime | Aggregate |
| 1 | — | 0.25 to 1 | 3.25 to 4 parts per part of cementitious material |
| 1 | 1 | — |  |
| Column 1 | 2 | 3 | 4 |

9.28.5.2.  Pigments

(1)  Pigment if used shall consist of pure mineral oxides inert to the action of sun, lime and cement.

(2)  Pigment shall not exceed 6% of the portland cement by weight.

9.28.5.3.  Mixing

(1)  Materials shall be thoroughly mixed before and after water is added.

(2)  Stucco shall be applied not later than 3 h after the initial mixing.

9.28.6. Stucco Application

9.28.6.1.  Low Temperature Conditions

(1)  The base for stucco shall be maintained above freezing.

(2)  Stucco shall be maintained at a temperature of not less than 10°C during application and for not less than 48 h afterwards.

9.28.6.2.  Number of Coats and Total Thickness

(1)  Stucco shall be applied with at least 2 base coats and one finish coat, providing a total thickness of not less than 15 mm, measured from the face of the lath or face of the masonry where no lath is used.

9.28.6.3.  First Coat

(1)  The first coat shall be not less than 6 mm thick, measured from the face of the lath or masonry, fully embedding the lath.

(2)  The surface of the first coat shall be scored to provide a key with the second coat.

9.28.6.4.  Second Coat

(1)  The second coat shall be not less than 6 mm thick.

(2)  The surface of the second shall be lightly roughened to provide a key with the finish coat if the finish coat is other than stone dash.

9.28.6.5.  Finish Coat

(1)  When the finish coat is other than stone dash, the base shall be dampened but not saturated before the finish coat is applied.

(2)  The thickness of the finish coat shall be not less than 3 mm.

(3)  When a stone dash finish is used, the stone shall be partially embedded in the second coat before the second coat starts to set or stiffen.

Section 9.29. Interior Wall and Ceiling Finishes

9.29.1. General

9.29.1.1.  Fire Protection and Sound Control

(1)  A wall or ceiling finish shall also conform to the appropriate requirements in Sections 9.10 and 9.11 in addition to the requirements in this Section.

9.29.2. Waterproof Wall Finish

9.29.2.1.  Where Required

(1)  Waterproof finish shall be provided to a height of not less than

(a)	1 800 mm above the floor in shower stalls,

(b)	1 200 mm above the rims of bathtubs equipped with showers, and

(c)	400 mm above the rims of bathtubs not equipped with showers.

9.29.2.2.  Materials

(1)  Waterproof finish shall consist of ceramic, plastic or metal tile, sheet vinyl, tempered hardboard, laminated thermosetting decorative sheets or linoleum.

9.29.3. Wood Furring

9.29.3.1.  Size and Spacing of Furring

(1)  Wood furring for the attachment of wall and ceiling finishes shall conform to Table 9.29.3.1.

Table 9.29.3.1.

Size and Spacing of Furring

Forming Part of Sentence 9.29.3.1.(1)

| Maximum Spacing of Furring, mm | Minimum Size of Furring, mm |  |  |
| --- | --- | --- | --- |
|  | Maximum Spacing of Furring Supports |  |  |
|  | Continuous Supports | 400 mm (o.c.) | 600 mm (o.c.) |
| 300 | 19 x 38 | 19 x 38 | 19 x 64 |
| 400 | 19 x 38 | 19 x 38 | 19 x 64 |
| 600 | 19 x 38 | 19 x 64 | 19 x 89 |
| Column 1 | 2 | 3 | 4 |

9.29.3.2.  Fastening

(1)  Furring shall be fastened to the framing or to wood blocks with not less than 51 mm nails.

9.29.4 Plastering

9.29.4.1.  Application

(1)  Application of plaster wall and ceiling finishes including installation of metal or gypsum lath, shall conform to CSA A82.30-M, “Interior Furring, Lathing and Gypsum Plastering”.

9.29.5. Gypsum Board Finish (Taped Joints)

9.29.5.1.  Application

(1)  The requirements for application of gypsum board in this Subsection apply to the single layer application of gypsum board to wood furring or framing using nails or screws.

(2)  Gypsum board applications not described in this Subsection shall conform to CSA A82.31-M, “Gypsum Board Application”.

9.29.5.2.  Materials

(1)  Gypsum products shall conform to

(a)	CAN/CSA-A82.27, “Gypsum Board”,

(b)	ASTM C 36, “Gypsum Wallboard”,

(c)	ASTM C 37, “Gypsum Lath”,

(d)	ASTM C 442, “Gypsum Backing Board and Coreboard”,

(e)	ASTM C 558, “Gypsum Base for Veneer Plaster”,

(f)	ASTM C 630, “Water Resistant Gypsum Board Backing”,

(g)	ASTM C 931, “Exterior Gypsum Soffit Board”, or

(h)	ASTM C 960, “Predecorated Gypsum Board”.

9.29.5.3.  Maximum Spacing of Supports

(1)  Maximum spacing of supports for gypsum board applied as a single layer shall conform to Table 9.29.5.3.

Table 9.29.5.3.

Spacing of Supports for Gypsum Board

Forming Part of Sentence 9.29.5.3.(1)

| Thickness mm | Orientation of Board to Framing | Maximum Spacing of Supports, mm o.c. |  |  |
| --- | --- | --- | --- | --- |
|  |  | Walls | Ceilings |  |
|  |  |  | Painted Finish | Water-Based Texture Finish |
| 9.5 | parallel | — | — | — |
|  | perpendicular | 400 | 400 | — |
| 12.7 | parallel | 600 | 400 | — |
|  | perpendicular | 600 | 600 | 400 |
| 15.9 | parallel | 600 | 400 | — |
|  | perpendicular | 600 | 600 | 600 |
| Column 1 | 2 | 3 | 4 | 5 |

9.29.5.4.  Support of Insulation

(1)  Gypsum board supporting insulation shall be at least 12.7 mm thick.

9.29.5.5.  Length of Fasteners

(1)  The length of fasteners for gypsum board shall conform to Table 9.29.5.5., except that lesser depths of penetration are permitted for assemblies required to have a fire-resistance rating provided it can be shown, on the basis of fire tests, that such depths are adequate for the required rating.

Table 9.29.5.5.

Fastener Penetration into Wood Supports

Forming Part of Sentence 9.29.5.5.(1)

| Required Fire-Resistance Rating of Assembly | Minimum Penetration, mm |  |  |  |
| --- | --- | --- | --- | --- |
|  | Walls |  | Ceilings |  |
|  | Nails | Screws | Nails | Screws |
| Not required | 20 | 15 | 20 | 15 |
| 45 min | 20 | 20 | 30 | 30 |
| 1 h | 20 | 20 | 45 | 45 |
| 1.5 h | 20 | 20 | 60 | 60 |
| Column 1 | 2 | 3 | 4 | 5 |

9.29.5.6.  Nails

(1)  Nails for fastening gypsum board to wood supports shall conform to CSA B111. “Wire Nails, Spikes and Staples”.

9.29.5.7.  Screws

(1)  Screws for fastening gypsum board to wood supports shall conform to ASTM C1002, “Steel Drill Screws for the Application of Gypsum Board or Metal Plaster Bases”.

9.29.5.8.  Spacing of Nails

(1)  For single-layer application nails shall be spaced not more than 180 mm on ceiling supports, and not more than 200 mm apart along vertical wall supports, except that nails may be spaced in pairs about 50 mm apart every 300 mm along such wall or ceiling supports.

(2)  Where the ceiling sheets are supported by the wall sheets around the perimeter of the ceiling, this support may be considered as equivalent to nailing at this location.

(3)  The uppermost wall nails shall be not more than 200 mm below the ceiling.

(4)  Nails shall be located not less than 10 mm from the side or edge of the board.

(5)  Nails shall be driven so that the heads are below the plane of the board surface but do not puncture the paper.

9.29.5.9.  Spacing of Screws

(1)  Where gypsum board is applied with drywall screws, the screws shall be spaced not more than 300 mm o.c. along supports, except that on vertical surfaces the screws may be spaced 400 mm o.c. where the supports are not more than 400 mm o.c.

9.29.5.10.  Low Temperature Conditions

(1)  In cold weather, heat shall be provided to maintain a temperature of not below 10°C for 48 h prior to taping and finishing and maintained for not less than 48 h thereafter.

9.29.6. Plywood Finish

9.29.6.1.  Thickness

(1)  Except as provided in Sentences (2) and (3), the minimum thickness of plywood interior finish shall conform to Table 9.29.6.1.

Table 9.29.6.1.

Thickness of Plywood Interior Finish

Forming Part of Articles 9.29.6.1. and 9.29.6.2.

| Maximum Spacing of Supports, mm | Minimum Thickness, mm (1) |  |
| --- | --- | --- |
|  | On supports with no Horizontal Blocking | On Supports with Blocking at Vertical Intervals not Exceeding 1.2 m |
| 400 | 4.7 | 4.0 |
| 600 | 8.0 | 4.7 |
| Column 1 | 2 | 3 |

Note to Table 9.29.6.1.

(1)	 Thickness limits shall apply to the net effective thickness (NET) of grooved, striated, textured and/or embossed panels and to the actual thickness of flat panels.

(2)  A manufacturing tolerance of -0.4 mm may be applied to the thicknesses listed in Table 9.29.6.1.

(3)  No minimum thickness is required where plywood is applied over continuous backing.

9.29.6.2.  Grooved Plywood

(1)  Except as permitted in Sentence (2), where plywood for interior finish is grooved, the grooves shall not extend through the face ply and into the plies below the face ply unless the groove is supported by framing or furring.

(2)  If the grain of the face ply is at right angles to the supporting members, the groove is permitted to extend into the plies below the face ply provided the thickness of the plywood exceeds the value shown in Table 9.29.6.1. by an amount equal to not less than the depth of penetration of the grooves into the plies below the face ply.

9.29.6.3.  Nails and Staples

(1)  Nails for attaching plywood finishes shall not be less than 38 mm casing or finishing nails spaced not more than 150 mm o.c. along edge supports and 300 mm o.c. along intermediate supports, except that staples providing equivalent lateral resistance may also be used.

9.29.6.4.  Edge Support

(1)  All plywood edges shall be supported by furring, blocking or framing.

9.29.7. Hardboard Finish

9.29.7.1.  Material Standard

(1)  Hardboard shall conform to CAN/CGSB-11.3-M, “Hardboard”.

9.29.7.2.  Thickness

(1)  Hardboard shall be not less than

(a)	3 mm thick where applied over continuous back-up,

(b)	6 mm thick where applied to supports spaced not more than 400 mm o.c., and

(c)	9 mm thick where applied to supports spaced not more than 600 mm o.c.

9.29.7.3.  Nails

(1)  Nails for fastening hardboard shall be casing or finishing nails not less than 38 mm long, spaced not more than 150 mm o.c. along edge supports and 300 mm o.c. along intermediate supports.

9.29.7.4.  Edge Support

(1)  All hardboard edges shall be supported by furring, blocking or framing where the back-up is not continuous.

9.29.8. Insulating Fibreboard Finish

9.29.8.1.  Material Standard

(1)  Insulating fibreboard shall conform to CAN/CSA-A247-M, “Insulating Fibreboard”.

9.29.8.2.  Thickness

(1)  Insulating fibreboard sheets shall be not less than 11.1 mm thick on supports not more than 400 mm o.c.

(2)  Insulating fibreboard tile shall be not less than 12.7 mm thick on supports spaced not more than 400 mm o.c.

9.29.8.3.  Nails

(1)  Nails for fastening fibreboard sheets shall be not less than 2.6 mm shank diameter casing or finishing nails of sufficient length to penetrate not less than 20 mm into the supports.

(2)  Nails shall be spaced not more than 100 mm o.c. along edge supports and 200 mm o.c. along intermediate supports.

9.29.8.4.  Edge Support

(1)  All fibreboard edges shall be supported by blocking, furring or framing.

9.29.9. Particleboard, OSB or Waferboard Finish

9.29.9.1. Material Standard

(1)  Particleboard finish shall conform to CAN3-O188.1, “Interior Mat-Formed Wood Particleboard”.

(2)  OSB or waferboard and strandboard finish shall conform to CSA O437.0, “OSB and Waferboard”.

9.29.9.2.  Minimum Thickness

(1)  Except as provided in Sentences (2) and (3), the minimum thickness of O-2 grade OSB used as an interior finish shall conform to that shown for plywood in Table 9.29.6.1.

(2)  Thickness listed in Table 9.29.6.1. shall permit a manufacturing tolerance of - 0.4 mm.

(3)  No minimum thickness is required where O-2 grade OSB is applied over continuous backing.

(4)  OSB conforming to O-1 grade, waferboard conforming to R-1 grade and particleboard shall be

(a)	not less than 6.35 mm thick on supports not more than 400 mm o.c.,

(b)	not less than 9.5 mm thick on supports not more than 600 mm o.c., and

(c)	not less than 6.35 mm thick on supports not more than 600 mm o.c. in walls where blocking is provided at midwall height.

9.29.9.3.  Nails

(1)  Nails for fastening particleboard, OSB or waferboard shall be not less than 38 mm casing or finishing nails spaced not more than 150 mm o.c. along edge supports and 300 mm o.c. along intermediate supports.

9.29.9.4.  Edge Support

(1)  All particleboard, OSB or waferboard edges shall be supported by furring, blocking or framing.

9.29.10. Wall Tile Finish

9.29.10.1.  Tile Application

(1)  Ceramic tile shall be set in a mortar base or applied with an adhesive.

(2)  Plastic tile shall be applied with an adhesive.

9.29.10.2.  Mortar Base

(1)  When ceramic tile is applied to a mortar base the cementitious material shall consist of 1 part portland cement to not more than one-quarter part lime by volume.

(2)  The cementitious material described in Sentence (1) shall be mixed with not less than 3 nor more than 5 parts of aggregate per part of cementitious material by volume.

(3)  Mortar shall be applied over metal lath or masonry.

(4)  Ceramic tile applied to a mortar base shall be thoroughly soaked and pressed into place forcing the mortar into the joints while the tile is wet.

9.29.10.3.  Adhesives

(1)  Adhesives to attach ceramic and plastic tile shall be applied to the finish coat or brown coat of plaster that has been steel-trowelled to an even surface or to gypsum board or to masonry provided the masonry has an even surface.

9.29.10.4.  Moisture Resistant Backing

(1)  Ceramic and plastic tile installed on walls around bathtubs or showers shall be applied over moisture resistant backing.

9.29.10.5.  Joints between Tiles and Bathtub

(1)  The joints between wall tiles and a bathtub or shower shall be suitably caulked with material conforming to CAN/CGSB-19.22-M, “Mildew Resistant Sealing Compound for Tubs and Tile”.

Section 9.30. Flooring

9.30.1. General

9.30.1.1.  Required Finish Flooring

(1)  Finished flooring shall be provided in all residential occupancies.

9.30.1.2.  Water Resistance

(1)  Finished flooring in bathrooms, kitchens, public entrance halls, laundry and general storage areas shall consist of resilient flooring, felted-synthetic-fibre floor coverings, concrete, terrazzo, ceramic tile, mastic or other types of flooring providing similar degrees of water resistance.

9.30.1.3.  Sleepers

(1)  Wood sleepers supporting finished flooring over a concrete base supported on the ground shall be not less than 19 mm by 38 mm and shall be treated with a wood preservative.

9.30.1.4.  Finish Quality

(1)  Finished flooring shall have a surface that is smooth, even and free from roughness or open defects.

9.30.2. Panel-Type Underlay

9.30.2.1.  Required Underlay

(1)  A panel-type underlay shall be provided under resilient flooring, parquet flooring, ceramic tile, felted-synthetic-fibre floor coverings or carpeting laid over lumber subflooring.

(2)  A panel-type underlay shall be provided under resilient flooring, parquet flooring, felted-synthetic-fibre floor coverings or carpeting on panel-type subflooring whose edges are unsupported.

(3)  Panel-type underlay shall be provided under resilient flooring on waferboard or strandboard subflooring.

(4)  Panel-type underlay shall be provided under ceramic tile applied with adhesive.

9.30.2.2.  Materials and Thickness

(1)  Panel-type underlay shall be not less than 6 mm thick and shall conform to

(a)	CAN/CGSB-11.3-M, “Hardboard”,

(b)	CSA O115-M, “Hardwood and Decorative Plywood”,

(c)	CSA O121-M, “Douglas Fir Plywood”,

(d)	CSA O151-M, “Canadian Softwood Plywood”,

(e)	CSA O153-M, “Poplar Plywood”,

(f)	CAN3-O188.1-M, “Interior Mat-Formed Wood Particleboard”, or

(g)	CSA O437.0, “OSB and Waferboard”

(2)  Reserved

9.30.2.3.  Fastening

(1)  Panel-type underlay shall be fastened to the subfloor with staples, annular grooved flooring nails or spiral nails, spaced not more than 150 mm o.c. along the edges and 200 mm o.c. both ways at other locations.

(2)  Nails for panel-type underlay shall be not less than 19 mm long for 6 mm thick underlay and 22 mm long for 7.9 mm thick underlay.

(3)  Staples for panel-type underlay shall

(a)	have not less than a 1.2 mm shank diameter or thickness with a 4.7 mm crown, and

(b)	be not less than

(i)	22 mm long for 6 mm underlay, and

(ii)	28 mm long for 7.9 mm and 9.5 mm underlay.

9.30.2.4.  Joints Offset

(1)  Where panel-type underlay is required to be installed over plywood, or OSB or waferboard, the joints in the underlay shall be offset at least 200 mm from the joints in the underlying subfloor.

9.30.2.5.  Surface Defects

(1)  Underlay beneath resilient or ceramic floors applied with an adhesive shall have all holes or open defects on the surface patched so that the defects will not be transmitted to the finished surface.

9.30.3. Wood Strip Flooring

9.30.3.1.  Thickness

(1)  The thickness of wood strip flooring shall conform to Table 9.30.3.1.

Table 9.30.3.1.

Thickness of Wood Strip Flooring

Forming Part of Sentence 9.30.3.1.(1)

| Type of Flooring | Max. Joist Spacing, mm | Minimum Thickness of Flooring, mm |  |
| --- | --- | --- | --- |
|  |  | With Subfloor | No Subfloor |
| Matched hardwood | 400 | 7.9 | 19.0 |
| (interior use only) | 600 | 7.9 | 33.3 |
| Matched softwood | 400 | 19.0 | 19.0 |
| (interior or exterior use) | 600 | 19.0 | 31.7 |
| Square edge softwood | 400 | — | 25.4 |
| (exterior use only) | 600 | — | 38.1 |
| Column 1 | 2 | 3 | 4 |

9.30.3.2.  Strip Direction and End Joints

(1)  Wood strip flooring shall not be laid parallel to lumber subflooring unless a separate underlay is provided.

(2)  If wood strip flooring is applied without a subfloor, it shall be laid at right angles to the joists so that the end joints are staggered and occur over supports or are end matched.

(3)  If the flooring is end matched, it shall be laid so that no 2 adjoining strips break joints in the same space between supports and each strip bears on no fewer than 2 supports.

9.30.3.3.  Nailing

(1)  When nails are used, wood strip flooring shall be toe nailed or face nailed with not less than 1 nail per strip at the spacings shown in Table 9.30.3.3., except that face nailed strips of more than 25 mm in width shall have at least 2 nails per strip.

Table 9.30.3.3.

Nailing of Wood Strip Flooring

Forming Part of Sentence 9.30.3.3.(1)

| Finish Floor Thickness, mm | Minimum Length of Flooring Nails, mm | Maximum Spacing of Flooring Nails, mm |
| --- | --- | --- |
| 7.9 | 38(1) | 200 |
| 11.1 | 51 | 300 |
| 19.0 | 57 | 400 |
| 25.4 | 63 | 400 |
| 31.7 | 70 | 600 |
| 38.1 | 83 | 600 |
| Column 1 | 2 | 3 |

Note to Table 9.30.3.3.:

(1) See Article 9.30.3.4.

(2)  Face nails shall be countersunk and the holes filled with suitable filler.

9.30.3.4.  Staples

(1)  Staples are permitted to be used to fasten wood strip flooring not more than 7.9 mm in thickness and not more than 50 mm in width provided the staples

(a)	are not less than 29 mm long,

(b)	have a shank diameter of not less than 1.19 mm,

(c)	have a crown of not less than 4.7 mm, and

(d)	are spaced not more than 400 mm o.c.

(2)  Staples are permitted to be used to fasten wood strip flooring not more than 19 mm in thickness and not more than 83 mm in width provided the staples

(a)	are not less than 51 mm long,

(b)	have a shank diameter of not less than 1.82 mm,

(c)	have a crown of not less than 12.7 mm, and

(d)	are spaced not more than 400 mm o.c.

9.30.4. Parquet Flooring

9.30.4.1.  Adhesive

(1)  Adhesive used to attach parquet block flooring shall be suitable for bonding wood to the applicable subfloor material.

9.30.5. Resilient Flooring

9.30.5.1.  Materials

(1)  Resilient flooring used on concrete slabs supported on ground shall consist of asphalt, rubber, vinyl-asbestos, unbacked vinyl or vinyl with an inorganic type backing.

(2)  Flooring described in Sentence (1) shall be attached to the base with a suitable waterproof and alkali-resistant adhesive.

9.30.6. Ceramic Tile

9.30.6.1.  Application

(1)  Ceramic tile shall be set in a mortar bed or applied to a sound smooth base with a suitable adhesive.

(2)  Panel-type subfloor to which ceramic tile is to be applied with adhesive shall have its edges supported according to Article 9.23.14.3.

9.30.6.2.  Ceramic Tile Set in Mortar Bed

(1)  When ceramic tile is set in mortar bed, the bed shall be not less than 32 mm thick. A 50 mm by 50 mm galvanized wire mesh shall be placed in the mortar bed, and asphalt sheathing paper, felt or polyethylene film shall be applied under the mortar bed when the mortar is applied over wood subfloors.

(2)  The mortar bed described in Sentence (1) shall consist of by volume

(a)	1 part portland cement,

(b)	4 parts sand, and

(c)	1 part water.

(3)  The tile joints for the ceramic tile in Sentence (1) shall be grouted with cement grout which shall be compressed into joints between the tiles and then wiped smooth.

9.30.6.3.  Reinforcement for Panel-Type Wood Sheathing

(1)  Except as permitted in Article 9.30.6.4., when ceramic floor tiles are set on panel-type wood sheathing, one of the following assemblies for reinforcing the floor assembly shall be used

(a)	20 mm thick plywood or waferboard with all edges supported by at least 38 mm by 38 mm blocking with floor joists spaced not more than 400 mm o.c., with 6 mm underlay,

(b)	sheathing with a thickness which conforms to Table 9.23.14.5.A. or a rating which complies to Table 9.23.14.5.B. and has an underlay consisting of 15.9 mm plywood or waferboard with offsetting joints, with a 4 mm gap between the sheets, or

(c)	sub-floor sheathing reinforced with close spaced 38 mm by 38 mm blocking at spacings at least half that of the floor joist spacing.

9.30.6.4.  Ceramic Tile Applied to Mortar Bed with Adhesive

(1)  When ceramic tile is applied to a mortar bed with adhesive, the bed shall be not less than 12.5 mm thick.

(2)  The mortar bed described in Sentence (1) shall consist of by volume

(a)	1 part portland cement,

(b)	3 parts sand, and

(c)	1 part water.

(3)  Not less than one layer of galvanized diamond mesh wire lath shall be imbedded in the mortar bed.

(4)  Joints in the wire lath required by Sentence (3) shall be overlapped not less than 12 mm.

(5)  The wire lath required in Sentence (1) shall be fastened to the subfloor with

(a)	lath nails not less than 38 mm in length spaced not more than 150 mm o.c., or

(b)	staples not less than 38 mm in length spaced not more than 150 mm o.c.

(6)  Asphalt sheathing paper, felt or polyethylene film shall be applied between the mortar bed and the wood subfloor.

(7)  Floor joists supporting the mortar bed described in Sentence (1) shall

(a)	be spaced not more than 400 mm o.c., and

(b)	have not less than two rows of 38 mm x 38 mm cross bridging.

(8)  The tile joints for the ceramic tile in Sentence (1) shall be grouted with cement grout which shall be compressed into joints between the tiles and then wiped smooth.

Section 9.31. Plumbing Facilities

9.31.1. Scope

9.31.1.1.  Application

(1)  This Section applies to plumbing facilities and plumbing systems within dwelling units that are not within a recreational camp or a camp for housing of workers.

(2)  Plumbing facilities other than those required in dwelling units shall conform to Subsection 3.7.4.

9.31.2. General

9.31.2.1.  General

(1)  The construction of plumbing systems shall conform to Part 7.

9.31.2.2.  Corrosion Protection

(1)  Metal pipes in contact with cinders or other corrosive material shall be protected by a heavy coating of bitumen or other corrosion protection.

9.31.2.3.  Grab Bars

(1)  When provided, grab bars shall be capable of resisting a load of not less than 1.3 kN applied vertically or horizontally.

9.31.3. Water Supply and Distribution

9.31.3.1.  Required Water Supply

(1)  Reserved

9.31.3.2.  Required Connections

(1)  In a dwelling unit with a water distribution system, piping for hot and cold water shall be connected to every kitchen sink, lavatory, bathtub, shower, slop sink and laundry area.

(2)  Piping for cold water shall be run to every water closet and hose bib.

9.31.4. Required Facilities

9.31.4.1.  Required Fixtures

(1)  In a dwelling unit with a water distribution system, a kitchen sink, lavatory, bathtub or shower stall and water closet shall be provided.

9.31.4.2.  Laundry Fixtures

(1)  Laundry facilities or a space for laundry facilities shall be provided in every dwelling unit or grouped elsewhere in the building in a location conveniently accessible to occupants of every dwelling unit.

9.31.4.3.  Hot Water Supply

(1)  In a dwelling unit with a water distribution system, a hot water supply shall be provided.

(2)  A water distribution system supplying hot water to plumbing fixtures shall conform to the requirements in Subsection 7.6.5.

9.31.4.4.  Floor Drains

(1)  A floor drain shall be installed in a basement forming part of a dwelling unit.

(2)  Where gravity drainage to a sanitary drainage system is possible, the floor drain in Sentence (1) shall be connected to the sanitary drainage system.

(3)  Where gravity drainage to a sanitary drainage system is not possible, the floor drain in Sentence (1) is permitted to be connected to a storm drainage system, dry well or drainage ditch.

(4)  A floor drain shall be provided in a public laundry room, garbage room, incinerator room, boiler or heating room, serving more than one dwelling unit.

9.31.4.5.  Required Facilities at Recreational Camps and a Camp for Housing of Workers

(1)  A minimum of one water closet or privy shall be provided

(a)	for every ten campers of each sex in a recreational camp, and

(b)	for every ten employees of each sex in a camp for housing of workers.

(2)  In recreational camps and a camp for housing of workers, at least two lavatories or provision for a pail or other portable container of sound construction shall be provided for each of the water closets or privies required in Sentence (1).

(3)  A camp for housing of workers shall

(a)	have at least one shower or other area of bathing, and

(b)	provide for at least one washing machine or laundry tub for every fifteen beds.

9.31.5. Reserved

9.31.6. Service Water Heating Facilities

9.31.6.1.  Hot Water Temperature

(1)  Where a hot water supply is required by Article 9.31.4.3., equipment shall be installed to provide to every dwelling unit an adequate supply of service hot water with a temperature range from 45°C to 60°C.

9.31.6.2.  Supply Source

(1)  Service hot water is permitted to be distributed from a centrally located heater to supply the entire building or may be supplied by an individual service water heater for each dwelling unit.

9.31.6.3.  Equipment and Installation

(1)  Every service water heater and its installation shall conform to Part 7.

(2)  Reserved

(3)  Where a building is located in seismic zone 4, 5, or 6, service water heaters shall be anchored to the structure to prevent overturning or breaking of gas, oil or electrical lines.

9.31.6.4.  Corrosion-Resistant Coating

(1)  Where storage tanks for service water heaters are steel, they shall be coated with zinc, vitreous enamel (glass lined), hydraulic cement or other corrosion-resistant material.

9.31.6.5.  Fuel-Burning Heaters

(1)  Fuel-burning service water heaters shall be connected to a chimney flue conforming to Section 9.21.

9.31.6.6.  Heating Coils

(1)  Heating coils of service water heaters shall not be installed in a flue or in the combustion chamber of a boiler or furnace heating a building.

Section 9.32. Ventilation

9.32.1. General

9.32.1.1.  Application

(1)  This Section applies to the ventilation of rooms and spaces in residential occupancies by natural ventilation and to self-contained mechanical ventilation systems serving only one dwelling unit.

(2)  Mechanical ventilation systems, other than self-contained systems serving single dwelling units, shall conform to Part 6.

(3)  Ventilation of rooms and spaces in other than residential occupancies shall conform to Part 6.

(4)  A storage garage for more than 5 cars shall be ventilated in accordance with Part 6.

9.32.1.2.  Mechanical Ventilation for Dwelling Units

(1)  Every dwelling unit that is supplied with electrical power shall be provided with a mechanical ventilation system in accordance with Subsection 9.32.3.

9.32.1.3.  Ventilation of Rooms and Spaces

(1)  Except as permitted in Sentence (2), rooms or spaces in a dwelling unit shall be ventilated by natural means in accordance with Subsection 9.32.2.

(2)  The natural ventilation of rooms or spaces required in Sentence (1) may be provided by mechanical means.

(3)  Where a room or space is not provided with natural ventilation as described in Sentence (1), mechanical ventilation shall be provided to exhaust inside air from or to introduce outside air to that room or space at the rate of one-half air change per hour if the room or space is mechanically cooled in summer, and one air change per hour if it is not.

9.32.2. Natural Ventilation

9.32.2.1.  Natural Ventilation Area

(1)  The unobstructed openable ventilation area to the outdoors for rooms and spaces in residential buildings ventilated by natural means shall conform to Table 9.32.2.1.

Table 9.32.2.1.

Natural Ventilation

Forming Part of Sentence 9.32.2.1.(1)

| Location |  | Minimum Unobstructed Area |
| --- | --- | --- |
| Within dwelling unit | Bathrooms or water closet rooms | 0.09 m2 |
|  | Unfinished basement space | 0.2 per cent of the floor area |
|  | Dining rooms, living rooms, bedrooms, kitchens, combined rooms, dens, recreation rooms and all other finished rooms | 0.28 m2 per room or combination of rooms |
| Other than within dwelling unit | Bathrooms or water closet rooms | 0.09 m2 per water closet |
|  | Sleeping areas | 0.14 m2 per occupant |
|  | Laundry rooms, kitchens, recreation rooms | 4 per cent of the floor area |
|  | Corridors, storage rooms and other similar public rooms or spaces | 2 per cent of the floor area |
|  | Unfinished basement space not used on a shared basis | 0.2 per cent of the floor area |
| Column 1 | 2 | 3 |

(2)  Where a vestibule opens directly off a living or dining room within a dwelling unit, ventilation to the outdoors for such rooms may be through the vestibule.

9.32.2.2.  Protection from Weather and Insects

(1)  Openings for natural ventilation other than windows shall be constructed to provide protection from the weather and insects.

(2)  Screening shall be of rust-proof material.

9.32.3. Mechanical Ventilation

9.32.3.1.  General

(1)  For the purposes of this Subsection a non-solid fuel-fired appliance shall be classified as

(a)	direct vented whereby the combustion air is supplied directly from the outdoors to the combustion chamber via a sealed passageway, and the products of combustion are exhausted directly outdoors through an independent sealed vent,

(b)	mechanically vented induced draft whereby combustion air is supplied from within the building envelope and the products of combustion are positively conveyed to the outdoors by means of a dedicated sealed vent, or

(c)	natural draft whereby combustion air is supplied from within the building envelope and the products of combustion are conveyed to the outdoors through a chimney or Type B vent.

(2)  For the purposes of this Subsection a dwelling unit shall be categorized as

(a)	Type I when

(i)	all fuel-fired combustion appliances located in the dwelling unit are direct vented or except for fireplaces, are mechanically vented induced draft, and

(ii)	the dwelling unit does not contain a solid fuel-fired combustion appliance,

(b)	Type II when a solid fuel-fired combustion appliance is installed in a Type I dwelling unit,

(c)	Type III when a mechanically vented induced draft non-solid fuel-fired fireplace or a natural draft appliance is present, or

(d)	Type IV when electric space heating is present.

9.32.3.2.  Required Mechanical Ventilation

(1)  The mechanical ventilation system required in Article 9.32.1.2. shall comply with

(a)	Part 6, or

(b)	this Subsection for a mechanical ventilation system in a Type I, Type II or Type IV dwelling unit.

9.32.3.3.  Total Ventilation Capacity

(1)  The minimum total ventilation capacity of the ventilation system required in Clauses 9.32.3.2.(1)(b) shall be the sum of the individual room capacities given in Table 9.32.3.3.

Table 9.32.3.3.

Ventilation Capacity

Forming Part of Sentence 9.32.3.3.(1)

| Room | Capacity, L/s |
| --- | --- |
| Master bedroom(1) | 10 |
| Other bedrooms | 5 |
| Living room(2) | 5 |
| Dining room(2) | 5 |
| Kitchen | 5 |
| Family Room(2) | 5 |
| Recreation room | 5 |
| Basement(3) | 10 |
| Other habitable rooms(4) | 5 |
| Bathroom or water closet room | 5 |
| Laundry room | 5 |
| Utility room | 5 |
| Column 1 | 2 |

Notes to Table 9.32.3.3.:

(1) At least one bedroom in each dwelling unit shall be designated as the master bedroom.

(2) Ventilation capacities assigned to any combined living/dining or family/dining space shall be determined as if the spaces were individual rooms.

(3)	 Where a basement incorporates rooms of the types designated in this Table, the assigned ventilation capacities for each room shall be as specified for those types of rooms. Basement areas used for other purposes that exceed 2/3 of the total basement floor area shall be assigned a fan capacity of 10 L/s.  Those that are less than 2/3 of the total floor area shall be assigned 5 L/s.

(4)	 Other habitable rooms shall be assigned a ventilation capacity of 5 L/s. This does not include spaces intended solely for access, egress, storage or service equipment.

9.32.3.4.  Principal Exhaust

(1)  A principal exhaust fan shall be installed and shall be rated to provide not less than the capacity given in Table 9.32.3.4.A.

Table 9.32.3.4.A.

Principal Exhaust Fan Capacity

Forming Part of Sentence 9.32.3.4.(1)

| Number of Bedrooms in Dwelling Unit | Capacity, L/s |
| --- | --- |
| 1 | 15 |
| 2 | 22.5 |
| 3 | 30 |
| 4 | 37.5 |
| More than 4 | Part 6 design |
| Column 1 | 2 |

(2)  Except as permitted in Sentence (3), the principal exhaust fan shall be controlled by a manual switch.

(3)  A principal exhaust fan required under this Article may be controlled by a dehumidistat or other automatic control device where the manual switch required in Sentence (2) is capable of activating the fan regardless of the setting of the automatic control.

(4)  The switches required in Sentences (2) and (3) shall be centrally located in the dwelling unit and shall be identified with the words VENTILATION FAN.

(5)  The principal exhaust required in this Article may be provided by means of a heat recovery ventilator installed in accordance with Article 9.32.3.11.

(6)  Where the installed capacity of the principal exhaust fan exceeds the minimum capacity required in Sentence (1) by more than 50%, the control required in Sentence (2) shall include provision to allow reduction of the flow to within ±10% of the minimum capacity specified in Sentence (1).

(7)  Where an exhaust air intake for the principal exhaust fan is connected directly to the duct system of a forced air heating system or other central air circulating system, it shall

(a)	be connected to the return air side of the system, and

(b)	be connected not less than 1 000 mm upstream from any outdoor air supply duct.

(8)  Where an exhaust air intake for the principal exhaust fan is located in the kitchen, it shall be located in the ceiling or on the wall within 300 mm of the ceiling.

(9)  Single or multiple exhaust ducts serving the principal exhaust fan required by Sentence (1) shall be sized according to Part 6 except that they may be sized according to Table 9.32.3.4.B. where

(a)	the longest total duct length, from intake grille to outdoor hood, does not exceed 12 m, and

(b)	the number of elbows does not exceed 4,

but, in any case, they shall not be smaller than recommended by the manufacturer of the fan.

Table 9.32.3.4.B.

Principal Exhaust Duct Size

Forming Part of Sentence 9.32.3.4.(9)

| Number of Bedrooms in Dwelling Unit | Minimum Exhaust Duct Diameter |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Ducts Connected to Inlet and Outlet of Principal Exhaust Fan |  |  | Ducts Connected to One Side Only of Principal Exhaust Fan |  |
|  | Smooth Duct, mm | Flexible Duct, mm | Smooth Duct, mm |  | Flexible Duct, mm |
| 1 | 100 | 125 | 100 |  | 125 |
| 2 | 125 | 150 | 125 |  | 150 |
| 3 | 125 | 150 | 150 |  | 175 |
| 4 | 150 | 175 | 150 |  | 175 |
| More than 4 | Part 6 Design | Part 6 Design | Part 6 Design |  | Part 6 Design |
| Column 1 | 2 | 3 | 4 |  | 5 |

(10)  In applying Table 9.32.3.4.B.

(a)	where there is more than one exhaust air inlet duct connected directly to the fan, the diameter of the inlet ducts may be decreased by 25 mm, and

(b)	where the exhaust duct is connected to the duct system of a forced air heating system, the duct diameter shall be increased by 25 mm.

9.32.3.5.  Supplemental Exhaust

(1)  Additional supplemental exhaust capacity shall be installed as necessary so that the total capacity of all kitchen, bathroom, water closet room and other supplemental exhaust air inlets is not less than the total ventilation capacity, as required in Article 9.32.3.3., minus the principal exhaust fan capacity, as required in Article 9.32.3.4.

(2)  An exhaust air intake shall be installed in each kitchen, bathroom and water closet room.

(3)  Where the intake for a supplemental exhaust fan other than a range hood or range-top fan is installed in a kitchen, it shall be installed in the ceiling or on the wall within 300 mm of the ceiling.

(4)  Exhaust ducts serving the required kitchen, bathroom, water closet room and other supplemental exhaust air inlets shall be sized according to Part 6 except that they may be sized according to Table 9.32.3.5. where

(a)	the total duct length does not exceed 9 m, and

(b)	the number of elbows does not exceed 4,

but, in any case, they shall not be smaller than recommended by the manufacturers of the fans.

Table 9.32.3.5.

Kitchen, Bathroom and Water Closet Room Exhaust Duct Size

Forming Part of Sentence 9.32.3.5.(4)

| Fan Capacity, L/s | Minimum Exhaust Duct Diameter(1) |  |
| --- | --- | --- |
|  | Ducts Connected to Inlet & Outlet of Exhaust Fan, mm | Ducts Connected to One Side Only of Exhaust Fan, mm |
| 25 | 125 | 125 |
| 50 | 150 | 150 |
| Column 1 | 2 | 3 |

Note to Table 9.32.3.5.:

(1) Where flexible duct is used, the duct diameter shall be increased by 25 mm.

(5)  A supplemental exhaust fan required by this Article shall be provided with a manual switch located in the same room as the exhaust air inlet.

(6)  Where a supplemental fan required by this Article is controlled by a dehumidistat or other automatic control in addition to the manual switch required by Sentence (5), the manual switch shall be capable of activating the fan regardless of the setting of the automatic control.

(7)  Supplemental exhaust required in this Article may be provided by means of a heat recovery ventilator installed in accordance with Article 9.32.3.11.

9.32.3.6.  Ventilation Systems Coupled with Forced Air Heating Systems

(1)  This Article applies to a mechanical ventilation system in a dwelling unit that contains a forced air heating system and the forced air heating system is used for delivery of ventilation air.

(2)  In a Type I dwelling unit, a ventilation supply inlet is not required.

(3)  In a Type II dwelling unit, the mechanical ventilation system shall include a heat recovery ventilator, coupled to the forced air heating system, installed in accordance with Article 9.32.3.11.

(4)  The forced air heating system circulation fan shall be controlled by a manual switch located adjacent to the ventilation fan switch required in Sentence 9.32.3.4.(4).

(5)  The switch required in Sentence (4) shall be identified by the words CIRCULATION FAN.

9.32.3.7.  Ventilation Systems Not Coupled with Forced Air Heating Systems

(1)  This Article applies to a mechanical ventilation system in a dwelling unit that

(a)	does not contains a forced air heating system, or

(b)	contains a forced air heating system and the forced air heating system is not used for circulation of the ventilation air.

(2)  The mechanical ventilation system shall introduce air to and circulate air throughout the dwelling unit in compliance with this Article.

(3)  The mechanical system in this Article shall include a heat recovery ventilator installed in accordance with Article 9.32.3.11.

(4)  Outdoor air shall be distributed by a ductwork system from the heat recovery ventilator required in Sentence (3) to each bedroom, to any storey without a bedroom and, if there is no storey without a bedroom, to the principal living area.

(5)  A supply duct from the outdoors to the heat recovery ventilator required and a main distribution trunk duct shall be provided and shall be sized according to Part 6, except that, the supply duct and the main distribution trunk duct may be sized according to Table 9.32.3.7.A. where

(a)	the total duct length from the outdoor hood to any supply register does not exceed 21 m, and

(b)	the total number of fittings does not exceed 8.

Table 9.32.3.7.A.

Minimum Outdoor Air Supply and Main Trunk Duct Sizes

Forming Part of Sentence 9.32.3.7.(5)

| Number of Bedrooms in Dwelling Unit | Minimum Outdoor Air Supply and Main Distribution Trunk Duct Diameter, mm |
| --- | --- |
| 1 | 150 |
| 2 | 150 |
| 3 | 175 |
| 4 | 175 |
| More than 4 | Part 6 design |
| Column 1 | 2 |

(6)  The outside air supply duct required by Sentence (5) shall not be considered to provide combustion and/or dilution air to fuel-burning appliances.

(7)  Branch supply ducts leading from the main distribution trunk duct required by Sentence (5) to the rooms to which outdoor air is to be distributed shall be provided and shall be sized according to Part 6 except that the branch supply ducts may be sized according to Table 9.32.3.7.B where

(a)	the total duct length from outdoor hood to supply register does not exceed 21 m, and

(b)	the total number of fittings does not exceed 8.

Table 9.32.3.7.B.

Minimum Branch Supply Duct Sizes

Forming Part of Sentence 9.32.3.7.(7)

| Room, Space or Storey Served | Minimum Branch Supply Duct Diameter |  |
| --- | --- | --- |
|  | 1 and 2 Bedroom Dwelling Units, mm | 3 and 4 Bedroom Dwelling Units, mm |
| Master bedroom | 100 | 100 |
| Other bedrooms | 75 | 75 |
| Storey with no bedrooms or living area | 75 | 100 |
| Column 1 | 2 | 3 |

(8)  In applying Sentence (7), where the dwelling unit has more than 4 bedrooms, ducting shall be sized according to Part 6.

(9)  All branch supply ducts which are not fitted with diffusers with adjustable balance stops shall be supplied with accessible dampers which can be adjusted and fixed in their adjusted positions and which include devices to indicate the positions of the dampers.

(10)  Provision shall be made for the free flow of air to all rooms by leaving gaps beneath doors, using louvred doors or installing grilles in doors.

9.32.3.8.  Protection Against Depressurization

(1)  When determining the need to provide protection against depressurization, consideration must be given to

(a)	whether the presence of soil gas is deemed to be a problem, and

(b)	the presence of solid fuel-fired combustion appliances.

(2)  Revoked:  O. Reg. 283/01, s. 5 (1).

(3)  Revoked:  O. Reg. 283/01, s. 5 (1).

(4)  Revoked:  O. Reg. 283/01, s. 5 (1).

(5)  Revoked:  O. Reg. 283/01, s. 5 (1).

(6)  Where a solid fuel-fired combustion appliance is installed, the ventilation system shall include a heat recovery ventilator which is designed to operate so that the flow of exhaust air does not exceed the flow of intake air in any operating mode, and which complies with the requirements of Article 9.32.3.11.

9.32.3.9.  Fan Ratings

(1)  Except as provided in Sentence (3), capacity and sound ratings for required fans shall be determined in accordance with CAN/CSA-C260, “Rating the Performance of Residential Mechanical Ventilating Equipment”.

(2)  Capacity ratings for required fans shall be based on a static pressure differential of 50 Pa, 25 Pa or 7.5 Pa depending on whether the fan is installed with ductwork connected on both sides, one side or neither side, respectively.

(3)  Except for heat recovery ventilators, exhaust fans required to make up any part of the total ventilation capacity required by Article 9.32.3.3. shall have a sound rating not greater than that specified in Table 9.32.3.9.

Table 9.32.3.9.

Fan Sound Rating

Forming Part of Sentence 9.32.3.9.(3)

| Type of Fan | Maximum Sound Ratings |  |
| --- | --- | --- |
|  | Sone | dBA |
| Principal exhaust | 2.5 | 55 |
| Kitchen | 3.5 | 60 |
| Bathroom or water closet room | 2.5 | 55 |
| Supply | 2.5 | 55 |
| Column 1 | 2 | 3 |

(4)  Required fans shall be installed according to the manufacturer’s instructions.

(5)  Mechanical ventilation devices shall conform to CSA-C22.2 No. 113, “Fans and Ventilators”.

9.32.3.10.  Ducts

(1)  Ventilation ducts shall conform to the requirements of Part 6 for supply ducts except that exhaust ducts that serve only a bathroom or water closet room may be of combustible material provided the duct is reasonably airtight and constructed of a material impervious to water.

(2)  Exhaust ducts shall not discharge into heated or unheated enclosed spaces.

(3)  Where an exhaust duct passes through or is adjacent to unheated space, the duct shall be insulated to not less than RSI 0.5.

(4)  Where a supply duct carrying outdoor air that is not tempered or not mixed with indoor air passes through heated space, it shall be insulated to not less than RSI 0.5 except that, where such a duct is exposed in the heated space for more than 3 m of length in the heated space, it shall be insulated to not less than the values listed in Table 9.32.3.10.A.

Table 9.32.3.10.A

Insulation of Fresh Air Supply Ducts

Forming Part of Sentence 9.32.3.10.(4)

| Outside Winter Design Temperature as per Article 2.5.1.1.(1), oC | Minimum Thermal Resistance, RSI |
| --- | --- |
| –7 to –11 | 0.5 |
| –12 to –17 | 0.9 |
| –18 to –24 | 1.2 |
| –25 to –29 | 1.4 |
| –30 to –34 | 1.8 |
| –35 and colder | 2.1 |
| Column 1 | 2 |

Note to Table 9.32.3.10.A:

(1) The outside winter design temperatures shall be those listed for the January 2.5 per cent values.

(5)  A kitchen exhaust duct not equipped with a filter at the inlet end shall be designed and installed so that the entire duct can be cleaned.

(6)  Ductwork for range hoods and range-top fans shall be of noncombustible, corrosion-resistant material and shall lead directly to the outdoors without connection to other exhaust fans or ducts.

(7)  Ductwork for range hoods and range-top fans shall be equipped with a grease filter at the intake.

(8)  All ductwork shall be permanently supported or clipped to prevent sagging, excessive movement and vibration.

(9)  All ducting connected to supply and exhaust fans shall be constructed so as to inhibit air leakage at joints.

(10)  Where rectangular duct is used in place of round duct, it shall be selected according to Table 9.32.3.10.B.

Table 9.32.3.10.B

Equivalent Duct Sizes

Forming Part of Sentence 9.32.3.10.(10)

| Required Round Duct Size, mm | Permitted Equivalent Rectangular Duct Size, mm |  |  |  |
| --- | --- | --- | --- | --- |
|  | Stack Duct | 100 mm Depth | 125 mm Depth | 150 mm Depth |
| 75 | 82 x 250 | 57 x 100 |  |  |
| 100 | 82 x 250 | 89 x 100 | 75 x 125 | 75 x 150 |
| 125 | 82 x 250 | 125 x 100 | 100 x 125 | 89 x 150 |
| 150 | 82 x 300 | 200 x 100 | 150 x 125 | 125 x 150 |
| 175 | 82 x 350 | 275 x 100 | 200 x 125 | 175 x 150 |
| More Than 175 | Part 6 Design | Part 6 Design | Part 6 Design | Part 6 Design |
| Column 1 | 2 | 3 | 4 | 5 |

9.32.3.11.  Heat Recovery Ventilators

(1)  Where a heat recovery ventilator is installed to provide all or part of the requirements of this Subsection, this Article shall apply.

(2)  Heat recovery ventilators shall be designed to provide a minimum 55% sensible heat recovery efficiency when tested to the low temperature thermal and ventilation performance test method set out in CAN/CSA-439-M, “Standard Methods of Test for Rating the Performance of Heat Recovery Ventilators”, at a Station 1 test temperature of −25°C at an air flow not less than 30 L/s.

(3)  Where a heat recovery ventilator is connected to a forced air heating system, the supply side of the ventilator shall be directly connected to the return air side of the forced air heating system.

(4)  Two or more heat recovery ventilators shall not be connected in parallel air flow to a common air supply duct unless specifically recommended by the manufacturer.

(5)  Two or more heat recovery ventilators shall not be connected in parallel air flow to a common downstream exhaust duct.

(6)  Heat recovery ventilators installed in unheated spaces shall be installed so as to avoid condensation of moisture on fans and motors in exhaust air, in accordance with the manufacturer’s instructions.

(7)  All start-up procedures recommended by the manufacturer including air balancing and air-flow determination shall be followed.

(8)  Free flow of condensate shall be provided in accordance with the manufacturer’s recommendations or, in their absence, a condensate drain of minimum 1/2 inch nominal pipe size pitched in the direction of flow and complete with a trap or condensate pump with sufficient capacity shall be installed.

(9)  The heat recovery ventilator and all condensate lines shall be installed in a space where the ambient temperature will not adversely affect the operation of the system.

(10)  When operating at the rate required in Article 9.32.3.4., the supply and exhaust airflow rates of the heat recovery ventilator shall be balanced so that the value of the lesser flow shall be at least 90% of the value of the greater flow, unless otherwise recommended by the manufacturer.

9.32.3.12.  Outdoor Intake and Exhaust Openings

(1)  Separate air intake and exhaust outlet openings, when located on the same wall or roof, shall be installed so as to avoid contamination of the ventilation air by the exhaust air.

(2)  Intake openings shall be located so as to avoid contamination of the ventilation air from other local sources such as automobile exhausts and exhaust from adjacent buildings.

(3)  The distance from the bottom of an air intake opening to finished ground level or to any nearer and lower permanent horizontal surface shall be not less than 450 mm or the depth of expected snow accumulation, whichever is greater.

(4)  The distance separating air intakes from building envelope penetrations that are potential sources of contaminants, such as gas vents or oil fill pipes, shall be not less than 900 mm.

(5)  Air intakes shall be clearly labelled as such for identification from locations outside the dwelling unit.

(6)  The distance from the bottom of an exhaust outlet to finished ground level or to any nearer and lower permanent horizontal surface shall be not less than 100 mm.

(7)  Where air intake and exhaust openings are in exposed locations, provision shall be made to protect them from the entry of precipitation by the use of louvres, weather cowls or other suitable protection.

(8)  Air intake openings shall incorporate screens or grilles to protect against the entry of animals and insects.

(9)  Except for exhaust outlets serving heat recovery ventilators, exhaust outlets shall incorporate backdraft dampers.

(10)  Where a backdraft damper required by Sentence (9) is not located at the building envelope, the exhaust outlet shall incorporate a screen, located at the building envelope, to protect against the entry of animals.

(11)  Where a screen or grille required by Sentences (8) and (10) has a mesh size of less than 6 mm, the screen or grille shall be removable for cleaning.

(12)  The gross area of the screens or grilles installed in intake and exhaust openings shall be three times that of the duct served.

(13)  Screens and grilles shall be of corrosion-resistant material.

(14)  The net free area of an air intake or exhaust outlet shall be equal to or greater than the cross-sectional area of the duct served.

9.32.3.13.  Installation

(1)  Installation of fans and heat recovery ventilators shall be in accordance with manufacturer’s instructions for minimizing noise and vibration transmission and achieving the required sound rating.

(2)  Where flow-regulating dampers are required, they shall be adjustable and accessible without requiring the removal of fans, motors, or insulating materials and without the need for specialized tools.

(3)  Ventilation equipment shall be accessible for inspection, maintenance, repair and cleaning.

(4)  Ventilation equipment installed in unheated spaces shall be installed so as to avoid condensation of moisture on fans and motors in accordance with the manufacturer’s instructions.

Section 9.33. Heating and Air-Conditioning

9.33.1. General

9.33.1.1.  Design and Installation Requirements

(1)  The design and installation of central heating systems including requirements for combustion air, shall conform to the requirements in Part 6 and to this Section.

(2)  The design and installation of air-conditioning systems shall conform to Part 6.

(3)  Repairs, adjustments or component replacements that change the capacity or extent of safety of an existing heating, ventilating or air-conditioning system and that alter the method of operation shall conform to this Code.

9.33.1.2.  Solid Fuel-Burning Appliances

(1)  The design and installation of solid-fuel burning stoves, ranges and space heaters, including the requirements for combustion air, shall conform to CAN/CSA-B365-M, “Installation Code for Solid-Fuel Burning Appliances and Equipment”.

9.33.2. Required Heating Systems

9.33.2.1.  Residential Heating Systems

(1)  Residential buildings intended for use in the winter months on a continuing basis shall be equipped with heating facilities conforming to this Section.

9.33.3. Design Temperatures

9.33.3.1.  Indoor Design Temperatures

(1)  At the outside design temperature, required heating facilities shall be capable of maintaining an indoor air temperature of not less than

(a)	22°C in all living spaces,

(b)	22°C in unfinished basements, and

(c)	15°C in heated crawl spaces.

9.33.3.2.  Outdoor Design temperatures

(1)  The outdoor conditions to be used in designing heating, ventilating and air-conditioning systems shall be the appropriate values for the Municipality as set out in Section 2.5 Climatic Data, using 2.5 per cent design temperature criteria.

9.33.4.  Carbon Monoxide Detectors

9.33.4.1.  Application

(1)  This subsection applies to every building that

(a)	contains a residential occupancy, and

(b)	contains a fuel-burning appliance or a storage garage.

9.33.4.2.  Location of Carbon Monoxide Detectors

(1)  Where a fuel-burning appliance is installed in a suite of residential occupancy, a carbon monoxide detector shall be installed adjacent to each sleeping area in the suite.

(2)  Where a fuel-burning appliance is installed in a service room that is not in a suite of residential occupancy, a carbon monoxide detector shall be installed

(a)	adjacent to each sleeping area in every suite of residential occupancy that is adjacent to the service room, and

(b)	in the service room.

(3)  Where a storage garage is located in a building containing a residential occupancy, a carbon monoxide detector shall be installed adjacent to each sleeping area in every suite of residential occupancy that is adjacent to the storage garage.

(4)  Where a storage garage serves only the dwelling unit to which it is attached or built in, a carbon monoxide detector shall be installed adjacent to each sleeping area in the dwelling unit.

9.33.4.3.  Installation and Conformance to Standards

(1)  The carbon monoxide detector required by Article 9.33.4.2. shall

(a)	be permanently connected to an electrical circuit and shall have no disconnect switch between the overcurrent device and the carbon monoxide detector,

(b)	be wired so that its activation will activate all carbon monoxide detectors within the suite, where located within a suite of residential occupancy,

(c)	be equipped with an alarm that is audible within bedrooms when the intervening doors are closed, where located adjacent to a sleeping area, and

(d)	conform to

(i)	CAN/CGA-6.19, “Residential Carbon Monoxide Detectors”,

(ii)	CSA 6.19, “Residential Carbon Monoxide Alarming Devices”, or

(iii)	UL 2034, “Single and Multiple Station Carbon Monoxide Detectors”.

Section 9.34. Electrical Facilities

9.34.1. General

9.34.1.1.  Reserved

9.34.1.2.  Required Facilities

(1)  Where electrical services are available, electrical facilities shall be provided for every building in conformance with this Section.

9.34.1.3.  Location of Equipment in Public Areas

(1)  Entrance switches, meters, panel boxes, splitter boxes, time clocks and other similar equipment shall not be located in any public area unless adequate precautions are taken to prevent interference with the equipment.

9.34.1.4.  Recessed Lighting Fixtures

(1)  Recessed lighting fixtures shall not be located in insulated ceilings unless the fixtures are designed for such installations.

9.34.1.5.  Wiring and Cables

(1)  Except for dwelling units and except as required in Sentence (2), electrical wiring and cables installed in buildings permitted to be of combustible construction shall conform to Sentence 3.1.4.3.(1).

(2)  Where a concealed space in a floor or ceiling assembly is used as a plenum, electrical wiring and cables within the plenum shall conform to Sentence 3.6.4.3.(1).

9.34.2. Lighting Outlets

9.34.2.1.  Lighting of Entrances

(1)  An exterior lighting outlet with fixture controlled by a wall switch located within the building shall be provided at every entrance to buildings of residential occupancy.

9.34.2.2.  Outlets in Dwelling Units

(1)  Except as provided in Sentence (2), a lighting outlet with fixture controlled by a wall switch shall be provided in kitchens, bedrooms, living rooms, utility rooms, laundry rooms, dining rooms, bathrooms, water-closet rooms, vestibules and hallways in dwelling units.

(2)  Where a receptacle controlled by a wall switch is provided in bedrooms or living rooms, such rooms need not conform to the requirements of Sentence (1).

9.34.2.3.  Stairways

(1)  Every stairway shall be lighted.

(2)  Except as provided in Sentence (3), 3-way wall switches located at the head and foot of every stairway shall be provided to control not less than one lighting outlet with fixture for stairways with 4 or more risers in dwelling units.

(3)  The stairway lighting for basements that do not contain finished space or lead to an outside entrance or built-in garage and which serve not more than one dwelling unit is permitted to be controlled by a single switch located at the head of the stairs.

9.34.2.4.  Basements

(1)  A lighting outlet with fixture shall be provided for each 30 m2 or fraction thereof of floor area in unfinished basements.

(2)  The outlet required in Sentence (1) nearest the stairs shall be controlled by a wall switch located at the head of the stairs.

9.34.2.5.  Storage Rooms

(1)  A lighting outlet with fixture shall be provided in storage rooms.

9.34.2.6.  Garages and Carports

(1)  A lighting outlet with fixture shall be provided for an attached, built-in or detached garage or carport.

(2)  Except as provided in Sentence (3), lighting outlets required in Sentence (1) shall be controlled by a wall switch near the doorway.

(3)  Where the lighting outlet and fixture required in Sentence (1) are ceiling mounted above an area not normally occupied by a parked car; or are wall mounted, a fixture with a built-in switch is permitted to be used.

(4)  Where a carport is lighted by a light at the entrance to a dwelling unit, additional carport lighting is not required.

9.34.2.7.  Public and Service Areas

(1)  Every public or service area in buildings, including a recreational camp and a camp for housing of workers, shall have lighting outlets with fixtures controlled by a wall switch or panel.

(2)  When provided by incandescent lighting, illumination required in Sentence (1) shall conform to Table 9.34.2.7.

(3)  When other types of lighting are used, illumination equivalent to that shown in Table 9.34.2.7. shall be provided.

Table 9.34.2.7.

Lighting for Public Areas

Forming Part of Sentences 9.34.2.7.(2) and (3)

| Room or Space | Minimum Illumination, 1 x | Minimum Lighting Power Density, W/M2 of floor area (incandescent lighting) |
| --- | --- | --- |
| Storage rooms | 50 | 5 |
| Service rooms and laundry areas | 200 | 20 |
| Garages | 50 | 5 |
| Public water-closet rooms | 100 | 10 |
| Service hallways and stairways | 50 | 5 |
| Recreation rooms | 100 | 10 |
| Recreational camps and camps for housing of workers hallways, corridors, stairways and sleeping areas | 100 | 10 |
| Kitchen | 500 | 50 |
| All other rooms | 250 | 25 |
| Column 1 | 2 | 3 |

9.34.2.8.  Motion Sensors

(1)  Lighting installed to provide the minimum illumination levels required by this Part may be controlled by motion sensors except where the lighting is installed in an exit.

(2)  Where motion sensors are used to control minimum lighting in a public corridor or corridor providing access to exit for the public, the motion sensors shall be installed with switch controllers equipped for fail-safe operation and illumination timers set for a minimum 15-minute duration.

(3)  A motion sensor shall not be used to control emergency lighting.

9.34.3. Emergency Lighting

9.34.3.1.  Emergency Lighting

(1)  Emergency lighting shall conform to Subsection 9.9.11.

9.34.4. Service Entrance Requirements

9.34.4.1.  Meter Mounting Device

(1)  Except in the case of externally mounted read-outs, each new residential consumer service of 200 amperes or less shall have a meter mounting device located outdoors in an accessible location.

(2)  For the purposes of this Subsection, the front of the building is the side nearest the utility distribution line.

9.34.4.2.  Location of Meter Mounting Device

(1)  Meter mounting devices shall be installed on the wall of the building or where that is not possible, on a separate support, so that the midpoint of the meter after installation will be 1 750 mm ± 100 mm from finished grade.

(2)  Meter mounting devices shall be located not more than 3 m back from the front of the single family and semi-detached homes.

9.34.4.3.  Location of Consumer Service Standpipe

(1)  For an underground supply, the bottom of the consumer service standpipe shall be located not more than 3 m from the corner of the building.

(2)  For an overhead supply, the top of the consumer service standpipe shall be located not more than 3 m from the corner of the building except that where this location does not permit a 4.5 m clearance at the point of attachment of the service conductors to the building, the top of the standpipe may be extended to a point not more than half way along the building.

9.34.4.4.  Meter Mounting Device

(1)  The meter mounting device shall be

(a)	one hundred ampere capacity except when the service equipment is to be greater,

(b)	standardized for each service size, and

(c)	capable of accepting 2 in. IPS conduit of steel, aluminum, copper or PVC if intended for underground service entrance.

9.34.4.5.  Underground Service

(1)  For consumer services supplied underground

(a)	a 2 in. IPS steel, aluminum, copper or PVC conduit shall be attached to the bottom of the meter-mounting device and shall terminate in the earth at a point at least 900 mm below grade and a conduit bushing shall be attached to the conduit in the earth, and

(b)	the conductors on the line side of the meter and those on the load side of the meter shall not be installed in the same conduit.

Section 9.35. Garages and Carports

9.35.1. Scope

9.35.1.1.  Application

(1)  This Section applies to garages and carports serving not more than 1 dwelling unit.

9.35.1.2.  Construction Requirements

(1)  The construction of a garage or carport shall conform to the requirements for other buildings in this Part except as provided in this Section.

9.35.2. General

9.35.2.1.  Carport Considered to be Garage

(1)  Where a roofed enclosure used for the storage or parking of motor vehicles has more than 60 per cent of the total perimeter enclosed by walls, doors or windows, the enclosure shall be considered a garage.

9.35.2.2.  Garage Floor

(1)  Where an attached or built-in garage is provided, the garage floor shall be sloped to drain liquids to the outdoors.

9.35.3. Foundations

9.35.3.1.  Foundation Required

(1)  Except as permitted in this Subsection, foundations conforming to Sections 9.12. and 9.15. shall be provided for the support of carport and garage super-structures, including that portion beneath garage doors.

9.35.3.2.  Protection from Damage due to Soil Movement

(1)  In clay-type soils subject to significant movement with a change in soil moisture content, the foundation depth of carports or garages connected to a dwelling unit directly or by a breezeway shall be approximately the same depth as the main building foundation.

(2)  Where slab-on-ground construction is used, a construction joint shall be provided between the main building slab and the garage or breezeway or carport slab.

(3)  Except as provided in Section 9.12., foundations for attached unheated garages or carports shall be below frost level.

9.35.3.3.  Small Garages

(1)  Detached garages of less than 50 m2 floor area and not more than 1 storey in height may be supported on wood mud sills provided the garage is not of masonry or masonry veneer construction.

9.35.3.4.  Column Piers

(1)  Piers for the support of carport columns shall extend not less than 150 mm above ground level.

(2)  Piers referred to in Sentence (1) shall project not less than 25 mm beyond the base of the column but in no case be less than 190 mm by 190 mm in size.

9.35.4. Walls and Columns

9.35.4.1.  Interior Finish

(1)  Interior finish need not be applied to garage and carport walls.

9.35.4.2.  Columns

(1)  Columns for garages and carports shall conform to Section 9.17, except that 89 mm by 89 mm wood columns may be used.

9.35.4.3.  Anchorage

(1)  Garage or carport walls and columns shall be anchored to the foundation to resist wind uplift in conformance with Subsection 9.23.6., except that where a garage is supported on the surface of the ground, ground anchors shall be provided to resist wind uplift.

Section 9.36. Cottages

9.36.1. Scope

9.36.1.1.  Application

(1)  This Section applies to buildings of residential occupancy used or intended to be used as seasonal recreational buildings.

(2)  The buildings described in Sentence (1) shall comply with all the requirements of this Part, except where they are specifically exempted in this Section.

9.36.2. General

9.36.2.1.  Exclusions

(1)  Except as provided in Articles 9.36.3.1. and 9.36.2.4. and Subsection 9.10.15., buildings used or intended to be used as seasonal recreational buildings need not comply with Sections 9.5. to 9.7. and 9.9. to 9.11.

(2)  Flooring need not comply with Section 9.30., but tight-fitting floors shall be provided to support the live and dead loads.

(3)  Except as provided in Sentences (4) and (5), thermal insulation, vapour barrier, air-barrier construction, interior finishes, plumbing, heating, mechanical ventilation, air-conditioning and electrical facilities, need not be provided, but where any of these are provided, they shall comply with the requirements of this Part.

(4)  Where heating and air-conditioning are provided, Article 9.33.3.1. need not be complied with.

(5)  Where thermal insulation is provided, the minimum thermal resistance of insulation in Table 9.25.2.1. need not be provided.

9.36.2.2.  Foundations

(1)  Continuous perimeter foundation walls are not required, but when they are provided, they shall comply with the requirements of this Part.

(2)  Where unit masonry columns are used, the height of such columns shall not exceed

(a)	in the case of hollow masonry units, 4 times the least dimension of the units,

(b)	in the case of solid masonry units or hollow units with voids filled with concrete, 10 times the least dimension of the column, or

(c)	where the column is reinforced with at least four 13 mm diameter bars and filled with concrete, 18 times the least dimension of the column.

(3)  Columns in excess of the height limitations of Clause (2)(a), (2)(b), or (2)(c) shall be designed in accordance with Part 4.

9.36.2.3.  Waterproofing and Dampproofing

(1)  Where foundations below ground level and concrete floors on grade are used, they shall comply with Section 9.13., “Waterproofing and Dampproofing”.

9.36.2.4.  Smoke Alarms

(1)  Every dwelling unit within the scope of this Section shall be provided with a smoke alarm in accordance with Subsection 9.10.18.

9.36.3. Tourist Accommodation

9.36.3.1.  Buildings for Seasonal Tourist Accommodation or for Rent

(1)  Where buildings are used or intended to be used for seasonal tourist accommodation or for rent, they shall comply with Sections 9.5. to 9.8. in addition to the requirements of this Section.

Section 9.37. Log Construction

9.37.1. General

9.37.1.1.  Material Requirements

(1)  Logs which are sound and free of fractures may be used for foundations, beams, posts and similar members providing it can be shown by a structural analysis or tests or previous experience that the strength of the member is adequate for its intended purposes.

9.37.1.2.  Requirement for Wood Preservative

(1)  The portion of any log coming in contact with masonry or concrete at or below grade shall be treated with a wood preservative to prevent decay.

9.37.1.3.  Exterior Joints

(1)  All exterior joints between logs shall be rendered water-tight by methods such as machined joints, oakum packing, cement parging, chinking, caulking or a combination of these.

9.37.2. Walls

9.37.2.1.  Logs

(1)  Walls may be built of natural or manufactured logs.

9.37.2.2.  Attachment of Logs

(1)  Walls made of logs in a horizontal position shall have interlocking intersections which will prevent the collection of water in the joints, or the horizontal logs shall butt to a vertical corner post to which the horizontal logs shall be firmly attached.

9.37.2.3.  Joining Logs

(1)  Each log in a horizontal position shall be scribed as close as possible to its bearer and fastened to the bearer in at least three places throughout its length, by dowels, continuous machined joints, vertical framing members or interlocking intersections or any combination of these, but in no case shall the distance between fastenings exceed 1 800 mm.

9.37.2.4.  Vertical Logs

(1)  Each log in a wall built of vertical logs shall be scribed to fit as closely as possible to the adjacent logs.

9.37.2.5.  Plates

(1)  Logs used in a vertical position shall have a plate at the top and a plate at the bottom, which are at least as wide as the largest end diameter of any of the logs.

9.37.3. Lintels

9.37.3.1.  Support Over Openings

(1)  Logs placed in vertical position shall be supported over window and door openings by lintels meeting the requirements of Tables A13 to A20.

9.37.3.2.  Clearance

(1)  At every opening in a wall made of logs in a horizontal position where shrinkage can occur there shall be a clearance between the rough buck header and the lintel log of not less than 13 mm in width for each 300 mm of height to allow for settlement.

Section 9.38. Thermal Design

9.38.1. Scope

9.38.1.1.  Application

(1)  This Section applies to the thermal design of a building of residential occupancy where such design is an alternative to the thermal insulation requirements of Section 9.25.

9.38.2. General

9.38.2.1.  Materials and Installation

(1)  The materials for, and the installation of, thermal insulation and vapour barrier protection shall conform to Section 9.25.

9.38.2.2.  Protection of Foamed Plastic

(1)  Foamed plastic thermal insulation shall be protected as described in Article 9.10.16.10.

9.38.2.3.  Crawl Spaces

(1)  Crawl spaces shall comply to Section 9.18.

9.38.2.4.  Roof Spaces

(1)  Roof spaces shall comply to Section 9.19.

9.38.2.5.  Ventilation

(1)  Ventilation requirements shall comply to Section 9.32 except as provided in Subsection 9.38.7.

9.38.2.6.  Heating and Air-Conditioning

(1)  Heating and air-conditioning requirements shall comply to Section 9.33.

9.38.3. Thermal Resistance of Assemblies

9.38.3.1.  Thermal Resistance

(1)  Except as provided in Articles 9.38.3.2. to 9.38.3.6., and except for doors, windows, skylights and other closures, the thermal resistance of each building assembly through any portion that does not include framing or furring shall conform to Table 9.38.3.1.

Table 9.38.3.1.

Minimum Thermal Resistance, RSI Value

Forming Part of Sentence 9.38.3.1.(1)

| Building Assembly | Maximum Number of Celsius Degree Days |  | Electric Space Heating |
| --- | --- | --- | --- |
|  | Up to 5000 | Above 5000 |  |
| Ceiling below attic or roof space | 5.6 | 6.9 | 7.20 |
| Roof assembly without attic or roof space | 3.8 | 3.8 | 4.15 |
| Wall other than foundation wall | 3.45 | 4.3 | 5.15 |
| Foundation walls enclosing heated space | 1.7 | 2.4 | 3.54 |
| Floor, other than slab-on-ground | 4.7 | 4.7 | 4.7 |
| Slab-on-ground(1) |  |  |  |
| - containing pipes or heating ducts | 2.11 | 2.11 | 2.11 |
| - not containing pipes or heating ducts | 1.76 | 1.76 | 1.76 |
| Column 1 | 2 | 3 | 4 |

Note to Table 9.38.3.1.:

(1) “RSI value” shown for slab-on-ground is for rigid insulation.

9.38.3.2.  Metal Framing Elements Acting as Thermal Bridge

(1)  Except as provided in Article 9.38.3.3., the thermal resistance of the insulated portion of a building assembly in Sentence 9.38.1.1.(1) that incorporates metal framing elements, such as steel studs and steel joists, that act as thermal bridges to facilitate heat flow through the assembly, shall be 20 per cent greater than the values shown in Table 9.38.3.1., unless it can be shown that the heat flow is not greater than the heat flow through a wood frame assembly of the same thickness.

9.38.3.3.  Insulated Thermal Bridges

(1)  Article 9.38.3.2. does not apply for building assemblies incorporating thermal bridges where the thermal bridges are insulated to restrict heat flow through the thermal bridges by a material providing a thermal resistance at least equal to 25 per cent of the thermal resistance required for the insulated portion of the assembly in Article 9.38.3.1.

9.38.3.4.  Reduction of Thermal Resistance

(1)  The thermal resistance of a building assembly may be reduced by not more than 20 per cent from that required in Articles 9.38.3.1. and 9.38.3.2., and the amount of glazing may be increased to more than permitted in Article 9.38.4.3., where it can be shown that the total calculated heat loss from the building enclosure does not exceed the heat loss that would result if the enclosure were constructed in conformance with the minimum thermal resistance requirements in Articles 9.38.3.1. and 9.38.3.2. and with the maximum amount of glazing permitted in Article 9.38.4.3., provided no allowance is made for solar heat gains or for the orientation of the glazing as described in Article 9.38.4.5.

9.38.3.5.  Thermal Resistance Values for Roof and Ceiling Assemblies

(1)  The thermal resistance values in Article 9.38.3.1. and 9.38.3.2. for roof or ceiling assemblies separating heated space from unheated space or the exterior may be reduced near the eaves to the extent made necessary by the roof slope and required ventilation clearances, except that the thermal resistance at the location directly above the inner surface of the exterior wall shall be at least 2.1 m2°C/W.

9.38.3.6.  Reduction in Thermal Resistance Values due to Thermal Inertia

(1)  The thermal resistance values required in Article 9.38.3.1. may be reduced to take into account the effect of thermal inertia resulting from the mass of the building in conformance with Building Research Note No. 126, published by the Division of Building Research, National Research Council of Canada, January 1978.

9.38.3.7.  Insulation on Exterior of Foundation Wall

(1)  Insulation applied to the exterior of a foundation wall or slab-on-ground floor shall extend down at least 600 mm below the adjacent exterior ground level or shall extend down and outward from the floor or wall for a total distance of at least 600 mm measured from the adjacent finished ground level.

9.38.3.8.  Insulation on Interior of Foundation Wall

(1)  Insulation applied to the interior of a foundation walls enclosing heated space shall extend from the underside of the subfloor to not less than 600 mm below the adjacent exterior ground level.

9.38.4. Glazing

9.38.4.1.  Thermal Resistance of Glazing

(1)  Except as provided in Articles 9.38.4.2. and 9.38.4.4., all glazing that separates heated space from unheated space or the exterior shall have a thermal resistance of at least 0.30 m2°C/W.

9.38.4.2.  Enclosed Unheated Space

(1)  Where an enclosed unheated space, such as a sun porch, enclosed veranda or vestibule, is separated from a heated space by glazing, the unheated enclosure may be considered to provide thermal resistance of 0.16 m2°C/W, or the equivalent of one layer of glazing.

9.38.4.3.  Maximum Area of Glazing

(1)  Except as provided in Articles 9.38.4.4. and 9.38.4.5., the total area of glazing, including glazing for doors and skylights, that separates heated space from unheated space or the exterior shall not exceed 20 per cent of the floor area of the storey served by the glazed areas and shall not exceed 40 per cent of the total area of the walls of that storey separating heated space from unheated space or the exterior.  (In the case of a sloping wall, the area of the opaque portion of the wall is calculated as its projected area on a vertical plane.)

9.38.4.4.  Different Thermal Resistance of Glazing

(1)  Where the thermal resistance of glazing is different from that required in Articles 9.38.4.1. and 9.38.4.2., the area of such glazing for the purpose of applying Article 9.38.4.3. may be assumed as being equal to the actual area multiplied by the ratio of the required thermal resistance divided by the actual thermal resistance of the glazing.

9.38.4.5.  Clear Glass or Shading Coefficient

(1)  Except as provided in Article 9.38.4.6., the area of glazing that contains clear glass or that has a shading coefficient of more than 0.70 that is unshaded in the winter and faces a direction within 45° of due South may be assumed to be 50 per cent of its unshaded area in calculating the maximum area of glazing in Articles 9.38.4.3. and 9.38.4.4. provided the building is designed with a system that is capable of distributing the solar heat gain from such glazed areas throughout the building.  For the purpose of determining whether or not the glazing is shaded in the winter, the shading shall be calculated using the noon sun angles of December 21.

9.38.4.6.  Building Designed to be Cooled

(1)  Article 9.38.4.5. shall not apply where the building is designed to be cooled unless the glazing described in 9.38.4.5. is shaded in the summer with exterior devices.  For the purpose of determining whether or not the glazing is shaded in the summer, the shading shall be calculated using the noon sun angles of June 21.

9.38.5. Doors and Windows

9.38.5.1.  Air Curtains

(1)  Air curtains shall not be used in place of exterior doors.

9.38.5.2.  Infiltration around Doors

(1)  Except for doors used primarily to facilitate the movement of vehicles or handling of material, infiltration around doors shall conform to the appropriate requirements in Subsection 9.38.6.

9.38.5.3.  Minimum Thermal Resistance of Doors

(1)  Except for doors on enclosed unheated vestibules, all doors separating heated space from the outside shall conform to the appropriate requirements of Article 9.25.2.1.

9.38.5.4.  Minimum Thermal Resistance of Windows

(1)  Windows shall conform to the appropriate requirements of Article 9.25.2.1.

(2)  When electric space heating is used, all sliding glass doors separating heated space from unheated space or the outdoors shall have an energy rating of not less than -13 ER.

(3)  When electric space heating is used, all glazing that separates heated space from unheated space or the outdoors shall have an energy rating of not less than -13 ER for openable windows and 0 ER for fixed glazing.

(4)  The energy rating required in Sentences (2) and (3) shall be determined in conformance with CAN/CSA-A440.2-M, “Energy Performance Evaluation of Windows and Sliding Glass Doors”.

9.38.6. Infiltration

9.38.6.1.  Air Infiltration of Exterior Windows

(1)  Windows separating heated space from unheated space or the exterior shall be designed to limit the rate of air infiltration to not more than 0.775 dm3/s for each metre of sash crack when tested at pressure differential of 75 Pa in conformance with ASTM E283, “Standard Method of Test for Rate of Air Leakage through Exterior Windows, Curtain Walls and Doors”.

9.38.6.2.  Air Infiltration of Exterior Sliding Glass Doors

(1)  Manually operated exterior sliding glass door assemblies that separate heated space from unheated space or the exterior shall be designed to limit air infiltration to not more than 2.5 dm3/s for each square metre of door area when tested in conformance with Article 9.38.6.1.

9.38.6.3.  Air Infiltration of Exterior Swing Type Doors

(1)  Except where the door is weather-stripped on all edges and protected with a storm door or by an enclosed unheated space, exterior swing type door assemblies for dwelling units, individually rented hotel and motel rooms and suites shall be designed to limit the rate of air infiltration to not more than 6.35 dm3/s for each square metre of door area when tested in conformance with Article 9.38.6.1.

9.38.6.4.  Air Infiltration of Other Doors

(1)  Door assemblies other than those described in Articles 9.38.6.2. and 9.38.6.3. that separate heated space from unheated space or the exterior shall be designed to limit the rate of air infiltration to not more than 17.0 dm3/s for each metre of door crack when tested in conformance with Article 9.38.6.1.

9.38.6.5.  Caulking Materials

(1)  Caulking material to reduce air infiltration shall conform to the requirements in Subsection 9.27.4.

9.38.6.6.  Sealing of Joints to Prevent Air Leakage

(1)  The junction between the sill plate and the foundation, joints between exterior wall panels and any other location where there is a possibility of air leakage into heated spaces in a building through the exterior walls, such as at utility service entrances, shall be caulked, gasketed or sealed to restrict such air leakage.

9.38.6.7.  Air Leakage

(1)  Air leakage between heated space and adjacent roof or attic space caused by the penetration of services shall be restricted in conformance with the requirements of Subsection 9.25.3.

9.38.7. Ventilation

9.38.7.1.  Minimum Ventilation Rate

(1)  Fresh air for the ventilation of rooms and spaces in buildings of residential occupancy shall be provided at a rate of at least 0.3 air change per hour by a combination of natural and mechanical ventilation.

Section 9.39. Park Model Trailers

9.39.1. Scope

9.39.1.1.  Application

(1)  This Section applies to manufactured buildings designed and constructed in conformance with CAN/CSA-Z241 Series-M, “Park Model Trailers” and used or intended to be used as a seasonal recreational building of residential occupancy.

9.39.2.  General

9.39.2.1.  General

(1)  Except as provided in Subsection 9.39.3., a manufactured building used or intended to be used as a seasonal recreational building of residential occupancy is deemed to comply with this Code if it is designed and constructed in conformance with CAN/CSA-Z241 Series-M, “Park Model Trailers”.

9.39.3.  Requirements

9.39.3.1.  Other Building Components

(1)  The requirements of this Code shall apply to building components designed and constructed outside the place of manufacture of a building described in Article 9.39.1.1.

9.39.3.2.  Spatial Separation

(1)  Buildings described in Article 9.39.1.1. shall comply with Section 9.10 where the building is

(a)	used or intended to be used for seasonal tourist accommodation, or

(b)	leased or intended to be leased.

9.39.3.3.  Foundations and Anchorage

(1)  Buildings described in Article 9.39.1.1. shall be supported and anchored in conformance with the manufacturer’s installation instructions.

9.39.3.4.  Proximity to Above Ground Electrical Conductors

(1)  Buildings described in Article 9.39.1.1. shall comply with Article 9.1.1.5.

Section 9.40.  Construction of Farm Buildings

9.40.1.  Scope

9.40.1.1.  Application

(1)  This Section applies to farm buildings of low human occupancy.

9.40.1.2.  Construction Requirements

(1)  The construction of farm buildings of low human occupancy shall, subject to Article 2.1.1.5., conform to the requirements of this Part except as provided in this Section.

9.40.2. Lumber

9.40.2.1.  Lumber Requirements

(1)  Except as permitted by Article 9.40.2.2., lumber shall conform to appropriate requirements in Subsection 9.3.2.

9.40.2.2.  Ungraded Lumber

(1)  Ungraded lumber may be used for wood posts, joists, rafters, lintels, beams and wall studs in a farm building of low human occupancy of not more than one storey in building height.

9.40.3. Structural Requirements

9.40.3.1.  Structural Design

(1)  Except as provided in Articles 9.40.3.2. to 9.40.3.4., wood posts, joists, rafters, lintels, beams and wall studs shall be designed in conformance with Section 9.4.

9.40.3.2.  Posts

(1)  In a farm building of low human occupancy, the size of wood posts shall conform to Tables 9.40.3.2.A. to 9.40.3.2.J. for the loads shown in the Tables.

9.40.3.3.  Spans

(1)  In a farm building of low human occupancy, the spans of wood joists, rafters, lintels and beams shall conform to the spans shown in Tables 9.40.3.3.K. to 9.40.3.3.T. for the loads shown in the Tables.

9.40.3.4.  Stud Size and Spacing

(1)  In a farm building of low human occupancy, the size and spacing of wood studs shall conform to Tables 9.40.3.4.U. to 9.40.3.4.W. for the loads shown in the Tables.

Table 9.40.3.2.A.

Post Sizes for Diaphragm-Braced Farm Buildings of Low Human Occupancy

Forming Part of Article 9.40.3.2.

| Building Width, m | Wall Height, m | Spruce – Pine – Fir, No. 1, Dressed (Post and Timber Grades) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | For Wind Loading q10  0.30 kPa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Post Spacing, 2.4 m |  |  |  |  | Post Spacing, 3.6 m |  |  |  |  | Post Spacing, 4.8 m |  |  |  |  |
|  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  |
|  |  | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 |
| 9.14 |  3.0 | A | A | A | A | A | A | A | A | A | A | A | A | B | B | B |
|  | 3.6 | A | A | A | A | A | A | A | B | B | B | B | B | B | C | C |
|  | 4.2 | B | B | B | B | B | B | B | B | C | C | B | C | C | C | C |
|  | 4.8 | B | B | B | B | B | B | C | C | C | C | C | C | C | C | C |
|  | 6.0 | C | C | C | C | C | C | C | C | D | D | C | D | D | — | — |
| 12.1 |  3.0 | A | A | A | A | A | A | A | A | B | B | A | B | B | B | C |
|  | 3.6 | A | A | A | A | B | A | B | B | B | C | B | B | C | C | C |
|  | 4.2 | B | B | B | B | B | B | B | C | C | C | C | C | C | C | C |
|  | 4.8 | B | B | B | C | C | C | C | C | C | C | C | C | D | D | D |
|  | 6.0 | C | C | C | C | C | C | C | D | D | — | D | D | — | — | — |
| 15.2 |  3.0 | A | A | A | A | A | A | A | B | B | B | B | B | B | C | C |
|  | 3.6 | A | A | A | B | B | B | B | B | C | C | B | C | C | C | C |
|  | 4.2 | B | B | B | B | C | B | C | C | C | C | C | C | C | D | D |
|  | 4.8 | B | B | C | C | C | C | C | C | C | D | C | C | D | D | — |
|  | 6.0 | C | C | C | C | D | C | D | D | — | — | D | — | — | — | — |
| 18.2 |  3.0 | A | A | A | B | B | A | B | B | B | C | B | B | C | C | C |
|  | 3.6 | A | A | B | B | B | B | B | C | C | C | C | C | C | C | D |
|  | 4.2 | B | B | B | C | C | C | C | C | C | C | C | C | D | D | D |
|  | 4.8 | B | C | C | C | C | C | C | C | D | D | C | D | D | — | — |
|  | 6.0 | C | C | C | D | D | D | D | — | — | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |

Legend — Post Sizes

A = 89 mm x 140 mm

B = 140 mm x 140 mm

C = 140 mm x 184 mm

D = 184 mm x 184 mm

Notes to Table 9.40.3.2.A.:

(1)	 Designs are based on load combinations of total roof load and wind load acting at the same time on a closed building.

(2)	 Posts shall be oriented with the long dimension parallel to the building width.

(3)	 Bracing systems shall be specified by a competent designer.

(4)	 Posts shall be situated on footings and shall be anchored to prevent wind uplift.

(5)	 Posts shall be constrained against lateral movement at ground level and at the footing.  Concrete floor, splash-rail and uplift anchor help to meet this condition.

(6)	 Post designs are based on partial fixity condition due to embedment in soil.

(7)	 Footing excavations should be backfilled with parent material unless otherwise specified by a competent designer.

Table 9.40.3.2.B.

Post Sizes for Diaphragm-Braced Farm Buildings of Low Human Occupancy

Forming Part of Article 9.40.3.2.

| Building Width, m | Wall Height, m | Spruce – Pine – Fir, No. 1, Dressed (Post and Timber Grades) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | For Wind Loading q10  0.45 kPa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Post Spacing, 2.4 m |  |  |  |  | Post Spacing, 3.6 m |  |  |  |  | Post Spacing, 4.8 m |  |  |  |  |
|  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  |
|  |  | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 |
| 9.14 |  3.0 | A | A | A | A | A | A | A | A | A | B | A | B | B | B | B |
|  | 3.6 | A | A | A | A | A | A | B | B | B | B | B | B | C | C | C |
|  | 4.2 | B | B | B | B | B | B | B | C | C | C | C | C | C | C | C |
|  | 4.8 | B | B | B | C | C | C | C | C | C | C | C | C | C | D | D |
|  | 6.0 | C | C | C | C | C | C | D | D | D | D | D | — | — | — | — |
| 12.1 |  3.0 | A | A | A | A | A | A | A | B | B | B | B | B | B | C | C |
|  | 3.6 | A | A | A | B | B | B | B | B | C | C | C | C | C | C | C |
|  | 4.2 | B | B | B | B | C | C | C | C | C | C | C | C | C | C | D |
|  | 4.8 | B | C | C | C | C | C | C | C | C | C | C | D | D | D | — |
|  | 6.0 | C | C | C | C | D | D | D | D | — | — | — | — | — | — | — |
| 15.2 |  3.0 | A | A | A | A | B | A | B | B | B | C | B | B | C | C | C |
|  | 3.6 | A | A | B | B | B | B | B | C | C | C | C | C | C | C | D |
|  | 4.2 | B | B | B | C | C | C | C | C | C | C | C | C | D | D | D |
|  | 4.8 | B | C | C | C | C | C | C | C | D | D | C | D | D | — | — |
|  | 6.0 | C | C | C | D | D | D | D | — | — | — | — | — | — | — | — |
| 18.2 |  3.0 | A | A | A | B | B | B | B | B | C | C | B | C | C | C | C |
|  | 3.6 | A | B | B | B | C | B | C | C | C | C | C | C | C | D | D |
|  | 4.2 | B | B | C | C | C | C | C | C | C | D | C | D | D | D | — |
|  | 4.8 | C | C | C | C | C | C | C | D | D | — | D | D | — | — | — |
|  | 6.0 | C | C | D | D | — | D | — | — | — | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |

Legend — Post Sizes

A = 89 mm x 140 mm

B = 140 mm x 140 mm

C = 140 mm x 184 mm

D = 184 mm x 184 mm

Notes to Table 9.40.3.2.B.:

(1)	 Designs are based on load combinations of total roof load and wind load acting at the same time on a closed building.

(2)	 Posts shall be oriented with the long dimension parallel to the building width.

(3) Bracing systems shall be specified by a competent designer.

(4)	 Posts shall be situated on footings and shall be anchored to prevent wind uplift.

(5)	 Posts shall be constrained against lateral movement at ground level and at the footing.  Concrete floor, splash-rail and uplift anchor help to meet this condition.

(6)	 Post designs are based on partial fixity condition due to embedment in soil.

(7)	 Footing excavations should be backfilled with parent material unless otherwise specified by a competent designer.

Table 9.40.3.2.C.

Post Sizes for Knee-Braced Farm Buildings of Low Human Occupancy

Forming Part of Article 9.40.3.2.

| Building Width, m | Wall Height m | Spruce — Pine —Fir, No. 1, Dressed (Post and Timber Grades) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | For Wind Loading q10  0.30 kPa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Post Spacing, 2.4 m |  |  |  |  | Post Spacing, 3.6 m |  |  |  |  | Post Spacing, 4.8 m |  |  |  |  |
|  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  |
|  |  | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 |
| 9.14 |  3.0 | A | A | A | A | A | A | A | A | B | B | A | B | B | B | C |
|  | 3.6 | A | A | A | A | B | A | B | B | B | C | B | C | C | C | C |
|  | 4.2 | B | B | B | B | B | B | C | C | C | C | C | C | C | C | C |
|  | 4.8 | C | C | C | C | C | C | C | C | C | C | C | C | C | D | D |
|  | 6.0 | C | C | C | C | C | C | D | D | D | — | D | — | — | — | — |
| 12.1 |  3.0 | A | A | A | A | A | A | A | B | B | B | B | B | C | C | C |
|  | 3.6 | A | A | B | B | B | B | B | C | C | C | C | C | C | C | C |
|  | 4.2 | B | B | B | C | C | C | C | C | C | C | C | C | C | D | D |
|  | 4.8 | C | C | C | C | C | C | C | C | D | D | C | D | D | — | — |
|  | 6.0 | C | C | C | D | D | D | D | — | — | — | — | — | — | — | — |
| 15.2 |  3.0 | A | A | A | B | B | A | B | B | C | C | B | C | C | C | C |
|  | 3.6 | A | B | B | B | C | B | C | C | C | C | C | C | C | C | D |
|  | 4.2 | B | B | C | C | C | C | C | C | C | D | C | C | D | D | — |
|  | 4.8 | C | C | C | C | C | C | C | D | D | — | D | D | — | — | — |
|  | 6.0 | C | C | D | D | — | D | — | — | — | — | — | — | — | — | — |
| 18.2 |  3.0 | A | A | B | B | B | B | B | C | C | C | B | C | C | C | D |
|  | 3.6 | B | B | B | C | C | C | C | C | C | C | C | C | C | D | D |
|  | 4.2 | B | C | C | C | C | C | C | C | D | D | C | D | D | — | — |
|  | 4.8 | C | C | C | C | D | C | D | D | — | — | D | — | — | — | — |
|  | 6.0 | C | D | D | — | — | — | — | — | — | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |

Legend — Post Sizes

A = 89 mm x 140 mm

B = 140 mm x 140 mm

C = 140 mm x 184 mm

D = 184 mm x 184 mm

Notes to Table 9.40.3.2.C.:

(1)	 Designs are based on load combinations of total roof load and wind load acting at the same time on a closed building.

(2)	 Posts shall be oriented with the long dimension parallel to the building width.

(3)	 Bracing systems shall be specified by a competent designer.

(4)	 Posts shall be situated on footings and shall be anchored to prevent wind uplift.

(5)	 Posts shall be constrained against lateral movement at ground level and at the footing.  Concrete floor, splash-rail and uplift anchor help to meet this condition.

(6)	 Post designs are based on partial fixity condition due to embedment in soil.

(7)	 Footing excavations should be backfilled with parent material unless otherwise specified by a competent designer.

Table 9.40.3.2.D.

Post Sizes for Knee-Braced Farm Buildings of Low Human Occupancy

Forming Part of Article 9.40.3.2.

| Building Width, m | Wall Height, m | Spruce – Pine – Fir, No. 1, Dressed (Post and Timber Grades) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | For Wind Loading q10  0.45 kPa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Post Spacing, 2.4 m |  |  |  |  | Post Spacing, 3.6 m |  |  |  |  | Post Spacing, 4.8 m |  |  |  |  |
|  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  |
|  |  | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 |
| 9.14 |  3.0 | A | A | A | A | A | A | A | B | B | B | B | B | B | C | C |
|  | 3.6 | A | A | A | B | B | B | B | B | C | C | C | C | C | C | C |
|  | 4.2 | B | B | B | B | C | C | C | C | C | C | C | C | C | C | D |
|  | 4.8 | C | C | C | C | C | C | C | C | C | D | C | D | D | D | — |
|  | 6.0 | C | C | C | C | D | D | D | — | — | — | — | — | — | — | — |
| 12.1 |  3.0 | A | A | A | A | B | A | B | B | B | C | B | B | C | C | C |
|  | 3.6 | B | B | B | B | B | B | C | C | C | C | C | C | C | C | C |
|  | 4.2 | B | B | C | C | C | C | C | C | C | C | C | C | D | D | D |
|  | 4.8 | C | C | C | C | C | C | C | D | D | D | D | D | — | — | — |
|  | 6.0 | C | C | D | D | D | D | — | — | — | — | — | — | — | — | — |
| 15.2 |  3.0 | A | A | B | B | B | B | B | B | C | C | B | C | C | C | C |
|  | 3.6 | A | B | B | C | C | C | C | C | C | C | C | C | C | D | D |
|  | 4.2 | B | C | C | C | C | C | C | C | D | D | C | D | D | — | — |
|  | 4.8 | C | C | C | C | C | C | D | D | D | — | D | — | — | — | — |
|  | 6.0 | C | D | D | — | — | — | — | — | — | — | — | — | — | — | — |
| 18.2 |  3.0 | A | A | B | B | B | B | B | C | C | C | C | C | C | C | D |
|  | 3.6 | B | B | C | C | C | C | C | C | C | D | C | C | D | D | — |
|  | 4.2 | C | C | C | C | C | C | C | D | D | D | D | D | — | — | — |
|  | 4.8 | C | C | C | D | D | C | D | — | — | — | D | — | — | — | — |
|  | 6.0 | D | D | — | — | — | — | — | — | — | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |

Legend — Post Sizes

A = 89 mm x 140 mm

B = 140 mm x 140 mm

C = 140 mm x 184 mm

D = 184 mm x 184 mm

Notes to Table 9.40.3.2.D.:

(1) Designs are based on load combinations of total roof load and wind load acting at the same time on a closed building.

(2) Posts shall be oriented with the long dimension parallel to the building width.

(3) Bracing systems shall be specified by a competent designer.

(4) Posts shall be situated on footings and shall be anchored to prevent wind uplift.

(5) Posts shall be constrained against lateral movement at ground level and at the footing.  Concrete floor, splash-rail and uplift anchor help to meet this condition.

(6) Post designs are based on partial fixity condition due to embedment in soil.

(7) Footing excavations should be backfilled with parent material unless otherwise specified by a competent designer.

Table 9.40.3.2.E.

Post Sizes for Diaphragm-Braced Farm Buildings of Low Human Occupancy

Forming Part of Article 9.40.3.2.

| Building Width, m | Wall Height, m | Ungraded Lumber, Full-Dimensioned |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | For Wind Loading q10  0.30 kPa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Post Spacing, 2.4 m |  |  |  |  | Post Spacing, 3.6 m |  |  |  |  | Post Spacing, 4.8 m |  |  |  |  |
|  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  |
|  |  | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 |
| 9.14 |  3.0 | A | A | A | A | A | A | A | A | B | B | A | B | B | C | C |
|  | 3.6 | A | A | A | A | B | A | B | B | B | C | B | C | C | C | C |
|  | 4.2 | B | B | B | B | B | B | B | C | C | C | C | C | C | C | D |
|  | 4.8 | B | B | B | B | C | C | C | C | C | C | C | C | C | D | D |
|  | 6.0 | C | C | C | C | C | C | C | D | D | D | D | D | — | — | — |
| 12.1 |  3.0 | A | A | A | A | B | A | B | B | B | C | B | B | C | C | C |
|  | 3.6 | A | A | B | B | B | B | B | C | C | C | C | C | C | C | D |
|  | 4.2 | B | B | B | B | C | B | C | C | C | C | C | C | D | D | D |
|  | 4.8 | B | B | C | C | C | C | C | C | C | D | C | D | D | D | — |
|  | 6.0 | C | C | C | C | D | C | D | D | — | — | D | — | — | — | — |
| 15.2 |  3.0 | A | A | A | B | B | B | B | C | C | C | B | C | C | D | D |
|  | 3.6 | A | B | B | B | C | B | C | C | C | C | C | C | D | D | D |
|  | 4.2 | B | B | C | C | C | C | C | C | D | D | C | D | D | — | — |
|  | 4.8 | B | C | C | C | C | C | C | D | D | D | D | D | — | — | — |
|  | 6.0 | C | C | C | D | D | D | D | — | — | — | — | — | — | — | — |
| 18.2 |  3.0 | A | A | B | B | C | B | B | C | C | D | C | C | D | D | — |
|  | 3.6 | A | B | B | C | C | C | C | C | D | D | C | D | D | — | — |
|  | 4.2 | B | C | C | C | C | C | C | D | D | D | C | D | — | — | — |
|  | 4.8 | C | C | C | C | D | C | D | D | — | — | D | — | — | — | — |
|  | 6.0 | C | C | D | D | — | D | — | — | — | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |

Legend — Post Sizes

A = 101.6 mm x 152.4 mm

B = 152.4 mm x 152.4 mm

C = 152.4 mm x 203.2 mm

D = 203.2 mm x 203.2 mm

Notes to Table 9.40.3.2.E:

(1) Designs are based on load combinations of total roof load and wind load acting at the same time on a closed building.

(2) Posts shall be oriented with the long dimension parallel to the building width.

(3) Bracing systems shall be specified by a competent designer.

(4) Posts shall be situated on footings and shall be anchored to prevent wind uplift.

(5) Posts shall be constrained against lateral movement at ground level and at the footing.  Concrete floor, splash-rail and uplift anchor help to meet this condition.

(6) Post designs are based on partial fixity condition due to embedment in soil.

(7) Footing excavations should be backfilled with parent material unless otherwise specified by a competent designer.

Table 9.40.3.2.F.

Post Sizes for Diaphragm-Braced Farm Buildings of Low Human Occupancy

Forming Part of Article 9.40.3.2.

| Building Width, m | Wall Height, m | Ungraded Lumber, Full-Dimensioned |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | For Wind Loading q10  0.45 kPa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Post Spacing, 2.4 m |  |  |  |  | Post Spacing, 3.6 m |  |  |  |  | Post Spacing, 4.8 m |  |  |  |  |
|  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  |
|  |  | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 |
| 9.14 |  3.0 | A | A | A | A | A | A | A | B | B | B | B | B | C | C | C |
|  | 3.6 | A | A | A | B | B | B | B | B | C | C | C | C | C | C | C |
|  | 4.2 | B | B | B | B | C | C | C | C | C | C | C | C | C | D | D |
|  | 4.8 | B | B | C | C | C | C | C | C | C | D | C | D | D | D | — |
|  | 6.0 | C | C | C | C | C | D | D | D | — | — | — | — | — | — | — |
| 12.1 |  3.0 | A | A | A | B | B | B | B | B | C | C | B | C | C | C | C |
|  | 3.6 | A | A | B | B | B | B | C | C | C | C | C | C | C | D | D |
|  | 4.2 | B | B | B | C | C | C | C | C | C | D | C | D | D | D | — |
|  | 4.8 | B | C | C | C | C | C | C | D | D | D | D | D | — | — | — |
|  | 6.0 | C | C | C | D | D | D | D | — | — | — | — | — | — | — | — |
| 15.2 |  3.0 | A | A | B | B | B | B | B | C | C | C | C | C | C | D | D |
|  | 3.6 | A | B | B | C | C | C | C | C | C | D | C | C | D | D | — |
|  | 4.2 | B | C | C | C | C | C | C | C | D | D | D | D | D | — | — |
|  | 4.8 | C | C | C | C | C | C | D | D | D | — | D | — | — | — | — |
|  | 6.0 | C | C | D | D | — | D | — | — | — | — | — | — | — | — | — |
| 18.2 |  3.0 | A | B | B | B | C | B | C | C | C | D | C | C | D | D | — |
|  | 3.6 | B | B | C | C | C | C | C | C | D | D | C | D | D | — | — |
|  | 4.2 | B | C | C | C | C | C | C | D | D | — | D | D | — | — | — |
|  | 4.8 | C | C | C | C | D | D | D | D | — | — | — | — | — | — | — |
|  | 6.0 | C | D | D | — | — | — | — | — | — | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |

Legend — Post Sizes

A = 101.6 mm x 152.4 mm

B = 152.4 mm x 152.4 mm

C = 152.4 mm x 203.2 mm

D = 203.2 mm x 203.2 mm

Notes to Table 9.40.3.2.F:

(1) Designs are based on load combinations of total roof load and wind load acting at the same time on a closed building.

(2) Posts shall be oriented with the long dimension parallel to the building width.

(3) Bracing systems shall be specified by a competent designer.

(4) Posts shall be situated on footings and shall be anchored to prevent wind uplift.

(5) Posts shall be constrained against lateral movement at ground level and at the footing.  Concrete floor, splash-rail and uplift anchor help to meet this condition.

(6) Post designs are based on partial fixity condition due to embedment in soil.

(7) Footing excavations should be backfilled with parent material unless otherwise specified by a competent designer.

Table 9.40.3.2.G.

Post Sizes for Knee-Braced Farm Buildings of Low Human Occupancy

Forming Part of Article 9.40.3.2.

| Building Width, m | Wall Height, m | Ungraded Lumber, Full-Dimensioned |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | For Wind Loading q10  0.30 kPa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Post Spacing, 2.4 m |  |  |  |  | Post Spacing, 3.6 m |  |  |  |  | Post Spacing, 4.8 m |  |  |  |  |
|  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  |
|  |  | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 |
| 9.14 |  3.0 | A | A | A | A | A | A | A | B | B | B | B | B | C | C | C |
|  | 3.6 | A | A | A | B | B | B | B | B | C | C | B | C | C | C | C |
|  | 4.2 | B | B | B | B | C | B | C | C | C | C | C | C | C | D | D |
|  | 4.8 | C | C | C | C | C | C | C | C | C | D | C | C | D | D | — |
|  | 6.0 | C | C | C | C | D | C | D | D | — | — | D | — | — | — | — |
| 12.1 |  3.0 | A | A | A | B | B | A | B | B | C | C | B | C | C | C | D |
|  | 3.6 | A | B | B | B | C | B | C | C | C | C | C | C | C | D | D |
|  | 4.2 | B | B | C | C | C | C | C | C | C | D | C | C | D | D | — |
|  | 4.8 | C | C | C | C | C | C | C | D | D | D | D | D | — | — | — |
|  | 6.0 | C | C | C | D | D | D | D | — | — | — | — | — | — | — | — |
| 15.2 |  3.0 | A | A | B | B | B | B | B | C | C | C | C | C | C | D | D |
|  | 3.6 | A | B | B | C | C | C | C | C | C | D | C | C | D | D | — |
|  | 4.2 | B | C | C | C | C | C | C | D | D | D | C | D | — | — | — |
|  | 4.8 | C | C | C | C | D | C | D | D | — | — | D | — | — | — | — |
|  | 6.0 | C | D | D | D | — | D | — | — | — | — | — | — | — | — | — |
| 18.2 |  3.0 | A | B | B | C | C | B | C | C | C | D | C | C | D | D | — |
|  | 3.6 | B | B | C | C | C | C | C | C | D | D | C | D | D | — | — |
|  | 4.2 | C | C | C | C | D | C | C | D | — | — | D | D | — | — | — |
|  | 4.8 | C | C | C | D | D | C | D | — | — | — | D | — | — | — | — |
|  | 6.0 | C | D | — | — | — | — | — | — | — | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |

Legend — Post Sizes

A = 101.6 mm x 152.4 mm

B = 152.4 mm x 152.4 mm

C = 152.4 mm x 203.2 mm

D = 203.2 mm x 203.2 mm

Notes to Table 9.40.3.2.G

(1) Designs are based on load combinations of total roof load and wind load acting at the same time on a closed building.

(2)	 Posts shall be oriented with the long dimension parallel to the building width.

(3) Bracing systems shall be specified by a competent designer.

(4) Posts shall be situated on footings and shall be anchored to prevent wind uplift.

(5) Posts shall be constrained against lateral movement at ground level and at the footing.  Concrete floor, splash-rail and uplift anchor help to meet this condition.

(6) Post designs are based on partial fixity condition due to embedment in soil.

(7) Footing excavations should be backfilled with parent material unless otherwise specified by a competent designer.

Table 9.40.3.2.H.

Post Sizes for Knee-Braced Farm Buildings of Low Human Occupancy

Forming Part of Article 9.40.3.2.

| Building Width, m | Wall Height, m | Ungraded Lumber, Full-Dimensioned |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | For Wind Loading q10  0.45 kPa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Post Spacing, 2.4 m |  |  |  |  | Post Spacing, 3.6 m |  |  |  |  | Post Spacing, 4.8 m |  |  |  |  |
|  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  | Roof Load, kPa |  |  |  |  |
|  |  | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 |
| 9.14 |  3.0 | A | A | A | A | B | A | B | B | B | C | B | C | C | C | C |
|  | 3.6 | A | A | B | B | B | B | C | C | C | C | C | C | C | C | D |
|  | 4.2 | B | B | B | C | C | C | C | C | C | C | C | C | D | D | D |
|  | 4.8 | C | C | C | C | C | C | C | C | D | D | D | D | D | — | — |
|  | 6.0 | C | C | C | D | D | D | D | — | — | — | — | — | — | — | — |
| 12.1 |  3.0 | A | A | B | B | B | B | B | C | C | C | C | C | C | C | D |
|  | 3.6 | A | B | B | C | C | C | C | C | C | C | C | C | D | D | D |
|  | 4.2 | B | C | C | C | C | C | C | C | D | D | C | D | D | — | — |
|  | 4.8 | C | C | C | C | C | C | D | D | D | — | D | — | — | — | — |
|  | 6.0 | C | D | D | D | — | — | — | — | — | — | — | — | — | — | — |
| 15.2 |  3.0 | A | B | B | B | C | B | C | C | C | C | C | C | D | D | D |
|  | 3.6 | B | B | C | C | C | C | C | C | D | D | C | D | D | — | — |
|  | 4.2 | C | C | C | C | C | C | C | D | D | — | D | D | — | — | — |
|  | 4.8 | C | C | C | D | D | D | D | — | — | — | — | — | — | — | — |
|  | 6.0 | D | D | D | — | — | — | — | — | — | — | — | — | — | — | — |
| 18.2 |  3.0 | A | B | B | C | C | C | C | C | D | D | C | D | D | — | — |
|  | 3.6 | B | C | C | C | C | C | C | D | D | — | D | D | — | — | — |
|  | 4.2 | C | C | C | C | C | C | C | D | D | — | D | D | — | — | — |
|  | 4.8 | C | C | C | C | D | C | D | D | — | — | D | — | — | — | — |
|  | 6.0 | C | C | D | D | D | D | — | — | — | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |

Legend — Post Sizes

A = 101.6 mm x 152.4 mm

B = 152.4 mm x 152.4 mm

C = 152.4 mm x 203.2 mm

D = 203.2 mm x 203.2 mm

Notes to Table 9.40.3.2.H.:

(1) Designs are based on load combinations of total roof load and wind load acting at the same time on a closed building.

(2) Posts shall be oriented with the long dimension parallel to the building width.

(3) Bracing systems shall be specified by a competent designer.

(4) Posts shall be situated on footings and shall be anchored to prevent wind uplift.

(5) Posts shall be constrained against lateral movement at ground level and at the footing.  Concrete floor, splash-rail and uplift anchor help to meet this condition.

(6) Post designs are based on partial fixity condition due to embedment in soil.

(7) Footing excavations should be backfilled with parent material unless otherwise specified by a competent designer.

Table 9.40.3.2.I.

Post Sizes for Farm Buildings of Low Human Occupancy (With Second Storey Loading)

Forming Part of Article 9.40.3.2.

| Side wall Height, m | Total Roof Load, kPa | Spruce – Pine – Fir, No. 1, Dressed (Post and Timber Grades) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Second Storey Plate, kN/m |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Wind load: q10  0.30 kPa |  |  |  |  |  |  |  | Wind load: q10  0.45 kPa |  |  |  |  |  |  |  |  |
|  |  | 2.4 m o.c. |  |  |  | 3.600 m o.c. |  |  |  | 2.400 m o.c. |  |  |  | 3.600 m o.c. |  |  |  |  |
|  |  | Building Width, m |  |  |  | Building Width, m |  |  |  | Building Width, m |  |  |  | Building Width, m |  |  |  |  |
|  |  | 9.14 | 12.2 | 15.2 | 18.3 | 9.14 | 12.2 | 15.2 | 18.3 | 9.14 | 12.2 | 15.2 | 18.3 | 9.14 | 12.2 | 15.2 | 18.3 |  |
| 3.0 | 1.9 | A | A | A | A | A | A | B | B | A | A | A | A | A | B | B | B | 14.6 |
|  | 2.4 | A | A | A | A | A | B | B | B | A | A | A | B | A | B | B | B |  |
|  | 2.8 | A | A | A | B | A | B | B | C | A | A | B | B | B | B | B | C |  |
|  | 3.3 | A | A | B | B | B | B | B | C | A | A | B | B | B | B | C | C |  |
| 3.6 | 1.9 | A | A | A | B | A | B | B | C | A | A | B | B | B | B | C | C | 14.6 |
|  | 2.4 | A | A | B | B | B | B | C | C | A | B | B | B | B | C | C | C |  |
|  | 2.8 | A | B | B | B | B | B | C | C | A | B | B | B | B | C | C | C |  |
|  | 3.3 | A | B | B | C | B | C | C | C | B | B | B | C | C | C | C | C |  |
| 3.0 | 1.9 | A | A | A | A | A | A | B | B | A | A | A | A | A | A | B | B | 7.3 |
|  | 2.4 | A | A | A | A | A | A | B | B | A | A | A | A | A | B | B | B |  |
|  | 2.8 | A | A | A | B | A | B | B | B | A | A | A | B | B | B | B | C |  |
|  | 3.3 | A | A | B | B | B | B | B | C | A | A | B | B | B | B | C | C |  |
| 3.6 | 1.9 | A | A | A | B | A | B | B | B | A | A | B | B | B | B | C | C | 7.3 |
|  | 2.4 | A | A | B | B | B | B | C | C | A | B | B | B | B | B | C | C |  |
|  | 2.8 | A | A | B | B | B | B | C | C | A | B | B | B | B | C | C | C |  |
|  | 3.3 | A | B | B | B | B | C | C | C | B | B | B | C | C | C | C | C |  |
| 3.0 | 1.9 | A | A | A | A | A | A | A | B | A | A | A | A | A | A | B | B | 3.6 |
|  | 2.4 | A | A | A | A | A | A | B | B | A | A | A | A | A | B | B | B |  |
|  | 2.8 | A | A | A | B | A | B | B | B | A | A | A | B | B | B | B | C |  |
|  | 3.3 | A | A | A | B | A | B | B | C | A | A | B | B | B | B | C | C |  |
| 3.6 | 1.9 | A | A | A | B | A | B | B | B | A | A | A | B | B | B | B | C | 3.6 |
|  | 2.4 | A | A | B | B | B | B | B | C | A | A | B | B | B | B | C | C |  |
|  | 2.8 | A | A | B | B | B | B | C | C | A | B | B | B | B | C | C | C |  |
|  | 3.3 | A | B | B | B | B | C | C | C | A | B | B | C | B | C | C | C |  |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 |

Legend — Post Sizes

A =  89 mm x 140 mm

B = 140 mm x 140 mm

C = 140 mm x 184 mm

Notes to Table 9.40.3.2.I.:

(1) Designs are based on load combinations of total roof load, wind load and stored product acting at the same time on a closed building.

(2) All notes following Table 9.40.3.2.A. apply, with the following conditions/exceptions:

—14.6 kN/m loading: Full 4.8 m sidewall hay/straw storage space above.  It is supported by beams spaced at 3.6 m o.c.  The outside plate carries a 1.8 m floor width.  If the loading is greater, refer to a qualified person for design.

—7.3 kN/m loading: Full 2.4 m sidewall hay/straw storage space above or a gambrel roof structure > 9.14 m in total width.  Floor support beams as above.

—3.6 kN/m loading: Small gambrel roof structure or storage space for light storage.  Floor support beams as above.

Table 9.40.3.2.J.

Round Posts

Forming Part of Article 9.40.3.2.

| Ungraded Lumber Full-dimension Size, mm | Equivalent Diameter Full Size, mm |
| --- | --- |
| 50.8 x 101.6 | 101.6 |
| 50.8 x 152.4 | 127.0 |
| 50.8 x 203.2 | 152.4 |
| 50.8 x 254.0 | 177.8 |
| 50.8 x 304.8 | 203.2 |
| 76.2 x 304.8 | 228.6 |
| 76.2 x 355.6 | 254.0 |
| 101.6 x 152.4 | 158.8 |
| 101.6 x 304.8 | 203.2 |
| 101.6 x 355.6 | 279.4 |
| 127.0 x 203.2 | 209.6 |
| 127.0 x 254.0 | 241.3 |
| 152.4 x 152.4 | 190.5 |
| 152.4 x 203.2 | 222.3 |
| 152.4 x 254.0 | 260.4 |
| 203.2 x 203.2 | 247.7 |
| 203.2 x 254.0 | 285.8 |
| 203.2 x 304.8 | 317.5 |
| 254.0 x 304.8 | 342.9 |
| 254.0 x 355.6 | 381.0 |
| Column 1 | 2 |

Notes to Table 9.40.3.2.J.:

(1) When selecting round, ungraded lumber, ensure that the material is of good quality.

(2) Any timber that is in contact with ground shall be chemically treated to resist growth of fungus and decay.

(3) Equivalent diameter indicated in this Table refers to the smallest diameter of a tapering pole.

(4) Used hydro or telephone poles may be used if they are of good quality and are chemically treated to prevent decay.

(5) Indicated equivalent diameter will provide bending, shear and deflection resisting capabilities equal to or better than the rectangular section that it replaces.

Table 9.40.3.3.K.

Common Rafter Sizes for Farm Buildings of Low Human Occupancy

Forming Part of Article 9.40.3.3.

| Rafter Span, m | Spruce – Pine – Fir, No. 1 and No. 2 (Dressed Lumber) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Rafter Spacing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 300 mm |  |  |  |  | 400 mm |  |  |  |  | 600 mm |  |  |  |  |
|  | Live Load, kPa |  |  |  |  | Live Load, kPa |  |  |  |  | Live Load, kPa |  |  |  |  |
|  | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 |
| 2.4 | A | A | B | B | B | A | B | B | B | B | B | B | B | B | B |
| 3.0 | B | B | B | B | B | B | B | B | B | C | B | B | C | C | D |
| 3.6 | B | B | C | C | C | B | C | C | C | C | C | C | D | D | D |
| 4.2 | B | C | C | C | C | C | C | C | D | D | C | D | D | E | E |
| 4.8 | C | C | D | D | D | C | D | D | E | E | D | E | E | — | — |
| 5.4 | C | D | D | D | E | D | D | E | E | — | E | E | — | — | — |
| 6.0 | D | D | D | E | — | D | E | E | — | — | E | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |

Legend — Rafter Sizes

A = 38 mm x 89 mm

B = 38 mm x 140 mm

C = 38 mm x 184 mm

D = 38 mm x 235 mm

E = 38 mm x 286 mm

Note to Table 9.40.3.3.K.:

(1) The rafter span is the unsupported length of the rafter from plate to plate or from plate to ridge.  A dead load of 0.24 kPa is incorporated to allow for weight of the roof sheathing and rafter.

Table 9.40.3.3.L.

Common Rafter Sizes for Farm Buildings of Low Human Occupancy

Forming Part of Article 9.40.3.3.

| Rafter Span, m | Ungraded Lumber, Full-Dimension |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Rafter Spacing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 300 mm |  |  |  |  | 400 mm |  |  |  |  | 600 mm |  |  |  |  |
|  | Live Load, kPa |  |  |  |  | Live Load, kPa |  |  |  |  | Live Load, kPa |  |  |  |  |
|  | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 | 1.4 | 1.9 | 2.4 | 2.8 | 3.3 |
| 2.4 | A | A | B | B | B | B | B | B | B | C | B | B | C | C | D |
| 3.0 | B | B | B | C | C | B | C | C | C | D | C | C | D | D | E |
| 3.6 | B | C | C | D | D | C | C | D | D | E | D | D | E | F | F |
| 4.2 | C | C | D | D | E | D | D | E | E | F | E | F | F | F | G |
| 4.8 | C | D | E | E | F | D | E | F | F | F | F | F | F | G | I |
| 5.4 | D | E | F | F | F | E | F | F | F | G | F | G | H | I | — |
| 6.0 | E | F | F | F | G | F | F | G | G | I | F | H | I | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |

Legend — Rafter Sizes

A = 50.8 mm x 101.6 mm

B = 50.8 mm x 152.4 mm

C = 50.8 mm x 203.2 mm

D = 50.8 mm x 254.0 mm

E = 50.8 mm x 304.8 mm

F = 76.2 mm x 304.8 mm

G = 76.2 mm x 355.6 mm

H = 101.6 mm x 304.8 mm

I = 101.6 mm x 355.6 mm

Note to Table 9.40.3.3.L.:

(1) The rafter span is the unsupported length of the rafter from plate to plate or from plate to ridge.  A dead load of 0.24 kPa is incorporated to allow for weight of the roof sheathing and rafter.

Table 9.40.3.3.M.

Floor Joists for Farm Buildings of Low Human Occupancy — Intermittent Loads(1)

Forming Part of Article 9.40.3.3.

| Joist Span, m | Spruce – Pine – Fir, No. 1 and No. 2 (Dressed Lumber) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Joist Spacing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 300 mm |  |  |  |  |  | 400 mm |  |  |  |  |  | 600 mm |  |  |  |  |  |
|  | Live Load, kPa |  |  |  |  |  | Live Load, kPa |  |  |  |  |  | Live Load, kPa |  |  |  |  |  |
|  | 1.9 | 2.8 | 3.8 | 4.8 | 6.7 | 8.6 | 1.9 | 2.8 | 3.8 | 4.8 | 6.7 | 8.6 | 1.9 | 2.8 | 3.8 | 4.8 | 6.7 | 8.6 |
| 2.4 | A | B | B | B | B | C | B | B | B | B | C | C | B | B | B | C | D | D |
| 3.0 | B | B | B | C | C | D | B | B | C | C | D | D | B | C | C | D | E | — |
| 3.6 | B | C | C | C | D | D | C | C | C | D | E | E | C | D | D | E | — | — |
| 4.2 | C | C | D | D | E | E | C | D | D | E | — | — | D | D | E | — | — | — |
| 4.8 | C | D | D | E | — | — | D | D | E | E | — | — | D | E | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 |

Legend — Joist Sizes

A = 38 mm x 89 mm

B = 38 mm x 140 mm

C = 38 mm x 184 mm

D = 38 mm x 235 mm

E = 38 mm x 286 mm

Notes to Table 9.40.3.3.M.:

(1) Loads are applied to the floor intermittently. (When loads are applied for extended periods of time, use Table 9.40.3.3.N.).

(2) A dead load of 0.48 kPa is incorporated to allow for the dead weight of the floor system.

Table 9.40.3.3.N.

Floor Joists for Farm Buildings of Low Human Occupancy — Continuous Loads(1)

Forming Part of Article 9.40.3.3.

| Joist Span, m | Spruce – Pine – Fir, No. 1 and No. 2 (Dressed Lumber) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Joist Spacing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 300 mm |  |  |  |  |  | 400 mm |  |  |  |  |  | 600 mm |  |  |  |  |  |
|  | Live Load, kPa |  |  |  |  |  | Live Load, kPa |  |  |  |  |  | Live Load, kPa |  |  |  |  |  |
|  | 1.9 | 2.8 | 3.8 | 4.8 | 6.7 | 8.6 | 1.9 | 2.8 | 3.8 | 4.8 | 6.7 | 8.6 | 1.9 | 2.8 | 3.8 | 4.8 | 6.7 | 8.6 |
| 2.4 | A | B | B | B | C | C | B | B | B | C | D | E | B | C | C | D | — | — |
| 3.0 | B | B | C | C | D | E | B | C | C | D | E | — | C | D | D | E | — | — |
| 3.6 | B | C | D | D | E | — | C | D | D | E | — | — | D | E | — | — | — | — |
| 4.2 | C | D | D | E | — | — | D | E | E | — | — | — | E | — | — | — | — | — |
| 4.8 | D | D | E | — | — | — | D | E | — | — | — | — | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 |

Legend — Joist Sizes

A = 38 mm x 89 mm

B = 38 mm x 140 mm

C = 38 mm x 184 mm

D = 38 mm x 235 mm

E = 38 mm x 286 mm

Notes to Table 9.40.3.3.N.:

(1) For use of floors that support hay, straw, grain or other continuous loads.

(2) A dead load of 0.48 kPa is incorporated to allow for the dead weight of the floor system.

Table 9.40.3.3.O.

Built-up Wood Beam Sizes for Farm Buildings of Low Human Occupancy — Intermittent Loads(1)

Forming Part of Article 9.40.3.3.

| Beam Span, m | Spruce – Pine – Fir, No. 1 and No. 2 (Dressed Lumber) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Total Load on Beam, kN/m |  |  |  |  |  |  |  |  |  |  |
|  | 5.84 | 8.76 | 11.67 | 14.59 | 17.51 | 20.43 | 23.35 | 26.27 | 29.19 | 32.11 | 35.03 |
| 1.8 | A | A | A | B | B | D | D | G | G | J | L |
| 2.4 | A | A | B | D | E | H | J | L | — | — | — |
| 3.0 | A | C | E | H | J | K | — | — | — | — | — |
| 3.6 | C | H | J | L | — | — | — | — | — | — | — |
| 4.2 | E | J | L | — | — | — | — | — | — | — | — |
| 4.8 | I | L | — | — | — | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |

Legend – Beam Sizes

A = 3 – 38 mm x 184 mm

B = 4 – 38 mm x 184 mm

C = 3 – 38 mm x 235 mm

D = 5 – 38 mm x 184 mm

E = 3 – 38 mm x 286 mm

F = 4 – 38 mm x 235 mm

G = 6 – 38 mm x 184 mm

H = 5 – 38 mm x 235 mm

I = 4 – 38 mm x 286 mm

J = 6 – 38 mm x 235 mm

K = 5 – 38 mm x 286 mm

L = 6 – 38 mm x 286 mm

Notes to Table 9.40.3.3.O.:

(1) Loads are applied to the beam intermittently.

(2) A dead load of 0.584 kN/m is assumed for all beams.

(3) Floors systems supporting heavy loads over larger spans will require the use of steel beams or other specialized materials.

Table 9.40.3.3.P.

Built-up Wood Beam Sizes for Farm Buildings of Low Human Occupancy — Continuous Loads(1)

Forming Part of Article 9.40.3.3.

| Beam Span, m | Spruce – Pine – Fir, No. 1 and No. 2 (Dressed Lumber) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Total Load on Beam, kN/m |  |  |  |  |  |  |
|  | 5.84 | 8.76 | 11.67 | 14.59 | 17.51 | 20.43 | 23.35 |
| 1.8 | A | A | B | D | G | J | L |
| 2.4 | A | C | E | J | L | — | — |
| 3.0 | D | H | J | L | — | — | — |
| 3.6 | H | K | — | — | — | — | — |
| 4.2 | K | — | — | — | — | — | — |
| 4.8 | L | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |

Legend – Beam Sizes

A = 3 – 38 mm x 184 mm

B = 4 – 38 mm x 184 mm

C = 3 – 38 mm x 235 mm

D = 5 – 38 mm x 184 mm

E = 3 – 38 mm x 286 mm

F = 4 – 38 mm x 235 mm

G = 6 – 38 mm x 184 mm

H = 5 – 38 mm x 235 mm

I = 4 – 38 mm x 286 mm

J = 6 – 38 mm x 235 mm

K = 5 – 38 mm x 286 mm

L = 6 – 38 mm x 286 mm

Notes to Table 9.40.3.3.P.:

(1) For use of floors that support hay, straw, grain or other continuous loads.

(2) A dead load of 0.48 kPa is assumed for all beams.

(3) Floor systems supporting heavy loads over larger spans will require use of steel beams or other specialized materials.

Table 9.40.3.3.Q.

Ungraded Lumber, Full-Dimension Roof Beam Sizes for Farm Buildings of Low Human Occupancy(1)

Forming Part of Article 9.40.3.3.

| Beam Span, m | Total Load on Built-up Wood Beam, kN/m |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 5.84 | 8.76 | 11.67 | 14.59 | 17.51 | 20.43 | 23.35 | 26.27 |
| 1.8 | A | A | B | C | D | F | G | H |
| 2.4 | B | D | E | H | I | J | — | — |
| 3.0 | D | G | I | — | — | — | — | — |
| 3.6 | G | J | — | — | — | — | — | — |
| 4.2 | J | — | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |

Legend – Built-up Wood Beam Sizes

A = 3 – 50.8 mm x 203.2 mm

B = 4 – 50.8 mm x 203.2 mm

C = 3 – 50.8 mm x 254.0 mm

D = 5 – 50.8 mm x 203.2 mm

E = 6 – 50.8 mm x 203.2 mm

F = 4 – 50.8 mm x 254.0 mm

G = 5 – 50.8 mm x 254.0 mm

H = 4 – 50.8 mm x 304.8 mm

I = 5 – 50.8 mm x 304.8 mm

J = 6 – 50.8 mm x 304.8 mm

Notes to Table 9.40.3.3.Q.:

(1) Ungraded lumber, full-dimension, built-up wood beam.

(2) A dead load of 0.584 kN/m is assumed.

(3) Beams are sized for roof load only.

Table 9.40.3.3.R.

Ungraded Lumber, Full-Dimension Roof Beam Sizes for Farm Buildings of Low Human Occupancy(1)

Forming Part of Article 9.40.3.3.

| Beam Span, m | Total Load on Built-up Sawn Beam, kN/m |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 5.84 | 8.76 | 11.67 | 14.59 | 17.51 | 20.43 | 23.35 | 26.27 |
| 1.8 | A | A | B | C | D | E | F | G |
| 2.4 | A | B | D | D | F | G | — | — |
| 3.0 | C | D | E | F | — | — | — | — |
| 3.6 | D | F | G | — | — | — | — | — |
| 4.2 | E | G | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |

Legend — Sawn Beam Sizes

A = 127.0 mm x 203.2 mm

B = 127.0 mm x 254.0 mm

C = 152.4 mm x 254.0 mm

D = 203.2 mm x 254.0 mm

E = 203.2 mm x 304.8 mm

F = 254.0 mm x 304.8 mm

G = 254.0 mm x 355.6 mm

Notes to Table 9.40.3.3.R.:

(1) Ungraded lumber, full-dimension, sawn wood beam.

(2) A dead load of 0.584 kN/m is assumed.

(3) Beams are sized for roof load only.

Table 9.40.3.3.S.

Roof Plate — Beams and Lintels for Farm Buildings of Low Human Occupancy

Forming Part of Article 9.40.3.3.

| Building Width, m | Spruce – Pine – Fir, No. 1 and No. 2 (Dressed Lumber) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Total Roof Load, kPa, with Post Spacing at 2.4 m |  |  |  |  |  |  |  |  |
|  | A | B | C | D | E | F | G | H | I |
| 7.3 | 1.67 | 2.77 | 3.68 | 2.49 | 4.11 | 5.50 | 3.35 | 5.55 | 7.42 |
| 8.5 | 1.43 | 2.34 | 3.16 | 2.15 | 3.54 | 4.74 | 2.87 | 4.74 | 6.36 |
| 9.7 | 1.24 | 2.05 | 2.77 | 1.86 | 3.11 | 4.11 | 2.53 | 4.16 | 5.55 |
| 10.9 | — | 1.81 | 2.44 | 1.67 | 2.72 | 3.68 | 2.25 | 3.68 | 4.93 |
| 12.1 | — | 1.62 | 2.20 | 1.48 | 2.49 | 3.30 | 2.01 | 3.30 | 4.45 |
| 13.4 | — | 1.48 | 2.01 | 1.34 | 2.25 | 3.01 | 1.81 | 3.01 | 4.02 |
| 14.6 | — | 1.38 | 1.81 | 1.24 | 2.05 | 2.72 | 1.67 | 2.77 | 3.68 |
| 15.8 | — | 1.24 | 1.67 | — | 1.91 | 2.53 | 1.53 | 2.53 | 3.40 |
| 17.0 | — | — | 1.58 | — | 1.77 | 2.34 | 1.43 | 2.39 | 3.16 |
| 18.2 | — | — | 1.48 | — | 1.62 | 2.20 | 1.34 | 2.20 | 2.96 |
| Building Width, m | Total Roof Load, kPa, with Post Spacing at 3.0 m |  |  |  |  |  |  |  |  |
|  | A | B | C | D | E | F | G | H | I |
| 7.3 | — | 1.72 | 2.29 | 1.53 | 2.58 | 3.44 | 2.10 | 3.44 | 4.64 |
| 8.5 | — | 1.48 | 1.96 | 1.34 | 2.20 | 2.96 | 1.77 | 2.96 | 3.97 |
| 9.7 | — | 1.29 | 1.72 | — | 1.91 | 2.58 | 1.58 | 2.58 | 3.44 |
| 10.9 | — | — | 1.53 | — | 1.72 | 2.29 | 1.38 | 2.29 | 3.06 |
| 12.1 | — | — | 1.38 | — | 1.53 | 2.05 | 1.24 | 2.05 | 2.77 |
| 13.4 | — | — | 1.24 | — | 1.38 | 1.86 | — | 1.86 | 2.53 |
| 14.6 | — | — | — | — | 1.29 | 1.72 | — | 1.72 | 2.29 |
| 15.8 | — | — | — | — | — | 1.58 | — | 1.58 | 2.10 |
| 17.0 | — | — | — | — | — | 1.48 | — | 1.48 | 1.96 |
| 18.2 | — | — | — | — | — | 1.38 | — | 1.38 | 1.81 |
| Building Width, m | Total Roof Load, kPa, with Post Spacing at 3.6 m |  |  |  |  |  |  |  |  |
|  | A | B | C | D | E | F | G | H | I |
| 7.3 | — | 1.38 | 1.81 | 1.24 | 2.05 | 2.72 | 1.67 | 2.77 | 3.68 |
| 8.5 | — | — | 1.58 | — | 1.77 | 2.34 | 1.43 | 2.39 | 3.16 |
| 9.7 | — | — | 1.38 | — | 1.53 | 2.05 | 1.24 | 2.05 | 2.77 |
| 10.9 | — | — | 1.19 | — | 1.38 | 1.81 | — | 1.81 | 2.44 |
| 12.1 | — | — | — | — | 1.24 | 1.62 | — | 1.67 | 2.20 |
| 13.4 | — | — | — | — | — | 1.48 | — | 1.48 | 2.01 |
| 14.6 | — | — | — | — | — | 1.38 | — | 1.38 | 1.81 |
| 15.8 | — | — | — | — | — | 1.24 | — | 1.29 | 1.67 |
| 17.0 | — | — | — | — | — | — | — | — | 1.58 |
| 18.2 | — | — | — | — | — | — | — | — | 1.48 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |

Legend — Roof Plate-Beam and Lintel Sizes

A = 2 – 38 mm x 184 mm

B = 3 – 38 mm x 184 mm

C = 4 – 38 mm x 184 mm

D = 2 – 38 mm x 235 mm

E = 3 – 38 mm x 235 mm

F = 4 – 38 mm x 235 mm

G = 2 – 38 mm x 286 mm

H = 3 – 38 mm x 286 mm

I = 4 – 38 mm x 286 mm

Notes to Table 9.40.3.3.S.:

(1) Trusses are at 1.2 m on centres.

(2) Plate-beam/lintel loading can be very significant.

(3) Specifications for anchorage at supporting posts must be specified by a competent designer.

Table 9.40.3.3.T.

Roof Plate — Beams and Lintels for Farm Buildings of Low Human Occupancy

Forming Part of Article 9.40.3.3.

| Building Width, m | Ungraded Lumber-Full Dimension |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Total Roof Load, kPa, with Post Spacing at 2.4 m |  |  |  |  |  |  |  |  |
|  | A | B | C | D | E | F | G | H | I |
| 7.3 | — | 1.72 | 2.29 | 1.48 | 2.44 | 3.25 | 1.91 | 3.20 | 4.26 |
| 8.5 | — | 1.43 | 1.96 | 1.24 | 2.10 | 2.77 | 1.67 | 2.72 | 3.68 |
| 9.7 | — | 1.29 | 1.72 | — | 1.81 | 2.44 | 1.43 | 2.39 | 3.20 |
| 10.9 | — | — | 1.53 | — | 1.62 | 2.15 | 1.29 | 2.15 | 2.87 |
| 12.1 | — | — | 1.34 | — | 1.48 | 1.96 | — | 1.91 | 2.58 |
| 13.4 | — | — | 1.24 | — | 1.34 | 1.77 | — | 1.72 | 2.34 |
| 14.6 | — | — | — | — | 1.19 | 1.62 | — | 1.58 | 2.15 |
| 15.8 | — | — | — | — | — | 1.48 | — | 1.48 | 1.96 |
| 17.0 | — | — | — | — | — | 1.38 | — | 1.38 | 1.81 |
| 18.2 | — | — | — | — | — | 1.29 | — | 1.29 | 1.72 |
| Building Width, m | Total Roof Load, kPa, with Post Spacing at 3.0 m |  |  |  |  |  |  |  |  |
|  | A | B | C | D | E | F | G | H | I |
| 7.3 | — | — | 1.43 | — | 1.53 | 2.05 | 1.19 | 2.01 | 2.68 |
| 8.5 | — | — | 1.19 | — | 1.29 | 1.72 | — | 1.72 | 2.29 |
| 9.7 | — | — | — | — | — | 1.53 | — | 1.48 | 2.01 |
| 10.9 | — | — | — | — | — | 1.34 | — | 1.34 | 1.77 |
| 12.1 | — | — | — | — | — | 1.19 | — | — | 1.58 |
| 13.4 | — | — | — | — | — | — | — | — | 1.43 |
| 14.6 | — | — | — | — | — | — | — | — | 1.34 |
| 15.8 | — | — | — | — | — | — | — | — | 1.24 |
| 17.0 | — | — | — | — | — | — | — | — | — |
| 18.2 | — | — | — | — | — | — | — | — | — |
| Building Width, m | Total Roof Load, kPa, with Post Spacing at 3.6 m |  |  |  |  |  |  |  |  |
|  | A | B | C | D | E | F | G | H | I |
| 7.3 | — | — | — | — | 1.19 | 1.62 | — | 1.58 | 2.15 |
| 8.5 | — | — | — | — | — | 1.38 | — | 1.38 | 1.81 |
| 9.7 | — | — | — | — | — | 1.19 | — | — | 1.58 |
| 10.9 | — | — | — | — | — | — | — | — | 1.43 |
| 12.1 | — | — | — | — | — | — | — | — | 1.29 |
| 13.4 | — | — | — | — | — | — | — | — | — |
| 14.6 | — | — | — | — | — | — | — | — | — |
| 15.8 | — | — | — | — | — | — | — | — | — |
| 17.0 | — | — | — | — | — | — | — | — | — |
| 18.2 | — | — | — | — | — | — | — | — | — |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |

Legend – Roof Plate–Beam and Lintel Sizes:

A = 2 – 50.8 mm x 203.2 mm

B = 3 – 50.8 mm x 203.2 mm

C = 4 – 50.8 mm x 203.2 mm

D = 2 – 50.8 mm x 254.0 mm

E = 3 – 50.8 mm x 254.0 mm

F = 4 – 50.8 mm x 254.0 mm

G = 2 – 50.8 mm x 304.8 mm

H = 3 – 50.8 mm x 304.8 mm

I = 4 – 50.8 mm x 304.8 mm

Notes to Table 9.40.3.3.T.:

(1) Trusses are at 1.2 m on centres.

(2) Plate-beam/lintel loading can be very significant.

(3) Specifications for anchorage at supporting posts must be specified by a competent designer.

Table 9.40.3.4.U.

Stud Sizes for Farm Buildings of Low Human Occupancy (Single Storey)

Forming Part of Article 9.40.3.4.

| Sidewall Height, m | Total Roof Load, kPa | Spruce – Pine – Fir, No. 1 and No. 2 (Dressed Lumber) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Wind Load: q10  0.30 kPa |  |  |  |  |  |  |  | Wind Load: q10  0.45 kPa |  |  |  |  |  |  |  |
|  |  | 400 mm o.c. |  |  |  | 600 mm o.c. |  |  |  | 400 mm o.c. |  |  |  | 600 mm o.c. |  |  |  |
|  |  | Building Width, m |  |  |  | Building Width, m |  |  |  | Building Width, m |  |  |  | Building Width, m |  |  |  |
|  |  | 9.14 | 12.2 | 15.2 | 18.3 | 9.14 | 12.2 | 15.2 | 18.3 | 9.14 | 12.2 | 15.2 | 18.3 | 9.14 | 12.2 | 15.2 | 18.3 |
| 3.0 | 1.9 | A | A | A | A | A | A | A | B | A | A | A | A | A | A | A | B |
|  | 2.4 | A | A | A | A | A | A | B | B | A | A | A | A | A | A | B | B |
|  | 2.8 | A | A | A | A | A | A | B | B | A | A | A | A | A | B | B | B |
|  | 3.3 | A | A | A | B | A | B | B | B | A | A | A | B | A | B | B | B |
| 3.6 | 1.9 | A | A | A | B | A | B | B | B | A | A | A | B | B | B | B | B |
|  | 2.4 | A | A | B | B | B | B | B | B | A | A | B | B | B | B | B | B |
|  | 2.8 | A | B | B | B | B | B | B | B | A | B | B | B | B | B | B | B |
|  | 3.3 | A | B | B | B | B | B | B | B | A | B | B | B | B | B | B | B |
| 4.2 | 1.9 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |
|  | 2.4 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |
|  | 2.8 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |
|  | 3.3 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |
| 4.8 | 1.9 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |
|  | 2.4 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | C |
|  | 2.8 | B | B | B | B | B | B | B | C | B | B | B | B | B | B | C | C |
|  | 3.3 | B | B | B | B | B | B | C | C | B | B | B | B | B | B | C | C |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |

Legend — Stud Sizes

A = 38 mm x 89 mm

B = 38 mm x 140 mm

C = 38 mm x 184 mm or double 38 mm x 140 mm under the trusses, with an intermediate 38 mm x 140 mm stud at 600 mm.

Notes to Table 9.40.3.4.U.:

(1) Designs are based on load combinations of total roof load and wind load acting at the same time on a closed building.

(2) It is assumed that the double top plate is rigid enough to cause load sharing amongst all studs regardless of the spacing 400 mm or 600 mm.

(3) Solid bridging shall be used on all walls as follows:

≤ 3.0 m: 1 row at mid-height.

3.6 m - 4.2 m: 2 rows at third-points.

4.8 m: 3 rows at quarter-points.

(4) Wind bracing shall not impose additional bending forces onto the stud.

Table 9.40.3.4.V.

Stud Sizes for Farm Buildings of Low Human Occupancy (With Second Storey Loading)

Forming Part of Article 9.40.3.4.

| Sidewall Height, m | Total Roof Load, kPa | Spruce — Pine —Fir, No. 1 and No. 2 (Dressed Lumber) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Second Storey Plate, kN/m |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Wind Load: q10  0.30 kPa |  |  |  |  |  |  |  | Wind Load: q10  0.45 kPa |  |  |  |  |  |  |  |  |
|  |  | 400 mm o.c. |  |  |  | 600 mm o.c. |  |  |  | 400 mm o.c. |  |  |  | 600 mm o.c. |  |  |  |  |
|  |  | Building Width, m |  |  |  | Building Width, m |  |  |  | Building Width, m |  |  |  | Building Width, m |  |  |  |  |
|  |  | 9.14 | 12.2 | 15.2 | 18.3 | 9.14 | 12.2 | 15.2 | 18.3 | 9.14 | 12.2 | 15.2 | 18.3 | 9.14 | 12.2 | 15.2 | 18.3 |  |
| 3.0 | 1.9 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | 14.6 |
|  | 2.4 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |  |
|  | 2.8 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |  |
|  | 3.3 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |  |
| 3.6 | 1.9 | B | B | B | B | B | B | B | C | B | B | B | B | B | B | C | C | 14.6 |
|  | 2.4 | B | B | B | B | B | B | C | C | B | B | B | B | B | C | C | C |  |
|  | 2.8 | B | B | B | B | B | B | C | C | B | B | B | B | B | C | C | C |  |
|  | 3.3 | B | B | B | B | B | C | C | C | B | B | B | B | C | C | C | C |  |
| 3.0 | 1.9 | A | A | B | B | B | B | B | B | B | B | B | B | B | B | B | B | 7.3 |
|  | 2.4 | A | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |  |
|  | 2.8 | A | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |  |
|  | 3.3 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |  |
| 3.6 | 1.9 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | 7.3 |
|  | 2.4 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |  |
|  | 2.8 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |  |
|  | 3.3 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | C |  |
| 3.0 | 1.9 | A | A | A | A | A | B | B | B | A | A | A | A | B | B | B | B | 3.6 |
|  | 2.4 | A | A | A | B | B | B | B | B | A | A | A | A | B | B | B | B |  |
|  | 2.8 | A | A | B | B | B | B | B | B | A | A | B | B | B | B | B | B |  |
|  | 3.3 | A | A | B | B | B | B | B | B | A | B | B | B | B | B | B | B |  |
| 3.6 | 1.9 | A | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | 3.6 |
|  | 2.4 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |  |
|  | 2.8 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |  |
|  | 3.3 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B |  |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 |

Legend — Stud Sizes

A = 38 mm x 89 mm

B = 38 mm x 140 mm

C = 38 mm x 184 mm or double 38 mm x 140 mm

Notes to Table 9.40.3.4.V.:

(1) Design is based on load combinations of total roof load, wind load and stored product acting at the same time on a closed building.

(2) All notes following Table 9.40.3.4.U. apply, with the following conditions/exceptions:

14.6 kN/m loading: Full 4.8 m sidewall hay/straw storage space above.  It is supported by beams spaced at 3.6 m o.c.  The outside plate carries a 1.8 m floor width.  If the loading is greater, refer to a qualified person for design.

7.3 kN/m loading: Full 2.4 m sidewall hay/straw storage space above or a gambrel roof structure >9.14 m in total width.  Floor support beams as above.

3.6 kN/m loading: Small gambrel roof structure or storage space for light storage.  Floor support beams as above.

Table 9.40.3.4.W.

Stud Sizes for Farm Buildings of Low Human Occupancy (Single Storey)

Forming Part of Article 9.40.3.4.

| Sidewall Height, m | Total Roof Load, kPa | Ungraded Lumber, Full-Dimensioned |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Wind Load: q10  0.30 kPa |  |  |  |  |  |  |  |  |  | Wind Load: q10  0.45 kPa |  |  |  |  |  |  |
|  |  | 400 mm o.c. |  |  |  | 600 mm o.c. |  |  |  | 400 mm o.c. |  |  |  |  | 600 mm o.c. |  |  |  |
|  |  | Building Width, m |  |  |  | Building Width, m |  |  |  | Building Width, m |  |  |  |  | Building Width, m |  |  |  |
|  |  | 9.14 | 12.2 | 15.2 | 18.3 | 9.14 | 12.2 | 15.2 | 18.3 | 9.14 | 12.2 |  | 15.2 | 18.3 | 9.14 | 12.2 | 15.2 | 18.3 |
| 3.0 | 1.9 | A | A | A | A | A | A | A | B | A | A |  | A | A | A | A | B | B |
|  | 2.4 | A | A | A | A | A | A | B | B | A | A |  | A | A | A | B | B | B |
|  | 2.8 | A | A | A | A | A | B | B | B | A | A |  | A | B | B | B | B | B |
|  | 3.3 | A | A | A | B | A | B | B | B | A | A |  | A | B | A | B | B | B |
| 3.6 | 1.9 | A | A | A | B | A | B | B | B | A | A |  | A | B | B | B | B | B |
|  | 2.4 | A | A | B | B | B | B | B | B | A | A |  | B | B | B | B | B | B |
|  | 2.8 | A | B | B | B | B | B | B | B | A | B |  | B | B | B | B | B | B |
|  | 3.3 | A | B | B | B | B | B | B | B | B | B |  | B | B | B | B | B | C |
| 4.2 | 1.9 | B | B | B | B | B | B | B | B | B | B |  | B | B | B | B | B | B |
|  | 2.4 | B | B | B | B | B | B | B | B | B | B |  | B | B | B | B | B | C |
|  | 2.8 | B | B | B | B | B | B | B | C | B | B |  | B | B | B | B | C | C |
|  | 3.3 | B | B | B | B | B | B | C | C | B | B |  | B | B | B | C | C | C |
| 4.8 | 1.9 | B | B | B | B | B | B | B | C | B | B |  | B | B | B | B | C | C |
|  | 2.4 | B | B | B | B | B | B | C | C | B | B |  | B | B | B | C | C | C |
|  | 2.8 | B | B | B | B | B | B | C | C | B | B |  | B | C | C | C | C | C |
|  | 3.3 | B | B | B | B | B | C | C | C | B | B |  | B | C | C | C | C | C |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | 13 | 14 | 15 | 16 | 17 | 18 |

Legend — Stud Sizes

A = 50.8 mm x 101.6 mm

B = 50.8 mm x 152.4 mm

C = 50.8 mm x 203.2 mm or double 50.8 mm x 152.4 mm under the trusses, with an intermediate 50.8 mm x 152.4 mm stud at 600 mm

Notes to Table 9.40.3.4.W.:

(1) Designs are based on load combinations of total roof load and wind load acting at the same time on a closed building.

(2) It is assumed that the double top plate is rigid enough to cause load sharing amongst all studs regardless of the spacing 400 mm or 600 mm.

(3) Solid bridging shall be used on all walls as follows:

| ≤ 3.0 m: | 1 row at mid-height. |
| --- | --- |
| 3.6 m to 4.2 m: | 2 rows at third-points. |
| 4.8 m: | 3 rows at quarter-points. |

(4) Wind bracing shall not impose additional bending forces onto the stud.

Section 9.41. Additional Requirements for Change of Use

9.41.1. Scope

9.41.1.1.  Application

(1)  This Section applies where proposed construction in respect of an existing building will result in the following changes of use of all or part of the building

(a)	a change of the major occupancy of all or part of a building that is designated with a “Y” in Table 2.4.1.1.,

(b)	a suite of a Group C major occupancy is converted into more than one suite of Group C major occupancy,

(c)	a farm building or part of a farm building is changed to a major occupancy, or

(d)	the use of a building or part of a building is changed and the previous major occupancy of the building or part of the building cannot be determined.

(2)  For the purposes of this Section and Sentences 11.4.2.1.(1) and 11.4.2.5.(4), the changes of use set out in Clauses (1)(b) to (d) shall also be deemed to constitute a change in major occupancy.

(3)  The requirements of this Section are in addition to the requirements of other Parts of the Code as they apply to the proposed construction.

9.41.2.  Additional Construction

9.41.2.1.  Change of Use and Compensating Construction

(1)  Where proposed construction will result in a change of use described in Clauses 9.41.1.1.(1)(a) to (d), additional construction shall be required in order that the building or part of a building subject to the change of use conforms to the requirements of Section 9.5. and 9.7., Subsection 9.10.16., Sections 9.31. and 9.32., and Subsections 9.34.1., 9.34.2. and 9.34.3. as they apply to the new major occupancy that the building or part of a building is to support.

(2)  For the purposes of this Article, existing buildings shall be classified as to their construction and occupancy as provided for in Sentence 11.2.1.1.(1).

9.41.2.2.  Performance Level Evaluation and Compensating Construction

(1)  The performance level of a building after construction shall not be less than the performance level of the building prior to construction.

(2)  For the purposes of Sentence (1), reduction of performance level shall be determined in accordance with Articles 11.4.2.1, 11.4.2.3. and 11.4.2.5.

(3)  Where the proposed construction would reduce the performance level of an existing building, compensating construction shall be required in conformance with Articles 11.4.3.1., 11.4.3.2, 11.4.3.4 and 11.4.3.6.

(4)  Section 11.5. applies in respect of the requirements of Sentences 11.4.3.4.(1), (3) and (4).

Table A-1

Maximum Spans for Floor Joists — General Cases(1)

Forming Part of Sentence 9.23.4.2.(1)

| Commercial Designation | Grade | Joist Size, mm | Maximum Span, m |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | With Strapping |  |  | With Bridging |  |  | With Strapping and Bridging |  |  |
|  |  |  | Joist Spacing, mm |  |  | Joist Spacing, mm |  |  | Joist Spacing, mm |  |  |
|  |  |  | 300 | 400 | 600 | 300 | 400 | 600 | 300 | 400 | 600 |
| Douglas Fir – Larch (includes Douglas Fir and Western Larch) | Select Structural | 38 x 89 | 2.13 | 1.97 | 1.73 | 2.19 | 1.99 | 1.73 | 2.19 | 1.99 | 1.73 |
|  |  | 38 x 140 | 3.23 | 3.07 | 2.73 | 3.44 | 3.12 | 2.73 | 3.44 | 3.12 | 2.73 |
|  |  | 38 x 184 | 3.88 | 3.69 | 3.51 | 4.18 | 3.92 | 3.59 | 4.37 | 4.07 | 3.59 |
|  |  | 38 x 235 | 4.57 | 4.34 | 4.13 | 4.86 | 4.57 | 4.29 | 5.05 | 4.70 | 4.39 |
|  |  | 38 x 286 | 5.21 | 4.95 | 4.71 | 5.49 | 5.16 | 4.85 | 5.66 | 5.28 | 4.92 |
|  | No. 1 and No. 2 | 38 x 89 | 2.00 | 1.85 | 1.66 | 2.09 | 1.90 | 1.66 | 2.09 | 1.90 | 1.66 |
|  |  | 38 x 140 | 3.09 | 2.91 | 2.62 | 3.29 | 2.99 | 2.62 | 3.29 | 2.99 | 2.62 |
|  |  | 38 x 184 | 3.71 | 3.53 | 3.36 | 4.00 | 3.76 | 3.44 | 4.19 | 3.90 | 3.44 |
|  |  | 38 x 235 | 4.38 | 4.16 | 3.96 | 4.66 | 4.38 | 4.11 | 4.84 | 4.51 | 4.20 |
|  |  | 38 x 286 | 4.99 | 4.75 | 4.52 | 5.26 | 4.94 | 4.65 | 5.43 | 5.06 | 4.72 |
|  | No. 3 | 38 x 89 | 1.90 | 1.69 | 1.38 | 1.95 | 1.69 | 1.38 | 1.95 | 1.69 | 1.38 |
|  |  | 38 x 140 | 2.78 | 2.41 | 1.97 | 2.78 | 2.41 | 1.97 | 2.78 | 2.41 | 1.97 |
|  |  | 38 x 184 | 3.38 | 2.93 | 2.39 | 3.38 | 2.93 | 2.39 | 3.38 | 2.93 | 2.39 |
|  |  | 38 x 235 | 4.14 | 3.58 | 3.93 | 4.14 | 3.58 | 2.93 | 4.14 | 3.58 | 2.93 |
|  |  | 38 x 286 | 4.80 | 4.16 | 3.39 | 4.80 | 4.16 | 3.39 | 4.80 | 4.16 | 3.39 |
|  | Construction | 38 x 89 | 1.90 | 1.77 | 1.61 | 2.03 | 1.84 | 1.61 | 2.03 | 1.84 | 1.61 |
|  | Standard | 38 x 89 | 1.81 | 1.63 | 1.33 | 1.88 | 1.63 | 1.33 | 1.88 | 1.63 | 1.33 |
| Hem – Fir (includes Western Hemlock and Amabilis Fir) | Select Structural | 38 x 89 | 2.08 | 1.93 | 1.71 | 2.16 | 1.96 | 1.71 | 2.16 | 1.96 | 1.71 |
|  |  | 38 x 140 | 3.18 | 3.03 | 2.69 | 3.39 | 3.08 | 2.69 | 3.39 | 3.08 | 2.69 |
|  |  | 38 x 184 | 3.82 | 3.64 | 3.46 | 4.12 | 3.87 | 3.54 | 4.31 | 4.02 | 3.54 |
|  |  | 38 x 235 | 4.50 | 4.28 | 4.08 | 4.80 | 4.51 | 4.23 | 4.98 | 4.64 | 4.33 |
|  |  | 38 x 286 | 5.14 | 4.89 | 4.65 | 5.42 | 5.09 | 4.78 | 5.59 | 5.21 | 4.86 |
|  | No. 1 and No. 2 | 38 x 89 | 2.00 | 1.85 | 1.66 | 2.09 | 1.90 | 1.66 | 2.09 | 1.90 | 1.66 |
|  |  | 38 x 140 | 3.09 | 2.91 | 2.62 | 3.29 | 2.99 | 2.62 | 3.29 | 2.99 | 2.62 |
|  |  | 38 x 184 | 3.71 | 3.53 | 3.36 | 4.00 | 3.76 | 3.44 | 4.19 | 3.90 | 3.44 |
|  |  | 38 x 235 | 4.38 | 4.16 | 3.96 | 4.66 | 4.38 | 4.11 | 4.84 | 4.51 | 4.20 |
|  |  | 38 x 286 | 4.99 | 4.75 | 4.52 | 5.26 | 4.94 | 4.65 | 5.43 | 5.06 | 4.72 |
|  | No. 3 | 38 x 89 | 1.90 | 1.77 | 1.61 | 2.03 | 1.84 | 1.61 | 2.03 | 1.84 | 1.61 |
|  |  | 38 x 140 | 2.99 | 2.78 | 2.43 | 3.19 | 2.90 | 2.43 | 3.19 | 2.90 | 2.43 |
|  |  | 38 x 184 | 3.60 | 3.42 | 2.95 | 3.88 | 3.61 | 2.95 | 4.06 | 3.61 | 2.95 |
|  |  | 38 x 235 | 4.24 | 4.03 | 3.61 | 4.51 | 4.24 | 3.61 | 4.68 | 4.37 | 3.61 |
|  |  | 38 x 286 | 4.84 | 4.60 | 4.19 | 5.10 | 4.79 | 4.19 | 5.26 | 4.90 | 4.19 |
|  | Construction | 38 x 89 | 1.90 | 1.77 | 1.61 | 2.03 | 1.84 | 1.61 | 2.03 | 1.84 | 1.61 |
|  | Standard | 38 x 89 | 1.81 | 1.68 | 1.39 | 1.96 | 1.71 | 1.39 | 1.96 | 1.71 | 1.39 |
| Spruce –Pine – Fir (includes Spruce (all species except Coast Sitka Spruce), Jack Pine, Lodgepole Pine, Balsam Fir and Alpine Fir) | Select Structural | 38 x 89 | 1.95 | 1.81 | 1.64 | 2.06 | 1.87 | 1.64 | 2.06 | 1.87 | 1.64 |
|  |  | 38 x 140 | 3.05 | 2.85 | 2.57 | 3.24 | 2.95 | 2.57 | 3.24 | 2.95 | 2.57 |
|  |  | 38 x 184 | 3.66 | 3.48 | 3.31 | 3.94 | 3.70 | 3.38 | 4.12 | 3.84 | 3.38 |
|  |  | 38 x 235 | 4.31 | 4.10 | 3.90 | 4.59 | 4.31 | 4.05 | 4.76 | 4.44 | 4.14 |
|  |  | 38 x 286 | 4.91 | 4.67 | 4.45 | 5.18 | 4.87 | 4.57 | 5.34 | 4.98 | 4.64 |
|  | No. 1 and No. 2 | 38 x 89 | 1.86 | 1.72 | 1.58 | 1.99 | 1.81 | 1.58 | 1.99 | 1.81 | 1.58 |
|  |  | 38 x 140 | 2.92 | 2.71 | 2.49 | 3.14 | 2.85 | 2.49 | 3.14 | 2.85 | 2.49 |
|  |  | 38 x 184 | 3.54 | 3.36 | 3.20 | 3.81 | 3.58 | 3.27 | 3.99 | 3.72 | 3.27 |
|  |  | 38 x 235 | 4.17 | 3.96 | 3.77 | 4.44 | 4.17 | 3.92 | 4.60 | 4.29 | 4.00 |
|  |  | 38 x 286 | 4.75 | 4.52 | 4.30 | 5.01 | 4.71 | 4.42 | 5.17 | 4.82 | 4.49 |
|  | No. 3 | 38 x 89 | 1.81 | 1.68 | 1.55 | 1.96 | 1.78 | 1.55 | 1.96 | 1.78 | 1.55 |
|  |  | 38 x 140 | 2.84 | 2.64 | 2.43 | 3.08 | 2.80 | 2.43 | 3.08 | 2.80 | 2.43 |
|  |  | 38 x 184 | 3.47 | 3.30 | 2.95 | 3.74 | 3.52 | 2.95 | 3.92 | 3.61 | 2.95 |
|  |  | 38 x 235 | 4.09 | 3.89 | 3.61 | 4.36 | 4.09 | 3.61 | 4.52 | 4.22 | 3.61 |
|  |  | 38 x 286 | 4.67 | 4.44 | 4.19 | 4.92 | 4.62 | 4.19 | 5.08 | 4.73 | 4.19 |
|  | Construction | 38 x 89 | 1.81 | 1.68 | 1.55 | 1.96 | 1.78 | 1.55 | 1.96 | 1.78 | 1.55 |
|  | Standard | 38 x 89 | 1.70 | 1.58 | 1.44 | 1.88 | 1.71 | 1.44 | 1.88 | 1.71 | 1.44 |
| Northern Species (includes any Canadian Species covered by the NLGA Standard Grading Rules) | Select Structural | 38 x 89 | 1.65 | 1.53 | 1.42 | 1.84 | 1.68 | 1.46 | 1.84 | 1.68 | 1.46 |
|  |  | 38 x 140 | 2.59 | 2.41 | 2.24 | 2.90 | 2.63 | 2.30 | 2.90 | 2.63 | 2.30 |
|  |  | 38 x 184 | 3.27 | 3.11 | 2.94 | 3.52 | 3.31 | 3.03 | 3.69 | 3.44 | 3.03 |
|  |  | 38 x 235 | 3.85 | 3.66 | 3.48 | 4.10 | 3.85 | 3.62 | 4.26 | 3.97 | 3.70 |
|  |  | 38 x 286 | 4.39 | 4.18 | 3.97 | 4.63 | 4.35 | 4.09 | 4.78 | 4.45 | 4.15 |
|  | No. 1 and No. 2 | 38 x 89 | 1.59 | 1.48 | 1.37 | 1.80 | 1.64 | 1.43 | 1.80 | 1.64 | 1.43 |
|  |  | 38 x 140 | 2.51 | 2.33 | 2.16 | 2.83 | 2.57 | 2.25 | 2.83 | 2.57 | 2.25 |
|  |  | 38 x 184 | 3.19 | 3.04 | 2.84 | 3.44 | 3.23 | 2.96 | 3.60 | 3.36 | 2.96 |
|  |  | 38 x 235 | 3.76 | 3.58 | 3.41 | 4.01 | 3.77 | 3.54 | 4.16 | 3.88 | 3.62 |
|  |  | 38 x 286 | 4.29 | 4.08 | 3.88 | 4.53 | 4.25 | 4.00 | 4.67 | 4.35 | 4.06 |
|  | No. 3 | 38 x 89 | 1.54 | 1.43 | 1.32 | 1.74 | 1.57 | 1.36 | 1.76 | 1.60 | 1.36 |
|  |  | 38 x 140 | 2.42 | 2.24 | 1.94 | 2.74 | 2.38 | 1.94 | 2.75 | 2.38 | 1.94 |
|  |  | 38 x 184 | 3.12 | 2.90 | 2.37 | 3.35 | 2.90 | 2.37 | 3.35 | 2.90 | 2.37 |
|  |  | 38 x 235 | 3.67 | 3.49 | 2.89 | 3.91 | 3.54 | 2.89 | 4.06 | 3.54 | 2.89 |
|  |  | 38 x 286 | 4.19 | 3.98 | 3.36 | 4.42 | 4.11 | 3.36 | 4.55 | 4.11 | 3.36 |
|  | Construction | 38 x 89 | 1.54 | 1.43 | 1.32 | 1.74 | 1.57 | 1.40 | 1.76 | 1.60 | 1.40 |
|  | Standard | 38 x 89 | 1.48 | 1.37 | 1.15 | 1.63 | 1.41 | 1.15 | 1.63 | 1.41 | 1.15 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |

Note to Table A-1:

(1) Spans apply only where the floors serve residential areas as described in Table 4.1.6.3., or the uniformly distributed live load on the floor does not exceed that specified for residential areas as described in Table 4.1.6.3.

Table A-2

Maximum Spans for Floor Joists — Special Cases(1)

Forming Part of Sentence 9.23.4.2.(1) and 9.23.4.4.(2)

| Commercial Designation | Grade | Joist Size, mm | Maximum Span, m |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Joists with Ceilings Attached to Wood Furring |  |  |  |  |  | Joists with Concrete Topping |  |  |
|  |  |  | Without Bridging |  |  | With Bridging |  |  | With or Without Bridging(2) |  |  |
|  |  |  | Joist Spacing, mm |  |  | Joist Spacing, mm |  |  | Joist Spacing, mm |  |  |
|  |  |  | 300 | 400 | 600 | 300 | 400 | 600 | 300 | 400 | 600 |
| Douglas Fir – Larch (includes Douglas Fir and Western Larch) | Select Structural | 38 x 89 | 2.19 | 1.99 | 1.73 | 2.19 | 1.99 | 1.73 | 2.19 | 1.99 | 1.73 |
|  |  | 38 x 140 | 3.44 | 3.12 | 2.73 | 3.44 | 3.12 | 2.73 | 3.44 | 3.12 | 2.73 |
|  |  | 38 x 184 | 4.24 | 3.99 | 3.59 | 4.52 | 4.11 | 3.59 | 4.52 | 4.11 | 3.59 |
|  |  | 38 x 235 | 4.98 | 4.69 | 4.29 | 5.47 | 5.20 | 4.58 | 5.77 | 5.24 | 4.58 |
|  |  | 38 x 286 | 5.67 | 5.34 | 4.88 | 6.19 | 5.89 | 5.54 | 6.83 | 6.37 | 5.58 |
|  | No. 1 and No. 2 | 38 x 89 | 2.09 | 1.90 | 1.66 | 2.09 | 1.90 | 1.66 | 2.09 | 1.90 | 1.66 |
|  |  | 38 x 140 | 3.29 | 2.99 | 2.62 | 3.29 | 2.99 | 2.62 | 3.29 | 2.99 | 2.55 |
|  |  | 38 x 184 | 4.06 | 3.83 | 3.44 | 4.33 | 3.93 | 3.44 | 4.33 | 3.81 | 3.11 |
|  |  | 38 x 235 | 4.78 | 4.50 | 4.11 | 5.24 | 4.98 | 4.31 | 5.37 | 4.65 | 3.80 |
|  |  | 38 x 286 | 5.44 | 5.12 | 4.68 | 5.93 | 5.64 | 5.00 | 6.24 | 5.40 | 4.41 |
|  | No. 3 | 38 x 89 | 1.95 | 1.69 | 1.38 | 1.95 | 1.69 | 1.38 | 1.72 | 1.49 | 1.21 |
|  |  | 38 x 140 | 2.78 | 2.41 | 1.97 | 2.78 | 2.41 | 1.97 | 2.45 | 2.12 | 1.73 |
|  |  | 38 x 184 | 3.38 | 2.93 | 2.39 | 3.38 | 2.93 | 2.39 | 2.98 | 2.58 | 2.11 |
|  |  | 38 x 235 | 4.14 | 3.58 | 2.93 | 4.14 | 3.58 | 2.93 | 3.65 | 3.16 | 2.58 |
|  |  | 38 x 286 | 4.80 | 4.16 | 3.39 | 4.80 | 4.16 | 3.39 | 4.23 | 3.66 | 2.99 |
|  | Construction | 38 x 89 | 2.03 | 1.84 | 1.61 | 2.03 | 1.84 | 1.61 | 2.03 | 1.84 | 1.61 |
|  | Standard | 38 x 89 | 1.88 | 1.63 | 1.33 | 1.88 | 1.63 | 1.33 | 1.66 | 1.44 | 1.17 |
| Hem – Fir (includes Western Hemlock and Amabilis Fir) | Select Structural | 38 x 89 | 2.16 | 1.96 | 1.71 | 2.16 | 1.96 | 1.71 | 2.16 | 1.96 | 1.71 |
|  |  | 38 x 140 | 3.39 | 3.08 | 2.69 | 3.39 | 3.08 | 2.69 | 3.39 | 3.08 | 2.69 |
|  |  | 38 x 184 | 4.18 | 3.94 | 3.54 | 4.46 | 4.05 | 3.54 | 4.46 | 4.05 | 3.54 |
|  |  | 38 x 235 | 4.92 | 4.63 | 4.23 | 5.39 | 5.13 | 4.52 | 5.69 | 5.17 | 4.52 |
|  |  | 38 x 286 | 5.60 | 5.27 | 4.82 | 6.10 | 5.81 | 5.47 | 6.74 | 6.28 | 5.50 |
|  | No .1 and No. 2 | 38 x 89 | 2.09 | 1.90 | 1.66 | 2.09 | 1.90 | 1.66 | 2.09 | 1.90 | 1.66 |
|  |  | 38 x 140 | 3.29 | 2.99 | 2.62 | 3.29 | 2.99 | 2.62 | 3.29 | 2.99 | 2.62 |
|  |  | 38 x 184 | 4.06 | 3.83 | 3.44 | 4.33 | 3.93 | 3.44 | 4.33 | 3.93 | 3.26 |
|  |  | 38 x 235 | 4.78 | 4.50 | 4.11 | 5.24 | 4.98 | 4.39 | 5.53 | 4.88 | 3.99 |
|  |  | 38 x 286 | 5.44 | 5.12 | 4.68 | 5.93 | 5.64 | 5.25 | 6.54 | 5.66 | 4.63 |
|  | No. 3 | 38 x 89 | 2.03 | 1.84 | 1.61 | 2.03 | 1.84 | 1.61 | 2.03 | 1.83 | 1.50 |
|  |  | 38 x 140 | 3.19 | 2.90 | 2.43 | 3.19 | 2.90 | 2.43 | 3.02 | 2.62 | 2.14 |
|  |  | 38 x 184 | 3.94 | 3.61 | 2.95 | 4.17 | 3.61 | 2.95 | 3.68 | 3.18 | 2.60 |
|  |  | 38 x 235 | 4.63 | 4.36 | 3.61 | 5.08 | 4.42 | 3.61 | 4.50 | 3.89 | 3.18 |
|  |  | 38 x 286 | 5.27 | 4.96 | 4.19 | 5.74 | 5.13 | 4.19 | 5.22 | 4.52 | 3.69 |
|  | Construction | 38 x 89 | 2.03 | 1.84 | 1.61 | 2.03 | 1.84 | 1.61 | 2.03 | 1.84 | 1.61 |
|  | Standard | 38 x 89 | 1.96 | 1.71 | 1.39 | 1.96 | 1.71 | 1.39 | 1.74 | 1.50 | 1.23 |
| Spruce – Pine – Fir (includes Spruce (all species except Coast Sitka Spruce), Jack Pine, Lodgepole Pine, Balsam Fir and Alpine Fir) | Select Structural | 38 x 89 | 2.06 | 1.87 | 1.64 | 2.06 | 1.87 | 1.64 | 2.06 | 1.87 | 1.64 |
|  |  | 38 x 140 | 3.24 | 2.95 | 2.57 | 3.24 | 2.95 | 2.57 | 3.24 | 2.95 | 2.57 |
|  |  | 38 x 184 | 4.00 | 3.77 | 3.38 | 4.26 | 3.87 | 3.38 | 4.26 | 3.87 | 3.38 |
|  |  | 38 x 235 | 4 70 | 4.43 | 4.05 | 5.16 | 4.91 | 4.32 | 5.45 | 4.95 | 4.32 |
|  |  | 38 x 286 | 5.35 | 5.04 | 4.61 | 5.84 | 5.55 | 5.23 | 6.45 | 6.01 | 5.26 |
|  | No. 1 and No. 2 | 38 x 89 | 1.99 | 1.81 | 1.58 | 1.99 | 1.81 | 1.58 | 1.99 | 1.81 | 1.58 |
|  |  | 38 x 140 | 3.14 | 2.85 | 2.49 | 3.14 | 2.85 | 2.49 | 3.14 | 2.85 | 2.49 |
|  |  | 38 x 184 | 3.87 | 3.64 | 3.27 | 4.12 | 3.75 | 3.27 | 4.12 | 3.75 | 3.27 |
|  |  | 38 x 235 | 4.55 | 4.28 | 3.91 | 4.99 | 4.75 | 4.18 | 5.27 | 4.79 | 4.13 |
|  |  | 38 x 286 | 5.18 | 4.88 | 4.46 | 5.65 | 5.37 | 5.06 | 6.23 | 5.81 | 4.79 |
|  | No. 3 | 38 x 89 | 1.96 | 1.78 | 1.55 | 1.96 | 1.78 | 1.55 | 1.96 | 1.78 | 1.50 |
|  |  | 38 x 140 | 3.08 | 2.80 | 2.43 | 3.08 | 2.80 | 2.43 | 3.02 | 2.62 | 2.14 |
|  |  | 38 x 184 | 3.80 | 3.58 | 2.95 | 4.05 | 3.61 | 2.95 | 3.68 | 3.18 | 2.60 |
|  |  | 38 x 235 | 4.47 | 4.21 | 3.61 | 4.90 | 4.42 | 3.61 | 4.50 | 3.89 | 3.18 |
|  |  | 38 x 286 | 5.09 | 4.79 | 4.19 | 5.55 | 5.13 | 4.19 | 5.22 | 4.52 | 3.69 |
|  | Construction | 38 x 89 | 1.96 | 1.78 | 1.55 | 1.96 | 1.78 | 1.55 | 1.96 | 1.78 | 1.55 |
|  | Standard | 38 x 89 | 1.88 | 1.71 | 1.44 | 1.88 | 1.71 | 1.44 | 1.80 | 1.56 | 1.27 |
| Northern Species (includes any Canadian Species covered by the NLGA Standard Grading Rules) | Select Structural | 38 x 89 | 1.84 | 1.68 | 1.46 | 1.84 | 1.68 | 1.46 | 1.84 | 1.68 | 1.46 |
|  |  | 38 x 140 | 2.90 | 2.63 | 2.30 | 2.90 | 2.63 | 2.30 | 2.90 | 2.63 | 2.30 |
|  |  | 38 x 184 | 3.58 | 3.37 | 3.03 | 3.81 | 3.46 | 3.03 | 3.81 | 3.46 | 3.03 |
|  |  | 38 x 235 | 4.20 | 3.96 | 3.62 | 4.61 | 4.39 | 3.86 | 4.87 | 4.42 | 3.86 |
|  |  | 38 x 286 | 4.79 | 4.51 | 4.12 | 5.22 | 4.96 | 4.68 | 5.76 | 5.37 | 4.54 |
|  | No. 1 and No. 2 | 38 x 89 | 1.80 | 1.64 | 1.43 | 1.80 | 1.64 | 1.43 | 1.80 | 1.64 | 1.43 |
|  |  | 38 x 140 | 2.83 | 2.57 | 2.25 | 2.83 | 2.57 | 2.25 | 2.83 | 2.57 | 2.23 |
|  |  | 38 x 184 | 3.50 | 3.29 | 2.96 | 3.72 | 3.38 | 2.96 | 3.72 | 3.32 | 2.71 |
|  |  | 38 x 235 | 4.11 | 3.87 | 3.54 | 4.51 | 4.29 | 3.76 | 4.69 | 4.06 | 3.31 |
|  |  | 38 x 286 | 4.68 | 4.40 | 4.03 | 5.10 | 4.85 | 4.36 | 5.44 | 4.71 | 3.84 |
|  | No. 3 | 38 x 89 | 1.76 | 1.60 | 1.36 | 1.76 | 1.60 | 1.36 | 1.70 | 1.47 | 1.20 |
|  |  | 38 x 140 | 2.75 | 2.38 | 1.94 | 2.75 | 2.38 | 1.94 | 2.42 | 2.10 | 1.71 |
|  |  | 38 x 184 | 3.35 | 2.90 | 2.37 | 3.35 | 2.90 | 2.37 | 2.95 | 2.55 | 2.08 |
|  |  | 38 x 235 | 4.01 | 3.54 | 2.89 | 4.09 | 3.54 | 2.89 | 3.61 | 3.12 | 2.55 |
|  |  | 38 x 286 | 4.56 | 4.11 | 3.36 | 4.75 | 4.11 | 3.36 | 4.18 | 3.62 | 2.96 |
|  | Construction | 38 x 89 | 1.76 | 1.60 | 1.40 | 1.76 | 1.60 | 1.40 | 1.76 | 1.60 | 1.37 |
|  | Standard | 38 x 89 | 1.63 | 1.41 | 1.15 | 1.63 | 1.41 | 1.15 | 1.44 | 1.25 | 1.02 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |

Notes to Table A-2:

(1) Spans apply only where the floors serve residential areas as described in Table 4.1.6.3., or the uniformly distributed live load on the floor does not exceed that specified for residential areas as described in Table 4.1.6.3.

(2) No bridging is assumed for spans for floor joists with concrete topping.

Table A-3

Maximum Spans for Ceiling Joists — Attic not Accessible by a Stairway

Forming Part of Sentence 9.23.4.2.(1)

| Commercial Designation | Grade | Joist Size, mm | Maximum Span, m |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Joist Spacing, mm |  |  |
|  |  |  | 300 | 400 | 600 |
| Douglas Fir – Larch (includes Douglas Fir and Western Larch) | Select Structural | 38 x 89 | 3.41 | 3.10 | 2.71 |
|  |  | 38 x 140 | 5.37 | 4.88 | 4.26 |
|  |  | 38 x 184 | 7.05 | 6.40 | 5.59 |
|  |  | 38 x 235 | 9.01 | 8.18 | 7.15 |
|  |  | 38 x 286 | 10.96 | 9.96 | 8.70 |
|  | No. 1 and No. 2 | 38 x 89 | 3.27 | 2.97 | 2.59 |
|  |  | 38 x 140 | 5.14 | 4.67 | 4.08 |
|  |  | 38 x 184 | 6.76 | 6.14 | 5.36 |
|  |  | 38 x 235 | 8.63 | 7.84 | 6.85 |
|  |  | 38 x 286 | 10.50 | 9.54 | 8.34 |
|  | No. 3 | 38 x 89 | 3.17 | 2.88 | 2.42 |
|  |  | 38 x 140 | 4.89 | 4.23 | 3.46 |
|  |  | 38 x 184 | 5.95 | 5.15 | 4.20 |
|  |  | 38 x 235 | 7.27 | 6.30 | 5.14 |
|  |  | 38 x 286 | 8.44 | 7.31 | 5.97 |
|  | Construction | 38 x 89 | 3.17 | 2.88 | 2.51 |
|  | Standard | 38 x 89 | 3.06 | 2.78 | 2.34 |
| Hem – Fir (includes Western Hemlock and Amabilis Fir) | Select Structural | 38 x 89 | 3.36 | 3.06 | 2.67 |
|  |  | 38 x 140 | 5.29 | 4.81 | 4.20 |
|  |  | 38 x 184 | 6.96 | 6.32 | 5.52 |
|  |  | 38 x 235 | 8.88 | 8.07 | 7.05 |
|  |  | 38 x 286 | 10.81 | 9.82 | 8.58 |
|  | No. 1 and No. 2 | 38 x 89 | 3.27 | 2.97 | 2.59 |
|  |  | 38 x 140 | 5.14 | 4.67 | 4.08 |
|  |  | 38 x 184 | 6.76 | 6.14 | 5.36 |
|  |  | 38 x 235 | 8.63 | 7.84 | 6.85 |
|  |  | 38 x 286 | 10.50 | 9.54 | 8.34 |
|  | No. 3 | 38 x 89 | 3.17 | 2.88 | 2.51 |
|  |  | 38 x 140 | 4.98 | 4.53 | 3.95 |
|  |  | 38 x 184 | 6.55 | 5.95 | 5.19 |
|  |  | 38 x 235 | 8.36 | 7.60 | 6.34 |
|  |  | 38 x 286 | 10.18 | 9.01 | 7.36 |
|  | Construction | 38 x 89 | 3.17 | 2.88 | 2.50 |
|  | Standard | 38 x 89 | 3.06 | 2.78 | 2.43 |
| Spruce – Pine – Fir (includes Spruce (all species except Coast Sitka Spruce), Jack Pine, Lodgepole Pine, Balsam Fir and Alpine Fir) | Select Structural | 38 x 89 | 3.22 | 2.92 | 2.55 |
|  |  | 38 x 140 | 5.06 | 4.60 | 4.02 |
|  |  | 38 x 184 | 6.65 | 6.05 | 5.28 |
|  |  | 38 x 235 | 8.50 | 7.72 | 6.74 |
|  |  | 38 x 286 | 10.34 | 9.40 | 8.21 |
|  | No. 1 and No. 2 | 38 x 89 | 3.11 | 2.83 | 2.47 |
|  |  | 38 x 140 | 4.90 | 4.45 | 3.89 |
|  |  | 38 x 184 | 6.44 | 5.85 | 5.11 |
|  |  | 38 x 235 | 8.22 | 7.47 | 6.52 |
|  |  | 38 x 286 | 10.00 | 9.09 | 7.94 |
|  | No. 3 | 38 x 89 | 3.06 | 2.78 | 2.43 |
|  |  | 38 x 140 | 4.81 | 4.37 | 3.82 |
|  |  | 38 x 184 | 6.32 | 5.74 | 5.02 |
|  |  | 38 x 235 | 8.07 | 7.33 | 6.34 |
|  |  | 38 x 286 | 9.82 | 8.93 | 7.36 |
|  | Construction | 38 x 89 | 3.06 | 2.78 | 2.43 |
|  | Standard | 38 x 89 | 2.94 | 2.67 | 2.33 |
| Northern Species (includes any Canadian Species covered by the NLGA Standard Grading Rules) | Select Structural | 38 x 89 | 2.88 | 2.61 | 2.28 |
|  |  | 38 x 140 | 4.53 | 4.11 | 3.59 |
|  |  | 38 x 184 | 5.95 | 5.40 | 4.72 |
|  |  | 38 x 235 | 7.60 | 6.90 | 6.03 |
|  |  | 38 x 286 | 9.25 | 8.40 | 7.34 |
|  | No. 1 and No. 2 | 38 x 89 | 2.81 | 2.55 | 2.23 |
|  |  | 38 x 140 | 4.42 | 4.02 | 3.51 |
|  |  | 38 x 184 | 5.81 | 5.28 | 4.61 |
|  |  | 38 x 235 | 7.42 | 6.74 | 5.89 |
|  |  | 38 x 286 | 9.03 | 8.21 | 7.17 |
|  | No. 3 | 38 x 89 | 2.74 | 2.49 | 2.18 |
|  |  | 38 x 140 | 4.31 | 3.92 | 3.42 |
|  |  | 38 x 184 | 5.67 | 5.09 | 4.16 |
|  |  | 38 x 235 | 7.19 | 6.23 | 5.08 |
|  |  | 38 x 286 | 8.34 | 7.23 | 5.90 |
|  | Construction | 38 x 89 | 2.74 | 2.49 | 2.18 |
|  | Standard | 38 x 89 | 2.67 | 2.43 | 2.03 |
| Column 1 | 2 | 3 | 4 | 5 | 6 |

Table A-4

Maximum Spans for Roof Joists — Specified Roof Snow Loads 1.0 to 2.0 kPa

Forming Part of Sentence 9.23.4.2.(1)

| Commercial Designation | Grade | Joist Size, mm | Maximum Span, m |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Specified Snow Load, kPa |  |  |  |  |  |  |  |  |
|  |  |  | 1.0 |  |  | 1.5 |  |  | 2.0 |  |  |
|  |  |  | Joist Spacing, mm |  |  | Joist Spacing, mm |  |  | Joist Spacing, mm |  |  |
|  |  |  | 300 | 400 | 600 | 300 | 400 | 600 | 300 | 400 | 600 |
| Douglas Fir – Larch (includes Douglas Fir and Western Larch) | Select Structural | 38 x 89 | 2.71 | 2.46 | 2.15 | 2.37 | 2.15 | 1.88 | 2.15 | 1.95 | 1.71 |
|  |  | 38 x 140 | 4.26 | 3.87 | 3.38 | 3.72 | 3.38 | 2.95 | 3.38 | 3.07 | 2.68 |
|  |  | 38 x 184 | 5.60 | 5.09 | 4.44 | 4.89 | 4.44 | 3.88 | 4.44 | 4.04 | 3.53 |
|  |  | 38 x 235 | 7.15 | 6.49 | 5.67 | 6.24 | 5.67 | 4.96 | 5.67 | 5.15 | 4.50 |
|  |  | 38 x 286 | 8.70 | 7.90 | 6.91 | 7.60 | 6.91 | 6.03 | 6.91 | 6.27 | 5.48 |
|  | No. 1 and No. 2 | 38 x 89 | 2.59 | 2.36 | 2.06 | 2.27 | 2.06 | 1.80 | 2.06 | 1.87 | 1.63 |
|  |  | 38 x 140 | 4.08 | 3.71 | 3.24 | 3.57 | 3.24 | 2.83 | 3.24 | 2.94 | 2.57 |
|  |  | 38 x 184 | 5.36 | 4.87 | 4.26 | 4.69 | 4.26 | 3.72 | 4.26 | 3.87 | 3.38 |
|  |  | 38 x 235 | 6.85 | 6.22 | 5.44 | 5.98 | 5.44 | 4.74 | 5.44 | 4.94 | 4.22 |
|  |  | 38 x 286 | 8.34 | 7.57 | 6.40 | 7.28 | 6.62 | 5.50 | 6.62 | 6.00 | 4.90 |
|  | No. 3 | 38 x 89 | 2.49 | 2.16 | 1.76 | 2.14 | 1.85 | 1.51 | 1.91 | 1.65 | 1.35 |
|  |  | 38 x 140 | 3.56 | 3.08 | 2.51 | 3.06 | 2.65 | 2.16 | 2.72 | 2.36 | 1.92 |
|  |  | 38 x 184 | 4.33 | 3.75 | 3.06 | 3.72 | 3.22 | 2.63 | 3.31 | 2.87 | 2.34 |
|  |  | 38 x 235 | 5.29 | 4.58 | 3.74 | 4.55 | 3.94 | 3.22 | 4.05 | 3.51 | 2.86 |
|  |  | 38 x 286 | 6.14 | 5.32 | 4.34 | 5.28 | 4.57 | 3.73 | 4.70 | 4.07 | 3.32 |
|  | Construction | 38 x 89 | 2.51 | 2.28 | 1.99 | 2.20 | 1.99 | 1.74 | 1.99 | 1.81 | 1.58 |
|  | Standard | 38 x 89 | 2.41 | 2.08 | 1.70 | 2.07 | 1.79 | 1.46 | 1.84 | 1.60 | 1.30 |
| Hem – Fir (includes Western Hemlock and Amabilis Fir) | Select Structural | 38 x 89 | 2.67 | 2.43 | 2.12 | 2.33 | 2.12 | 1.85 | 2.12 | 1.93 | 1.68 |
|  |  | 38 x 140 | 4.20 | 3.82 | 3.33 | 3.67 | 3.33 | 2.91 | 3.33 | 3.03 | 2.65 |
|  |  | 38 x 184 | 5.52 | 5.02 | 4.38 | 4.82 | 4.38 | 3.83 | 4.38 | 3.98 | 3.48 |
|  |  | 38 x 235 | 7.05 | 6.41 | 5.60 | 6.16 | 5.60 | 4.89 | 5.60 | 5.09 | 4.44 |
|  |  | 38 x 286 | 8.58 | 7.80 | 6.81 | 7.50 | 6.81 | 5.95 | 6.81 | 6.19 | 5.41 |
|  | No. 1 and No. 2 | 38 x 89 | 2.59 | 2.36 | 2.06 | 2.27 | 2.06 | 1.80 | 2.06 | 1.87 | 1.63 |
|  |  | 38 x 140 | 4.08 | 3.71 | 3.24 | 3.57 | 3.24 | 2.83 | 3.24 | 2.94 | 2.57 |
|  |  | 38 x 184 | 5.36 | 4.87 | 4.26 | 4.69 | 4.26 | 3.72 | 4.26 | 3.87 | 3.38 |
|  |  | 38 x 235 | 6.85 | 6.22 | 5.44 | 5.98 | 5.44 | 4.75 | 5.44 | 4.94 | 4.32 |
|  |  | 38 x 286 | 8.34 | 7.57 | 6.62 | 7.28 | 6.62 | 5.77 | 6.62 | 6.01 | 5.25 |
|  | No. 3 | 38 x 89 | 2.51 | 2.28 | 1.99 | 2.20 | 1.99 | 1.74 | 1.99 | 1.81 | 1.58 |
|  |  | 38 x 140 | 3.95 | 3.59 | 3.10 | 3.45 | 3.14 | 2.67 | 3.14 | 2.85 | 2.37 |
|  |  | 38 x 184 | 5.20 | 4.62 | 3.77 | 4.54 | 3.97 | 3.24 | 4.09 | 3.54 | 2.89 |
|  |  | 38 x 235 | 6.53 | 5.65 | 4.61 | 5.61 | 4.86 | 3.97 | 5.00 | 4.33 | 3.53 |
|  |  | 38 x 286 | 7.57 | 6.56 | 5.35 | 6.51 | 5.64 | 4.60 | 5.80 | 5.02 | 4.10 |
|  | Construction | 38 x 89 | 2.51 | 2.28 | 1.99 | 2.20 | 1.99 | 1.74 | 1.99 | 1.81 | 1.58 |
|  | Standard | 38 x 89 | 2.43 | 2.18 | 1.78 | 2.12 | 1.88 | 1.53 | 1.93 | 1.67 | 1.36 |
| Spruce – Pine – Fir (includes Spruce (all species except Coast Sitka Spruce), Jack Pine, Lodgepole Pine, Balsam Fir and Alpine Fir) | Select Structural | 38 x 89 | 2.55 | 2.32 | 2.03 | 2.23 | 2.03 | 1.77 | 2.03 | 1.84 | 1.61 |
|  |  | 38 x 140 | 4.02 | 3.65 | 3.19 | 3.51 | 3.19 | 2.79 | 3.19 | 2.90 | 2.53 |
|  |  | 38 x 184 | 5.28 | 4.80 | 4.19 | 4.61 | 4.19 | 3.66 | 4.19 | 3.81 | 3.33 |
|  |  | 38 x 235 | 6.74 | 6.13 | 5.35 | 5.89 | 5.35 | 4.68 | 5.35 | 4.86 | 4.25 |
|  |  | 38 x 286 | 8.21 | 7.46 | 6.52 | 7.17 | 6.52 | 5.69 | 6.52 | 5.92 | 5.17 |
|  | No. 1 and No. 2 | 38 x 89 | 2.47 | 2.24 | 1.96 | 2.16 | 1.96 | 1.71 | 1.96 | 1.78 | 1.56 |
|  |  | 38 x 140 | 3.89 | 3.53 | 3.08 | 3.40 | 3.08 | 2.69 | 3.08 | 2.80 | 2.45 |
|  |  | 38 x 184 | 5.11 | 4.64 | 4.05 | 4.46 | 4.05 | 3.54 | 4.05 | 3.68 | 3.22 |
|  |  | 38 x 235 | 6.52 | 5.93 | 5.18 | 5.70 | 5.18 | 4.52 | 5.18 | 4.70 | 4.11 |
|  |  | 38 x 286 | 7.94 | 7.21 | 6.30 | 6.94 | 6.30 | 5.50 | 6.30 | 5.73 | 5.00 |
|  | No. 3 | 38 x 89 | 2.43 | 2.20 | 1.93 | 2.12 | 1.93 | 1.68 | 1.93 | 1.75 | 1.53 |
|  |  | 38 x 140 | 3.82 | 3.47 | 3.03 | 3.33 | 3.03 | 2.65 | 3.03 | 2.75 | 2.37 |
|  |  | 38 x 184 | 5.02 | 4.56 | 3.77 | 4.38 | 3.97 | 3.24 | 3.98 | 3.54 | 2.89 |
|  |  | 38 x 235 | 6.41 | 5.65 | 4.61 | 5.60 | 4.86 | 3.97 | 5.00 | 4.33 | 3.53 |
|  |  | 38 x 286 | 7.57 | 6.56 | 5.35 | 6.51 | 5.64 | 4.60 | 5.80 | 5.02 | 4.10 |
|  | Construction | 38 x 89 | 2.43 | 2.20 | 1.93 | 2.12 | 1.93 | 1.68 | 1.93 | 1.75 | 1.53 |
|  | Standard | 38 x 89 | 2.33 | 2.12 | 1.85 | 2.04 | 1.85 | 1.59 | 1.85 | 1.68 | 1.41 |
| Northern Species (includes any Canadian Species covered by the NLGA Standard Grading Rules) | Select Structural | 38 x 89 | 2.28 | 2.07 | 1.81 | 1.99 | 1.81 | 1.58 | 1.81 | 1.65 | 1.44 |
|  |  | 38 x 140 | 3.59 | 3.26 | 2.85 | 3.14 | 2.85 | 2.49 | 2.85 | 2.59 | 2.26 |
|  |  | 38 x 184 | 4.72 | 4.29 | 3.75 | 4.12 | 3.75 | 3.27 | 3.75 | 3.40 | 2.97 |
|  |  | 38 x 235 | 6.03 | 5.48 | 4.79 | 5.27 | 4.79 | 4.18 | 4.79 | 4.35 | 3.80 |
|  |  | 38 x 286 | 7.34 | 6.67 | 5.82 | 6.41 | 5.82 | 5.09 | 5.82 | 5.29 | 4.62 |
|  | No. 1 and No. 2 | 38 x 89 | 2.23 | 2.03 | 1.77 | 1.95 | 1.77 | 1.55 | 1.77 | 1.61 | 1.41 |
|  |  | 38 x 140 | 3.51 | 3.19 | 2.79 | 3.07 | 2.79 | 2.43 | 2.79 | 2.53 | 2.21 |
|  |  | 38 x 184 | 4.61 | 4.19 | 3.66 | 4.03 | 3.66 | 3.20 | 3.66 | 3.33 | 2.91 |
|  |  | 38 x 235 | 5.89 | 5.35 | 4.68 | 5.15 | 4.68 | 4.09 | 4.68 | 4.25 | 3.68 |
|  |  | 38 x 286 | 7.17 | 6.52 | 5.58 | 6.26 | 5.69 | 4.80 | 5.69 | 5.17 | 4.27 |
|  | No. 3 | 38 x 89 | 2.18 | 1.98 | 1.73 | 1.90 | 1.73 | 1.50 | 1.73 | 1.57 | 1.33 |
|  |  | 38 x 140 | 3.42 | 3.05 | 2.49 | 2.99 | 2.62 | 2.14 | 2.69 | 2.33 | 1.90 |
|  |  | 38 x 184 | 4.28 | 3.71 | 3.03 | 3.68 | 3.19 | 2.60 | 3.28 | 2.84 | 2.32 |
|  |  | 38 x 235 | 5.23 | 4.53 | 3.70 | 4.50 | 3.90 | 3.18 | 4.01 | 3.47 | 2.83 |
|  |  | 38 x 286 | 6.07 | 5.26 | 4.29 | 5.22 | 4.52 | 3.69 | 4.65 | 4.03 | 3.29 |
|  | Construction | 38 x 89 | 2.18 | 1.98 | 1.73 | 1.90 | 1.73 | 1.51 | 1.73 | 1.57 | 1.37 |
|  | Standard | 38 x 89 | 2.09 | 1.81 | 1.48 | 1.80 | 1.56 | 1.27 | 1.60 | 1.38 | 1.13 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |

Table A-5

Maximum Spans for Roof Joists — Specified Roof Snow Loads 2.5 and 3.0 kPa

Forming Part of Sentence 9.23.4.2.(1)

| Commercial Designation | Grade | Joist Size, mm | Maximum Span, m |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Specified Snow Load, kPa |  |  |  |  |  |
|  |  |  | 2.5 |  |  | 3.0 |  |  |
|  |  |  | Joist Spacing, mm |  |  | Joist Spacing, mm |  |  |
|  |  |  | 300 | 400 | 600 | 300 | 400 | 600 |
| Douglas Fir – Larch (includes Douglas Fir and Western Larch) | Select Structural | 38 x 89 | 1.99 | 1.81 | 1.58 | 1.88 | 1.71 | 1.49 |
|  |  | 38 x 140 | 3.14 | 2.85 | 2.49 | 2.95 | 2.68 | 2.34 |
|  |  | 38 x 184 | 4.12 | 3.75 | 3.27 | 3.88 | 3.53 | 3.08 |
|  |  | 38 x 235 | 5.27 | 4.79 | 4.18 | 4.96 | 4.50 | 3.93 |
|  |  | 38 x 286 | 6.41 | 5.82 | 5.09 | 6.03 | 5.48 | 4.79 |
|  | No. 1 and No. 2 | 38 x 89 | 1.91 | 1.74 | 1.52 | 1.80 | 1.63 | 1.43 |
|  |  | 38 x 140 | 3.01 | 2.73 | 2.39 | 2.83 | 2.57 | 2.25 |
|  |  | 38 x 184 | 3.95 | 3.59 | 3.14 | 3.72 | 3.38 | 2.90 |
|  |  | 38 x 235 | 5.05 | 4.59 | 3.84 | 4.75 | 4.32 | 3.55 |
|  |  | 38 x 286 | 6.14 | 5.46 | 4.46 | 5.78 | 5.05 | 4.12 |
|  | No. 3 | 38 x 89 | 1.74 | 1.50 | 1.23 | 1.60 | 1.39 | 1.13 |
|  |  | 38 x 140 | 2.48 | 2.15 | 1.75 | 2.29 | 1.98 | 1.62 |
|  |  | 38 x 184 | 3.01 | 2.61 | 2.13 | 2.79 | 2.41 | 1.97 |
|  |  | 38 x 235 | 3.69 | 3.19 | 2.61 | 3.41 | 2.95 | 2.41 |
|  |  | 38 x 286 | 4.28 | 3.70 | 3.03 | 3.95 | 3.42 | 2.79 |
|  | Construction | 38 x 89 | 1.85 | 1.68 | 1.47 | 1.74 | 1.58 | 1.38 |
|  | Standard | 38 x 89 | 1.68 | 1.45 | 1.19 | 1.55 | 1.34 | 1.10 |
| Hem – Fir (includes Western Hemlock and Amabilis Fir) | Select Structural | 38 x 89 | 1.97 | 1.79 | 1.56 | 1.85 | 1.68 | 1.47 |
|  |  | 38 x 140 | 3.10 | 2.81 | 2.46 | 2.91 | 2.65 | 2.31 |
|  |  | 38 x 184 | 4.07 | 3.70 | 3.23 | 3.83 | 3.48 | 3.04 |
|  |  | 38 x 235 | 5.20 | 4.72 | 4.12 | 4.89 | 4.44 | 3.88 |
|  |  | 38 x 286 | 6.32 | 5.75 | 5.02 | 5.95 | 5.41 | 4.72 |
|  | No. 1 and No. 2 | 38 x 89 | 1.91 | 1.74 | 1.52 | 1.80 | 1.63 | 1.43 |
|  |  | 38 x 140 | 3.01 | 2.73 | 2.39 | 2.83 | 2.57 | 2.25 |
|  |  | 38 x 184 | 3.95 | 3.59 | 3.14 | 3.72 | 3.38 | 2.95 |
|  |  | 38 x 235 | 5.05 | 4.59 | 4.01 | 4.75 | 4.32 | 3.72 |
|  |  | 38 x 286 | 6.14 | 5.58 | 4.68 | 5.78 | 5.25 | 4.32 |
|  | No. 3 | 38 x 89 | 1.85 | 1.68 | 1.47 | 1.74 | 1.58 | 1.38 |
|  |  | 38 x 140 | 2.91 | 2.65 | 2.16 | 2.74 | 2.45 | 2.00 |
|  |  | 38 x 184 | 3.72 | 3.22 | 2.63 | 3.44 | 2.98 | 2.43 |
|  |  | 38 x 235 | 4.55 | 3.94 | 3.22 | 4.20 | 3.64 | 2.97 |
|  |  | 38 x 286 | 5.28 | 4.57 | 3.73 | 4.88 | 4.22 | 3.45 |
|  | Construction | 38 x 89 | 1.85 | 1.68 | 1.47 | 1.74 | 1.58 | 1.38 |
|  | Standard | 38 x 89 | 1.76 | 1.52 | 1.24 | 1.62 | 1.40 | 1.15 |
| Spruce – Pine – Fir (includes Spruce (all species except Coast Sitka Spruce), Jack Pine, Lodgepole Pine, Balsam Fir and Alpine Fir) | Select Structural | 38 x 89 | 1.88 | 1.71 | 1.49 | 1.77 | 1.61 | 1.41 |
|  |  | 38 x 140 | 2.96 | 2.69 | 2.35 | 2.79 | 2.53 | 2.21 |
|  |  | 38 x 184 | 3.89 | 3.54 | 3.09 | 3.66 | 3.33 | 2.91 |
|  |  | 38 x 235 | 4.97 | 4.52 | 3.94 | 4.68 | 4.25 | 3.71 |
|  |  | 38 x 286 | 6.05 | 5.50 | 4.80 | 5.69 | 5.17 | 4.52 |
|  | No. 1 and No. 2 | 38 x 89 | 1.82 | 1.65 | 1.44 | 1.71 | 1.56 | 1.36 |
|  |  | 38 x 140 | 2.86 | 2.60 | 2.27 | 2.69 | 2.45 | 2.14 |
|  |  | 38 x 184 | 3.76 | 3.42 | 2.99 | 3.54 | 3.22 | 2.81 |
|  |  | 38 x 235 | 4.81 | 4.37 | 3.82 | 4.52 | 4.11 | 3.59 |
|  |  | 38 x 286 | 5.85 | 5.31 | 4.64 | 5.50 | 5.00 | 4.37 |
|  | No. 3 | 38 x 89 | 1.79 | 1.62 | 1.42 | 1.68 | 1.53 | 1.34 |
|  |  | 38 x 140 | 2.81 | 2.56 | 2.16 | 2.65 | 2.40 | 2.00 |
|  |  | 38 x 184 | 3.70 | 3.22 | 2.63 | 3.44 | 2.98 | 2.43 |
|  |  | 38 x 235 | 4.55 | 3.94 | 3.22 | 4.20 | 3.64 | 2.97 |
|  |  | 38 x 286 | 5.28 | 4.57 | 3.73 | 4.88 | 4.22 | 3.45 |
|  | Construction | 38 x 89 | 1.79 | 1.62 | 1.42 | 1.68 | 1.53 | 1.34 |
|  | Standard | 38 x 89 | 1.72 | 1.56 | 1.29 | 1.62 | 1.46 | 1.19 |
| Northern Species (includes any Canadian Species covered by the NLGA Standard Grading Rules | Select Structural | 38 x 89 | 1.68 | 1.53 | 1.34 | 1.58 | 1.44 | 1.26 |
|  |  | 38 x 140 | 2.65 | 2.40 | 2.10 | 2.49 | 2.26 | 1.98 |
|  |  | 38 x 184 | 3.48 | 3.16 | 2.76 | 3.27 | 2.97 | 2.60 |
|  |  | 38 x 235 | 4.44 | 4.04 | 3.53 | 4.18 | 3.80 | 3.32 |
|  |  | 38 x 286 | 5.41 | 4.91 | 4.29 | 5.09 | 4.62 | 4.04 |
|  | No. 1 and No. 2 | 38 x 89 | 1.64 | 1.49 | 1.31 | 1.55 | 1.41 | 1.23 |
|  |  | 38 x 140 | 2.59 | 2.35 | 2.05 | 2.43 | 2.21 | 1.93 |
|  |  | 38 x 184 | 3.40 | 3.09 | 2.70 | 3.20 | 2.91 | 2.53 |
|  |  | 38 x 235 | 4.34 | 3.94 | 3.35 | 4.09 | 3.71 | 3.10 |
|  |  | 38 x 286 | 5.28 | 4.76 | 3.89 | 4.97 | 4.40 | 3.59 |
|  | No. 3 | 38 x 89 | 1.60 | 1.46 | 1.21 | 1.51 | 1.37 | 1.12 |
|  |  | 38 x 140 | 2.45 | 2.12 | 1.73 | 2.26 | 1.96 | 1.60 |
|  |  | 38 x 184 | 2.98 | 2.58 | 2.11 | 2.76 | 2.39 | 1.95 |
|  |  | 38 x 235 | 3.65 | 3.16 | 2.58 | 3.37 | 2.92 | 2.38 |
|  |  | 38 x 286 | 4.23 | 3.66 | 2.99 | 3.91 | 3.39 | 2.76 |
|  | Construction | 38 x 89 | 1.60 | 1.46 | 1.27 | 1.51 | 1.37 | 1.20 |
|  | Standard | 38 x 89 | 1.46 | 1.26 | 1.03 | 1.34 | 1.16 | 0.95 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |

Table A-6

Maximum Spans for Roof Rafters Specified Roof Snow Loads 1.0 to 2.0 kPa

Forming Part of Sentence 9.23.4.2.(1)

| Commercial Designation | Grade | Rafter Size, mm | Maximum Span, m |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Specified Snow Load, kPa |  |  |  |  |  |  |  |  |
|  |  |  | 1.0 |  |  | 1.5 |  |  | 2.0 |  |  |
|  |  |  | Rafter Spacing, mm |  |  | Rafter Spacing, mm |  |  | Rafter Spacing, mm |  |  |
|  |  |  | 300 | 400 | 600 | 300 | 400 | 600 | 300 | 400 | 600 |
| Douglas Fir – Larch (includes Douglas Fir and Western Larch) | Select Structural | 38 x 89 | 3.41 | 3.10 | 2.71 | 2.98 | 2.71 | 2.37 | 2.71 | 2.46 | 2.15 |
|  |  | 38 x 140 | 5.37 | 4.88 | 4.26 | 4.69 | 4.26 | 3.72 | 4.26 | 3.87 | 3.38 |
|  |  | 38 x 184 | 7.05 | 6.41 | 5.60 | 6.16 | 5.60 | 4.89 | 5.60 | 5.09 | 4.44 |
|  |  | 38 x 235 | 9.01 | 8.18 | 7.15 | 7.87 | 7.15 | 6.24 | 7.15 | 6.49 | 5.62 |
|  |  | 38 x 285 | 10.96 | 9.96 | 8.70 | 9.58 | 8.70 | 7.40 | 8.70 | 7.90 | 6.52 |
|  | No. 1 and No. 2 | 38 x 89 | 3.27 | 2.97 | 2.59 | 2.86 | 2.59 | 2.27 | 2.59 | 2.36 | 2.06 |
|  |  | 38 x 140 | 5.14 | 4.67 | 3.95 | 4.49 | 4.08 | 3.34 | 4.08 | 3.60 | 2.94 |
|  |  | 38 x 184 | 6.76 | 5.88 | 4.80 | 5.74 | 4.97 | 4.06 | 5.06 | 4.38 | 3.58 |
|  |  | 38 x 235 | 8.30 | 7.19 | 5.87 | 7.02 | 6.08 | 4.96 | 6.19 | 5.36 | 4.38 |
|  |  | 38 x 285 | 9.63 | 8.34 | 6.81 | 8.14 | 7.05 | 5.76 | 7.18 | 6.22 | 5.08 |
|  | No. 3 | 38 x 89 | 2.65 | 2.30 | 1.87 | 2.24 | 1.94 | 1.58 | 1.98 | 1.71 | 1.40 |
|  |  | 38 x 140 | 3.78 | 3.28 | 2.68 | 3.20 | 2.77 | 2.26 | 2.82 | 2.44 | 1.99 |
|  |  | 38 x 184 | 4.61 | 3.99 | 3.26 | 3.89 | 3.37 | 2.75 | 3.43 | 2.97 | 2.43 |
|  |  | 38 x 235 | 5.63 | 4.88 | 3.98 | 4.76 | 4.12 | 3.37 | 4.20 | 3.64 | 2.97 |
|  |  | 38 x 285 | 6.53 | 5.66 | 4.62 | 5.52 | 4.78 | 3.91 | 4.87 | 4.22 | 3.44 |
|  | Construction | 38 x 89 | 3.17 | 2.88 | 2.42 | 2.77 | 2.50 | 2.04 | 2.51 | 2.21 | 1.80 |
|  | Standard | 38 x 89 | 2.56 | 2.22 | 1.81 | 2.17 | 1.88 | 1.53 | 1.91 | 1.65 | 1.35 |
| Hem – Fir (includes Western Hemlock and Amabilis Fir) | Select Structural | 38 x 89 | 3.36 | 3.06 | 2.67 | 2.94 | 2.67 | 2.33 | 2.67 | 2.43 | 2.12 |
|  |  | 38 x 140 | 5.29 | 4.81 | 4.20 | 4.62 | 4.20 | 3.67 | 4.20 | 3.82 | 3.33 |
|  |  | 38 x 184 | 6.96 | 6.32 | 5.52 | 6.08 | 5.52 | 4.82 | 5.52 | 5.02 | 4.38 |
|  |  | 38 x 235 | 8.88 | 8.07 | 7.05 | 7.76 | 7.05 | 6.16 | 7.05 | 6.41 | 5.54 |
|  |  | 38 x 285 | 10.81 | 9.82 | 8.58 | 9.45 | 8.58 | 7.28 | 8.58 | 7.80 | 6.42 |
|  | No. 1 and No. 2 | 38 x 89 | 3.27 | 2.97 | 2.59 | 2.86 | 2.59 | 2.27 | 2.59 | 2.36 | 2.06 |
|  |  | 38 x 140 | 5.14 | 4.67 | 4.08 | 4.49 | 4.08 | 3.50 | 4.08 | 3.71 | 3.08 |
|  |  | 38 x 184 | 6.76 | 6.14 | 5.04 | 5.90 | 5.21 | 4.26 | 5.31 | 4.60 | 3.75 |
|  |  | 38 x 235 | 8.63 | 7.54 | 6.16 | 7.36 | 6.37 | 5.20 | 6.49 | 5.62 | 4.59 |
|  |  | 38 x 285 | 10.11 | 8.75 | 7.15 | 8.54 | 7.40 | 6.04 | 7.53 | 6.52 | 5.33 |
|  | No. 3 | 38 x 89 | 3.17 | 2.83 | 2.31 | 2.76 | 2.39 | 1.95 | 2.44 | 2.11 | 1.72 |
|  |  | 38 x 140 | 4.67 | 4.04 | 3.30 | 3.95 | 3.42 | 2.79 | 3.48 | 3.01 | 2.46 |
|  |  | 38 x 184 | 5.68 | 4.92 | 4.02 | 4.80 | 4.16 | 3.40 | 4.23 | 3.67 | 2.99 |
|  |  | 38 x 235 | 6.95 | 6.02 | 4.91 | 5.87 | 5.08 | 4.15 | 5.18 | 4.48 | 3.66 |
|  |  | 38 x 285 | 8.06 | 6.98 | 5.70 | 6.81 | 5.90 | 4.82 | 6.01 | 5.20 | 4.25 |
|  | Construction | 38 x 89 | 3.17 | 2.88 | 2.51 | 2.77 | 2.51 | 2.14 | 2.51 | 2.28 | 1.89 |
|  | Standard | 38 x 89 | 2.68 | 2.32 | 1.90 | 2.27 | 1.96 | 1.60 | 2.00 | 1.73 | 1.41 |
| Spruce – Pine – Fir (includes Spruce (all species except Coast Sitka Spruce), Jack Pine, Lodgepole Pine, Balsam Fir and Alpine Fir) | Select Structural | 38 x 89 | 3.22 | 2.92 | 2.55 | 2.81 | 2.55 | 2.23 | 2.55 | 2.32 | 2.03 |
|  |  | 38 x 140 | 5.06 | 4.60 | 4.02 | 4.42 | 4.02 | 3.51 | 4.02 | 3.65 | 3.19 |
|  |  | 38 x 184 | 6.65 | 6.05 | 5.28 | 5.81 | 5.28 | 4.61 | 5.28 | 4.80 | 4.19 |
|  |  | 38 x 235 | 8.50 | 7.72 | 6.74 | 7.42 | 6.74 | 5.89 | 6.74 | 6.13 | 5.35 |
|  |  | 38 x 285 | 10.34 | 9.40 | 8.21 | 9.03 | 8.21 | 7.17 | 8.21 | 7.46 | 6.52 |
|  | No. 1 and No. 2 | 38 x 89 | 3.11 | 2.83 | 2.47 | 2.72 | 2.47 | 2.16 | 2.47 | 2.24 | 1.96 |
|  |  | 38 x 140 | 4.90 | 4.45 | 3.89 | 4.28 | 3.89 | 3.40 | 3.89 | 3.53 | 3.08 |
|  |  | 38 x 184 | 6.44 | 5.85 | 5.11 | 5.62 | 5.11 | 4.41 | 5.11 | 4.64 | 3.89 |
|  |  | 38 x 235 | 8.22 | 7.47 | 6.38 | 7.18 | 6.52 | 5.39 | 6.52 | 5.82 | 4.75 |
|  |  | 38 x 285 | 10.00 | 9.06 | 7.40 | 8.74 | 7.66 | 6.25 | 7.80 | 6.76 | 5.52 |
|  | No. 3 | 38 x 89 | 3.06 | 2.78 | 2.31 | 2.67 | 2.39 | 1.95 | 2.43 | 2.11 | 1.72 |
|  |  | 38 x 140 | 4.67 | 4.04 | 3.30 | 3.95 | 3.42 | 2.79 | 3.48 | 3.01 | 2.46 |
|  |  | 38 x 184 | 5.68 | 4.92 | 4.02 | 4.80 | 4.16 | 3.40 | 4.23 | 3.67 | 2.99 |
|  |  | 38 x 235 | 6.95 | 6.02 | 4.91 | 5.87 | 5.08 | 4.15 | 5.18 | 4.48 | 3.66 |
|  |  | 38 x 285 | 8.06 | 6.98 | 5.70 | 6.81 | 5.90 | 4.82 | 6.01 | 5.20 | 4.25 |
|  | Construction | 38 x 89 | 3.06 | 2.78 | 2.43 | 2.67 | 2.43 | 2.12 | 2.43 | 2.20 | 1.93 |
|  | Standard | 38 x 89 | 2.78 | 2.41 | 1.97 | 2.35 | 2.04 | 1.66 | 2.07 | 1.79 | 1.47 |
| Northern Species (includes any Canadian species covered by the NLGA Standard Grading Rules) | Select Structural | 38 x 89 | 2.88 | 2.61 | 2.28 | 2.51 | 2.28 | 1.99 | 2.28 | 2.07 | 1.81 |
|  |  | 38 x 140 | 4.53 | 4.11 | 3.59 | 3.95 | 3.59 | 3.14 | 3.59 | 3.26 | 2.85 |
|  |  | 38 x 184 | 5.95 | 5.40 | 4.72 | 5.20 | 4.72 | 4.12 | 4.72 | 4.29 | 3.68 |
|  |  | 38 x 235 | 7.60 | 6.90 | 6.03 | 6.64 | 6.03 | 5.11 | 6.03 | 5.48 | 4.51 |
|  |  | 38 x 285 | 9.25 | 8.40 | 7.01 | 8.08 | 7.26 | 5.93 | 7.34 | 6.40 | 5.23 |
|  | No. 1 and No. 2 | 38 x 89 | 2.81 | 2.55 | 2.23 | 2.46 | 2.23 | 1.95 | 2.23 | 2.03 | 1.77 |
|  |  | 38 x 140 | 4.42 | 4.02 | 3.44 | 3.86 | 3.51 | 2.91 | 3.51 | 3.14 | 2.56 |
|  |  | 38 x 184 | 5.81 | 5.13 | 4.19 | 5.00 | 4.33 | 3.54 | 4.41 | 3.82 | 3.12 |
|  |  | 38 x 235 | 7.24 | 6.27 | 5.12 | 6.12 | 5.30 | 4.33 | 5.40 | 4.67 | 3.82 |
|  |  | 38 x 285 | 8.40 | 7.27 | 5.94 | 7.10 | 6.15 | 5.02 | 6.26 | 5.42 | 4.43 |
|  | No. 3 | 38 x 89 | 2.62 | 2.27 | 1.85 | 2.22 | 1.92 | 1.57 | 1.95 | 1.69 | 1.38 |
|  |  | 38 x 140 | 3.74 | 3.24 | 2.65 | 3.16 | 2.74 | 2.24 | 2.79 | 2.42 | 1.97 |
|  |  | 38 x 184 | 4.56 | 3.94 | 3.22 | 3.85 | 3.33 | 2.72 | 3.40 | 2.94 | 2.40 |
|  |  | 38 x 235 | 5.57 | 4.82 | 3.94 | 4.71 | 4.08 | 3.33 | 4.15 | 3.60 | 2.94 |
|  |  | 38 x 285 | 6.46 | 5.60 | 4.57 | 5.46 | 4.73 | 3.86 | 4.82 | 4.17 | 3.41 |
|  | Construction | 38 x 89 | 2.74 | 2.49 | 2.11 | 2.40 | 2.18 | 1.90 | 2.18 | 1.93 | 1.57 |
|  | Standard | 38 x 89 | 2.22 | 1.93 | 1.57 | 1.88 | 1.63 | 1.33 | 1.66 | 1.44 | 1.17 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |

Table A-7

Maximum Spans for Roof Rafters — Specified Roof Snow Loads 2.5 and 3.0 kPa

Forming Part of Sentence 9.23.4.2.(1)

| Commercial Designation | Grade | Rafter Size, mm | Maximum Span, m |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Specified Snow Load, kPa |  |  |  |  |  |
|  |  |  | 2.5 |  |  | 3.0 |  |  |
|  |  |  | Rafter Spacing, mm |  |  | Rafter Spacing, mm |  |  |
|  |  |  | 300 | 400 | 600 | 300 | 400 | 600 |
| Douglas Fir – Larch (includes Douglas Fir and Western Larch) | Select Structural | 38 x 89 | 2.51 | 2.28 | 1.99 | 2.37 | 2.15 | 1.88 |
|  |  | 38 x 140 | 3.95 | 3.59 | 3.14 | 3.72 | 3.38 | 2.95 |
|  |  | 38 x 184 | 5.20 | 4.72 | 4.12 | 4.89 | 4.44 | 3.83 |
|  |  | 38 x 235 | 6.64 | 6.03 | 5.08 | 6.24 | 5.67 | 4.68 |
|  |  | 38 x 285 | 8.08 | 7.23 | 5.90 | 7.60 | 6.65 | 5.43 |
|  | No. 1 and No. 2 | 38 x 89 | 2.41 | 2.19 | 1.86 | 2.27 | 2.06 | 1.71 |
|  |  | 38 x 140 | 3.76 | 3.26 | 2.66 | 3.46 | 3.00 | 2.45 |
|  |  | 38 x 184 | 4.58 | 3.96 | 3.24 | 4.21 | 3.65 | 2.98 |
|  |  | 38 x 235 | 5.60 | 4.85 | 3.96 | 5.15 | 4.46 | 3.64 |
|  |  | 38 x 285 | 6.50 | 5.63 | 4.59 | 5.98 | 5.17 | 4.23 |
|  | No. 3 | 38 x 89 | 1.79 | 1.55 | 1.26 | 1.64 | 1.42 | 1.16 |
|  |  | 38 x 140 | 2.55 | 2.21 | 1.80 | 2.35 | 2.03 | 1.66 |
|  |  | 38 x 184 | 3.10 | 2.69 | 2.20 | 2.86 | 2.47 | 2.02 |
|  |  | 38 x 235 | 3.80 | 3.29 | 2.68 | 3.49 | 3.02 | 2.47 |
|  |  | 38 x 285 | 4.41 | 3.82 | 3.12 | 4.05 | 3.51 | 2.87 |
|  | Construction | 38 x 89 | 2.30 | 2.00 | 1.63 | 2.12 | 1.84 | 1.50 |
|  | Standard | 38 x 89 | 1.73 | 1.50 | 1.22 | 1.59 | 1.38 | 1.12 |
| Hem – Fir (includes Western Hemlock and Amabilis Fir) | Select Structural | 38 x 89 | 2.48 | 2.25 | 1.97 | 2.33 | 2.12 | 1.85 |
|  |  | 38 x 140 | 3.90 | 3.54 | 3.10 | 3.67 | 3.33 | 2.91 |
|  |  | 38 x 184 | 5.13 | 4.66 | 4.07 | 4.82 | 4.38 | 3.77 |
|  |  | 38 x 235 | 6.55 | 5.95 | 5.01 | 6.16 | 5.60 | 4.61 |
|  |  | 38 x 285 | 7.97 | 7.12 | 5.81 | 7.50 | 6.55 | 5.34 |
|  | No. 1 and No. 2 | 38 x 89 | 2.41 | 2.19 | 1.91 | 2.27 | 2.06 | 1.80 |
|  |  | 38 x 140 | 3.79 | 3.42 | 2.79 | 3.57 | 3.14 | 2.57 |
|  |  | 38 x 184 | 4.80 | 4.16 | 3.40 | 4.42 | 3.83 | 3.12 |
|  |  | 38 x 235 | 5.87 | 5.08 | 4.15 | 5.40 | 4.68 | 3.82 |
|  |  | 38 x 285 | 6.81 | 5.90 | 4.82 | 6.27 | 5.43 | 4.43 |
|  | No. 3 | 38 x 89 | 2.21 | 1.91 | 1.56 | 2.03 | 1.76 | 1.43 |
|  |  | 38 x 140 | 3.15 | 2.73 | 2.23 | 2.90 | 2.51 | 2.05 |
|  |  | 38 x 184 | 3.83 | 3.32 | 2.71 | 3.52 | 3.05 | 2.49 |
|  |  | 38 x 235 | 4.68 | 4.06 | 3.31 | 4.31 | 3.73 | 3.05 |
|  |  | 38 x 285 | 5.53 | 4.71 | 3.84 | 5.00 | 4.33 | 3.54 |
|  | Commercial | 38 x 89 | 2.33 | 2.09 | 1.71 | 2.20 | 1.93 | 1.57 |
|  | Standard | 38 x 89 | 1.81 | 1.57 | 1.28 | 1.66 | 1.44 | 1.18 |
| Spruce – Pine – Fir (includes Spruce (all species except Coast Sitka Spruce), Jack Pine, Lodgepole Pine, Balsam Fir and Alpine Fir) | Select Structural | 38 x 89 | 2.37 | 2.15 | 1.88 | 2.23 | 2.03 | 1.77 |
|  |  | 38 x 140 | 3.73 | 3.39 | 2.96 | 3.51 | 3.19 | 2.79 |
|  |  | 38 x 184 | 4.90 | 4.45 | 3.89 | 4.61 | 4.19 | 3.66 |
|  |  | 38 x 235 | 6.26 | 5.69 | 4.97 | 5.89 | 5.35 | 4.68 |
|  |  | 38 x 285 | 7.62 | 6.92 | 5.90 | 7.17 | 6.52 | 5.43 |
|  | No. 1 and No. 2 | 38 x 89 | 2.29 | 2.08 | 1.82 | 2.16 | 1.96 | 1.71 |
|  |  | 38 x 140 | 3.61 | 3.28 | 2.86 | 3.40 | 3.08 | 2.66 |
|  |  | 38 x 184 | 4.74 | 4.31 | 3.52 | 4.46 | 3.96 | 3.23 |
|  |  | 38 x 235 | 6.06 | 5.27 | 4.30 | 5.59 | 4.84 | 3.96 |
|  |  | 38 x 285 | 7.06 | 6.11 | 4.99 | 6.49 | 5.62 | 4.59 |
|  | No. 3 | 38 x 89 | 2.21 | 1.91 | 1.56 | 2.03 | 1.76 | 1.43 |
|  |  | 38 x 140 | 3.15 | 2.73 | 2.23 | 2.90 | 2.51 | 2.05 |
|  |  | 38 x 184 | 3.83 | 3.32 | 2.71 | 3.52 | 3.05 | 2.49 |
|  |  | 38 x 235 | 4.68 | 4.06 | 3.31 | 4.31 | 3.73 | 3.05 |
|  |  | 38 x 285 | 5.43 | 4.71 | 3.84 | 5.00 | 4.33 | 3.54 |
|  | Construction | 38 x 89 | 2.25 | 2.05 | 1.77 | 2.12 | 1.93 | 1.63 |
|  | Standard | 38 x 89 | 1.87 | 1.62 | 1.33 | 1.72 | 1.49 | 1.22 |
| Northern Species (includes any Canadian species covered by the NLGA Standard Grading Rules) | Select Structural | 38 x 89 | 2.12 | 1.93 | 1.68 | 1.99 | 1.81 | 1.58 |
|  |  | 38 x 140 | 3.33 | 3.03 | 2.65 | 3.14 | 2.85 | 2.49 |
|  |  | 38 x 184 | 4.38 | 3.98 | 3.33 | 4.12 | 3.75 | 3.07 |
|  |  | 38 x 235 | 5.60 | 4.99 | 4.08 | 5.27 | 4.59 | 3.75 |
|  |  | 38 x 285 | 6.69 | 5.79 | 4.73 | 6.15 | 5.33 | 4.35 |
|  | No. 1 and No. 2 | 38 x 89 | 2.07 | 1.88 | 1.62 | 1.95 | 1.77 | 1.49 |
|  |  | 38 x 140 | 3.26 | 2.84 | 2.32 | 3.02 | 2.61 | 2.13 |
|  |  | 38 x 184 | 3.99 | 3.46 | 2.82 | 3.67 | 3.18 | 2.60 |
|  |  | 38 x 235 | 4.88 | 4.23 | 3.45 | 4.49 | 3.89 | 3.17 |
|  |  | 38 x 285 | 5.66 | 4.90 | 4.00 | 5.21 | 4.51 | 3.68 |
|  | No. 3 | 38 x 89 | 1.77 | 1.53 | 1.25 | 1.63 | 1.41 | 1.15 |
|  |  | 38 x 140 | 2.52 | 2.19 | 1.78 | 2.32 | 2.01 | 1.64 |
|  |  | 38 x 184 | 3.07 | 2.66 | 2.17 | 2.82 | 2.45 | 2.00 |
|  |  | 38 x 235 | 3.76 | 3.25 | 2.66 | 3.45 | 2.99 | 2.44 |
|  |  | 38 x 285 | 4.36 | 3.77 | 3.08 | 4.01 | 3.47 | 2.83 |
|  | Construction | 38 x 89 | 2.01 | 1.74 | 1.42 | 1.85 | 1.60 | 1.31 |
|  | Standard | 38 x 89 | 1.50 | 1.30 | 1.06 | 1.38 | 1.19 | 0.98 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |

Table A-8

Maximum Spans for Built-up Floor Beams Supporting not more than One Floor(1)

Forming Part of Sentence 9.23.4.2.(3)

| Commercial Designation | Grade | Supported Length, mm(4)(5) | Maximum Span, m(2)(3) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Size of Built-up Beam, mm |  |  |  |  |  |  |  |  |
|  |  |  | 3 - | 4 - | 5 - | 3 - | 4 - | 5 - | 3 - | 4 - | 5 - |
|  |  |  | 38 x | 38 x | 38 x | 38 x | 38 x | 38 x | 38 x | 38 x | 38 x |
|  |  |  | 184 | 184 | 184 | 235 | 235 | 235 | 286 | 286 | 286 |
| Douglas Fir – Larch (includes Douglas Fir and Western larch) | Select Structural | 2.4 | 3.84 | 4.43 | 4.96 | 4.70 | 5.42 | 6.06 | 5.45 | 6.29 | 7.03 |
|  |  | 3.0 | 3.43 | 3.97 | 4.43 | 4.20 | 4.85 | 5.42 | 4.87 | 5.63 | 6.29 |
|  |  | 3.6 | 3.14 | 3.62 | 4.05 | 3.83 | 4.43 | 4.95 | 4.45 | 5.14 | 5.74 |
|  |  | 4.2 | 2.90 | 3.35 | 3.75 | 3.55 | 4.10 | 4.58 | 4.12 | 4.76 | 5.32 |
|  |  | 4.8 | 2.72 | 3.14 | 3.51 | 3.32 | 3.83 | 4.29 | 3.85 | 4.45 | 4.97 |
|  |  | 5.4 | 2.56 | 2.96 | 3.31 | 3.13 | 3.61 | 4.04 | 3.63 | 4.19 | 4.69 |
|  |  | 6.0 | 2.43 | 2.80 | 3.14 | 2.97 | 3.43 | 3.83 | 3.34 | 3.98 | 4.45 |
|  | No. 1 and No. 2 | 2.4 | 2.99 | 3.45 | 3.86 | 3.66 | 4.22 | 4.72 | 4.24 | 4.90 | 5.48 |
|  |  | 3.0 | 2.67 | 3.09 | 3.45 | 3.27 | 3.78 | 4.22 | 3.79 | 4.38 | 4.90 |
|  |  | 3.6 | 2.44 | 2.82 | 3.15 | 2.98 | 3.45 | 3.85 | 3.46 | 4.00 | 4.47 |
|  |  | 4.2 | 2.26 | 2.61 | 2.92 | 2.76 | 3.19 | 3.57 | 3.21 | 3.70 | 4.14 |
|  |  | 4.8 | 2.11 | 2.44 | 2.73 | 2.59 | 2.98 | 3.34 | 3.00 | 3.46 | 3.87 |
|  |  | 5.4 | 1.99 | 2.30 | 2.57 | 2.44 | 2.81 | 3.15 | 2.83 | 3.27 | 3.65 |
|  |  | 6.0 | 1.89 | 2.18 | 2.44 | 2.31 | 2.67 | 2.98 | 2.68 | 3.10 | 3.46 |
| Hem – Fir (includes Western Hemlock and Amabilis Fir) | Select Structural | 2.4 | 3.78 | 4.37 | 4.88 | 4.62 | 5.34 | 5.97 | 5.37 | 6.20 | 6.93 |
|  |  | 3.0 | 3.38 | 3.91 | 4.37 | 4.14 | 4.78 | 5.34 | 4.80 | 5.54 | 6.20 |
|  |  | 3.6 | 3.09 | 3.57 | 3.99 | 3.78 | 4.36 | 4.87 | 4.35 | 5.06 | 5.66 |
|  |  | 4.2 | 2.86 | 3.30 | 3.69 | 3.39 | 4.04 | 4.51 | 3.81 | 4.68 | 5.24 |
|  |  | 4.8 | 2.55 | 3.09 | 3.45 | 3.03 | 3.78 | 4.22 | 3.40 | 4.35 | 4.90 |
|  |  | 5.4 | 2.31 | 2.91 | 3.25 | 2.74 | 3.50 | 3.98 | 3.09 | 3.93 | 4.62 |
|  |  | 6.0 | 2.12 | 2.70 | 3.09 | 2.52 | 3.20 | 3.78 | 2.84 | 3.59 | 4.35 |
|  | No. 1 and No. 2 | 2.4 | 3.14 | 3.62 | 4.05 | 3.83 | 4.43 | 4.95 | 4.45 | 5.14 | 5.74 |
|  |  | 3.0 | 2.80 | 3.24 | 3.62 | 3.43 | 3.96 | 4.43 | 3.98 | 4.60 | 5.14 |
|  |  | 3.6 | 2.56 | 2.96 | 3.31 | 3.13 | 3.61 | 4.04 | 3.63 | 4.19 | 4.69 |
|  |  | 4.2 | 2.37 | 2.74 | 3.06 | 2.90 | 3.35 | 3.74 | 3.36 | 3.88 | 4.34 |
|  |  | 4.8 | 2.22 | 2.56 | 2.86 | 2.71 | 3.13 | 3.50 | 3.15 | 3.63 | 4.06 |
|  |  | 5.4 | 2.09 | 2.41 | 2.70 | 2.56 | 2.95 | 3.30 | 2.97 | 3.42 | 3.83 |
|  |  | 6.0 | 1.98 | 2.29 | 2.56 | 2.42 | 2.80 | 3.13 | 2.81 | 3.25 | 3.63 |
| Spruce – Pine – Fir (includes Spruce (all species except Coast Sitka Spruce), Jack Pine, Lodgepole Pine, Balsam Fir and Alpine Fir) | Select Structural | 2.4 | 3.84 | 4.43 | 4.96 | 4.70 | 5.42 | 6.06 | 5.45 | 6.29 | 7.03 |
|  |  | 3.0 | 3.43 | 3.97 | 4.43 | 4.20 | 4.85 | 5.42 | 4.87 | 5.63 | 6.29 |
|  |  | 3.6 | 3.14 | 3.62 | 4.05 | 3.83 | 4.43 | 4.95 | 4.45 | 5.14 | 5.74 |
|  |  | 4.2 | 2.90 | 3.35 | 3.75 | 3.55 | 4.10 | 4.58 | 4.12 | 4.76 | 5.32 |
|  |  | 4.8 | 2.72 | 3.14 | 3.51 | 3.31 | 3.83 | 4.29 | 3.72 | 4.45 | 4.97 |
|  |  | 5.4 | 2.53 | 2.96 | 3.31 | 3.00 | 3.61 | 4.04 | 3.37 | 4.19 | 4.69 |
|  |  | 6.0 | 2.31 | 2.80 | 3.14 | 2.74 | 3.43 | 3.83 | 3.09 | 3.93 | 4.45 |
|  | No. 1 and No. 2 | 2.4 | 3.25 | 3.75 | 4.19 | 3.97 | 4.59 | 5.13 | 4.61 | 5.32 | 5.95 |
|  |  | 3.0 | 2.90 | 3.35 | 3.75 | 3.55 | 4.10 | 4.59 | 4.12 | 4.76 | 5.32 |
|  |  | 3.6 | 2.65 | 3.06 | 3.42 | 3.24 | 3.74 | 4.19 | 3.76 | 4.34 | 4.86 |
|  |  | 4.2 | 2.45 | 2.83 | 3.17 | 3.00 | 3.47 | 3.88 | 3.48 | 4.02 | 4.50 |
|  |  | 4.8 | 2.30 | 2.65 | 2.96 | 2.81 | 3.24 | 3.63 | 3.26 | 3.76 | 4.21 |
|  |  | 5.4 | 2.17 | 2.50 | 2.80 | 2.65 | 3.06 | 3.42 | 3.07 | 3.55 | 3.97 |
|  |  | 6.0 | 2.05 | 2.37 | 2.65 | 2.51 | 2.90 | 3.24 | 2.91 | 3.37 | 3.76 |
| Northern Species (includes any Canadian species covered by the NLGA Standard Grading Rules) | Select Structural | 2.4 | 3.08 | 3.55 | 3.97 | 3.76 | 4.35 | 4.86 | 4.37 | 5.04 | 5.64 |
|  |  | 3.0 | 2.75 | 3.18 | 3.55 | 3.37 | 3.89 | 4.35 | 3.91 | 4.51 | 5.04 |
|  |  | 3.6 | 2.51 | 2.90 | 3.24 | 3.07 | 3.55 | 3.97 | 3.57 | 4.12 | 4.60 |
|  |  | 4.2 | 2.33 | 2.69 | 3.00 | 2.85 | 3.29 | 3.67 | 3.30 | 3.81 | 4.26 |
|  |  | 4.8 | 2.18 | 2.51 | 2.81 | 2.66 | 3.07 | 3.44 | 3.09 | 3.57 | 3.99 |
|  |  | 5.4 | 2.05 | 2.37 | 2.65 | 2.51 | 2.90 | 3.24 | 2.91 | 3.36 | 3.76 |
|  |  | 6.0 | 1.95 | 2.25 | 2.51 | 2.38 | 2.75 | 3.07 | 2.76 | 3.19 | 3.57 |
|  | No. 1 and No. 2 | 2.4 | 2.61 | 3.01 | 3.36 | 3.19 | 3.68 | 4.11 | 3.70 | 4.27 | 4.77 |
|  |  | 3.0 | 2.33 | 2.69 | 3.01 | 2.85 | 3.29 | 3.68 | 3.31 | 3.82 | 4.27 |
|  |  | 3.6 | 2.13 | 2.46 | 2.75 | 2.60 | 3.00 | 3.36 | 3.02 | 3.49 | 3.90 |
|  |  | 4.2 | 1.97 | 2.27 | 2.54 | 2.41 | 2.78 | 3.11 | 2.80 | 3.23 | 3.61 |
|  |  | 4.8 | 1.84 | 2.13 | 2.38 | 2.25 | 2.60 | 2.91 | 2.61 | 3.02 | 3.38 |
|  |  | 5.4 | 1.74 | 2.01 | 2.24 | 2.12 | 2.45 | 2.74 | 2.47 | 2.85 | 3.18 |
|  |  | 6.0 | 1.65 | 1.90 | 2.13 | 2.02 | 2.33 | 2.60 | 2.34 | 2.70 | 3.02 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |

Notes to Table A-8:

(1) Spans apply only where the floors serve residential areas as described in Table 4.1.6.3., or the uniformly distributed live load on the floors does not exceed that specified for residential areas as described in Table 4.1.6.3.

(2) Spans are clear spans between supports. For total span, add two bearing lengths.

(3) Provide minimum 89 mm of bearing.

(4) Supported length means half the sum of the joists spans on both sides of the beam.

(5) Straight line interpolation may be used for other supported lengths.

Table A-9

Maximum Spans for Built-up Floor Beams Supporting not more than Two Floors(1)

Forming Part of Sentence 9.23.4.2.(3)

| Commercial Designation | Grade | Supported Length, mm(4)(5) | Maximum Span, m(2) (3) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Size of Built-up Beam, mm |  |  |  |  |  |  |  |  |
|  |  |  | 3 - | 4 - | 5 - | 3 - | 4 - | 5 - | 3 - | 4 - | 5 - |
|  |  |  | 38 x | 38 x | 38 x | 38 x | 38 x | 38 x | 38 x | 38 x | 38 x |
|  |  |  | 184 | 184 | 184 | 235 | 235 | 235 | 286 | 286 | 286 |
| Douglas Fir – Larch (includes Douglas Fir and Western Larch) | Select Structural | 2.4 | 2.91 | 3.36 | 3.76 | 3.56 | 4.11 | 4.60 | 4.13 | 4.77 | 5.34 |
|  |  | 3.0 | 2.61 | 3.01 | 3.36 | 3.19 | 3.68 | 4.11 | 3.70 | 4.27 | 4.77 |
|  |  | 3.6 | 2.38 | 2.75 | 3.07 | 2.87 | 3.36 | 3.76 | 3.23 | 3.90 | 4.36 |
|  |  | 4.2 | 2.13 | 2.54 | 2.84 | 2.53 | 3.11 | 3.48 | 2.85 | 3.61 | 4.04 |
|  |  | 4.8 | 1.91 | 2.38 | 2.66 | 2.27 | 2.87 | 3.25 | 2.56 | 3.23 | 3.77 |
|  |  | 5.4 | 1.74 | 2.19 | 2.51 | 2.07 | 2.60 | 3.07 | 2.34 | 2.93 | 3.52 |
|  |  | 6.0 | 1.60 | 2.01 | 2.38 | 1.91 | 2.39 | 2.87 | 2.17 | 2.70 | 3.23 |
|  | No. 1 and No. 2 | 2.4 | 2.27 | 2.62 | 2.93 | 2.77 | 3.20 | 3.58 | 3.22 | 3.72 | 4.16 |
|  |  | 3.0 | 2.03 | 2.34 | 2.62 | 2.48 | 2.86 | 3.20 | 2.88 | 3.32 | 3.72 |
|  |  | 3.6 | 1.85 | 2.14 | 2.39 | 2.26 | 2.62 | 2.92 | 2.63 | 3.03 | 3.39 |
|  |  | 4.2 | 1.71 | 1.98 | 2.21 | 2.10 | 2.42 | 2.71 | 2.43 | 2.81 | 3.14 |
|  |  | 4.8 | 1.60 | 1.85 | 2.07 | 1.96 | 2.26 | 2.53 | 2.28 | 2.63 | 2.94 |
|  |  | 5.4 | 1.51 | 1.75 | 1.95 | 1.85 | 2.14 | 2.39 | 2.15 | 2.48 | 2.77 |
|  |  | 6.0 | 1.43 | 1.66 | 1.85 | 1.75 | 2.03 | 2.26 | 2.04 | 2.35 | 2.63 |
| Hem – Fir (includes Western Hemlock and Amabilis Fir) | Select Structural | 2.4 | 2.87 | 3.31 | 3.70 | 3.42 | 4.05 | 4.53 | 3.83 | 4.70 | 5.26 |
|  |  | 3.0 | 2.38 | 2.96 | 3.31 | 2.83 | 3.61 | 4.05 | 3.18 | 4.05 | 4.70 |
|  |  | 3.6 | 2.05 | 2.61 | 3.02 | 2.43 | 3.09 | 3.70 | 2.75 | 3.47 | 4.19 |
|  |  | 4.2 | 1.81 | 2.29 | 2.77 | 2.15 | 2.72 | 3.28 | 2.44 | 3.06 | 3.68 |
|  |  | 4.8 | 1.63 | 2.05 | 2.47 | 1.94 | 2.43 | 2.93 | 2.20 | 2.75 | 3.29 |
|  |  | 5.4 | 1.49 | 1.86 | 2.23 | 1.78 | 2.22 | 2.65 | 2.02 | 2.50 | 2.99 |
|  |  | 6.0 | 1.37 | 1.71 | 2.05 | 1.65 | 2.04 | 2.43 | 1.88 | 2.31 | 2.75 |
|  | No. 1 and No. 2 | 2.4 | 2.38 | 2.75 | 3.07 | 2.91 | 3.36 | 3.76 | 3.38 | 3.90 | 4.36 |
|  |  | 3.0 | 2.13 | 2.46 | 2.75 | 2.60 | 3.00 | 3.36 | 3.02 | 3.49 | 3.90 |
|  |  | 3.6 | 1.94 | 2.24 | 2.51 | 2.38 | 2.74 | 3.07 | 2.75 | 3.18 | 3.56 |
|  |  | 4.2 | 1.80 | 2.08 | 2.32 | 2.15 | 2.54 | 2.84 | 2.44 | 2.95 | 3.29 |
|  |  | 4.8 | 1.63 | 1.94 | 2.17 | 1.94 | 2.38 | 2.66 | 2.20 | 2.75 | 3.08 |
|  |  | 5.4 | 1.49 | 1.83 | 2.05 | 1.78 | 2.22 | 2.50 | 2.02 | 2.50 | 2.91 |
|  |  | 6.0 | 1.37 | 1.71 | 1.94 | 1.65 | 2.04 | 2.38 | 1.88 | 2.31 | 2.75 |
| Spruce – Pine – Fir (includes Spruce (all species except Coast Sitka Spruce), Jack Pine, Lodgepole Pine, Balsam Fir and Alpine Fir) | Select Structural | 2.4 | 2.91 | 3.36 | 3.76 | 3.56 | 4.11 | 4.60 | 4.13 | 4.77 | 5.34 |
|  |  | 3.0 | 2.61 | 3.01 | 3.36 | 3.09 | 3.68 | 4.11 | 3.47 | 4.27 | 4.77 |
|  |  | 3.6 | 2.23 | 2.75 | 3.07 | 2.65 | 3.36 | 3.76 | 2.99 | 3.79 | 4.36 |
|  |  | 4.2 | 1.97 | 2.50 | 2.84 | 2.34 | 2.96 | 3.48 | 2.64 | 3.33 | 4.02 |
|  |  | 4.8 | 1.77 | 2.23 | 2.66 | 2.11 | 2.65 | 3.20 | 2.38 | 2.99 | 3.59 |
|  |  | 5.4 | 1.61 | 2.03 | 2.44 | 1.93 | 2.41 | 2.90 | 2.18 | 2.72 | 3.26 |
|  |  | 6.0 | 1.49 | 1.86 | 2.23 | 1.78 | 2.22 | 2.65 | 2.02 | 2.50 | 2.99 |
|  | No. 1 and No. 2 | 2.4 | 2.46 | 2.85 | 3.18 | 3.01 | 3.48 | 3.89 | 3.50 | 4.04 | 4.51 |
|  |  | 3.0 | 2.20 | 2.55 | 2.85 | 2.70 | 3.11 | 3.48 | 3.13 | 3.61 | 4.04 |
|  |  | 3.6 | 2.01 | 2.32 | 2.60 | 2.46 | 2.84 | 3.18 | 2.85 | 3.30 | 3.69 |
|  |  | 4.2 | 1.86 | 2.15 | 2.40 | 2.28 | 2.63 | 2.94 | 2.64 | 3.05 | 3.41 |
|  |  | 4.8 | 1.74 | 2.01 | 2.25 | 2.11 | 2.46 | 2.75 | 2.38 | 2.85 | 3.19 |
|  |  | 5.4 | 1.61 | 1.90 | 2.12 | 1.93 | 2.32 | 2.59 | 2.18 | 2.69 | 3.01 |
|  |  | 6.0 | 1.49 | 1.80 | 2.01 | 1.78 | 2.20 | 2.46 | 2.02 | 2.50 | 2.85 |
| Northern Species (includes any Canadian Species covered by the NLGA Standard Grading Rules) | Select Structural | 2.4 | 2.34 | 2.70 | 3.02 | 2.86 | 3.30 | 3.69 | 3.31 | 3.83 | 4.28 |
|  |  | 3.0 | 2.09 | 2.41 | 2.70 | 2.55 | 2.95 | 3.30 | 2.96 | 3.42 | 3.83 |
|  |  | 3.6 | 1.91 | 2.20 | 2.46 | 2.33 | 2.69 | 3.01 | 2.71 | 3.12 | 3.49 |
|  |  | 4.2 | 1.77 | 2.04 | 2.28 | 2.15 | 2.49 | 2.79 | 2.44 | 2.89 | 3.23 |
|  |  | 4.8 | 1.63 | 1.91 | 2.13 | 1.94 | 2.33 | 2.61 | 2.20 | 2.71 | 3.03 |
|  |  | 5.4 | 1.49 | 1.80 | 2.01 | 1.78 | 2.20 | 2.46 | 2.02 | 2.50 | 2.85 |
|  |  | 6.0 | 1.37 | 1.71 | 1.91 | 1.65 | 2.04 | 2.33 | 1.88 | 2.31 | 2.71 |
|  | No. 1 and No.2 | 2.4 | 1.98 | 2.28 | 2.55 | 2.42 | 2.79 | 3.12 | 2.81 | 3.24 | 3.62 |
|  |  | 3.0 | 1.77 | 2.04 | 2.28 | 2.16 | 2.50 | 2.79 | 2.51 | 2.90 | 3.24 |
|  |  | 3.6 | 1.61 | 1.86 | 2.08 | 1.97 | 2.28 | 2.55 | 2.29 | 2.65 | 2.96 |
|  |  | 4.2 | 1.49 | 1.73 | 1.93 | 1.83 | 2.11 | 2.36 | 2.12 | 2.45 | 2.74 |
|  |  | 4.8 | 1.40 | 1.61 | 1.81 | 1.71 | 1.97 | 2.21 | 1.98 | 2.29 | 2.56 |
|  |  | 5.4 | 1.32 | 1.52 | 1.70 | 1.61 | 1.86 | 2.08 | 1.87 | 2.16 | 2.42 |
|  |  | 6.0 | 1.25 | 1.44 | 1.61 | 1.53 | 1.77 | 1.97 | 1.77 | 2.05 | 2.29 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |

Notes to Table A-9:

(1) Spans apply only where the floors serve residential areas as described in Table 4.1.6.A., or the uniformly distributed live load on the floors does not exceed that specified for residential areas as described in Table 4.1.6.A.

(2) Spans are clear spans between supports. For total span, add two bearing lengths.

(3) Provide minimum 89 mm of bearing.

(4) Supported length means half the sum of the joists spans on both sides of the beam.

(5) Straight line interpolation may be used for other supported lengths.

Table A-10

Maximum Spans for Built-up Floor Beams Supporting not more than Three Floors(1)

Forming Part of Sentence 9.23.4.2.(3)

| Commercial Designation | Grade | Supported Length, mm(4)(5) | Maximum Span, m(2)(3) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Size of Built-up Beam, mm |  |  |  |  |  |  |  |  |
|  |  |  | 3- | 4- | 5- | 3- | 4- | 5- | 3- | 4- | 5- |
|  |  |  | 38 x | 38 x | 38 x | 38 x | 38 x | 38 x | 38 x | 38 x | 38 x |
|  |  |  | 184 | 184 | 184 | 235 | 235 | 235 | 286 | 286 | 286 |
| Douglas Fir – Larch (includes Douglas Fir and Western Larch) | Select Structural | 2.4 | 2.44 | 2.82 | 3.15 | 2.99 | 3.45 | 3.85 | 3.37 | 4.00 | 4.47 |
|  |  | 3.0 | 2.10 | 2.52 | 2.82 | 2.49 | 3.08 | 3.45 | 2.81 | 3.56 | 4.00 |
|  |  | 3.6 | 1.81 | 2.29 | 2.57 | 2.16 | 2.72 | 3.15 | 2.44 | 3.06 | 3.65 |
|  |  | 4.2 | 1.60 | 2.01 | 2.38 | 1.92 | 2.40 | 2.88 | 2.17 | 2.70 | 3.24 |
|  |  | 4.8 | 1.45 | 1.81 | 2.17 | 1.73 | 2.16 | 2.58 | 1.97 | 2.44 | 2.90 |
|  |  | 5.4 | 1.33 | 1.65 | 1.97 | 1.59 | 1.97 | 2.34 | 1.82 | 2.23 | 2.64 |
|  |  | 6.0 | 1.23 | 1.52 | 1.81 | 1.48 | 1.82 | 2.16 | 1.69 | 2.06 | 2.44 |
|  | No. 1 and No. 2 | 2.4 | 1.90 | 2.19 | 2.45 | 2.32 | 2.68 | 3.00 | 2.70 | 3.11 | 3.48 |
|  |  | 3.0 | 1.70 | 1.96 | 2.19 | 2.08 | 2.40 | 2.68 | 2.41 | 2.79 | 3.11 |
|  |  | 3.6 | 1.55 | 1.79 | 2.00 | 1.90 | 2.19 | 2.45 | 2.20 | 2.54 | 2.84 |
|  |  | 4.2 | 1.44 | 1.66 | 1.86 | 1.76 | 2.03 | 2.27 | 2.04 | 2.35 | 2.63 |
|  |  | 4.8 | 1.34 | 1.55 | 1.74 | 1.64 | 1.90 | 2.12 | 1.91 | 2.20 | 2.46 |
|  |  | 5.4 | 1.27 | 1.46 | 1.64 | 1.55 | 1.79 | 2.00 | 1.80 | 2.08 | 2.32 |
|  |  | 6.0 | 1.20 | 1.39 | 1.55 | 1.47 | 1.70 | 1.90 | 1.69 | 1.97 | 2.20 |
| Hem – Fir (includes Western Hemlock and Amabilis Fir) | Select Structural | 2.4 | 2.14 | 2.72 | 3.10 | 2.54 | 3.23 | 3.80 | 2.86 | 3.62 | 4.39 |
|  |  | 3.0 | 1.78 | 2.25 | 2.72 | 2.13 | 2.68 | 3.23 | 2.40 | 3.01 | 3.62 |
|  |  | 3.6 | 1.55 | 1.94 | 2.33 | 1.85 | 2.31 | 2.77 | 2.10 | 2.61 | 3.12 |
|  |  | 4.2 | 1.38 | 1.71 | 2.05 | 1.65 | 2.05 | 2.44 | 1.88 | 2.32 | 2.75 |
|  |  | 4.8 | 1.25 | 1.55 | 1.84 | 1.50 | 1.85 | 2.19 | 1.72 | 2.10 | 2.48 |
|  |  | 5.4 | 1.15 | 1.42 | 1.68 | 1.39 | 1.70 | 2.00 | 1.59 | 1.93 | 2.27 |
|  |  | 6.0 | 1.07 | 1.31 | 1.55 | 1.30 | 1.57 | 1.85 | 1.49 | 1.79 | 2.10 |
|  | No. 1 and No. 2 | 2.4 | 1.99 | 2.30 | 2.57 | 2.44 | 2.81 | 3.15 | 2.83 | 3.27 | 3.65 |
|  |  | 3.0 | 1.78 | 2.06 | 2.30 | 2.13 | 2.52 | 2.81 | 2.40 | 2.92 | 3.27 |
|  |  | 3.6 | 1.55 | 1.88 | 2.10 | 1.85 | 2.30 | 2.57 | 2.10 | 2.61 | 2.98 |
|  |  | 4.2 | 1.38 | 1.71 | 1.95 | 1.65 | 2.05 | 2.38 | 1.88 | 2.32 | 2.75 |
|  |  | 4.8 | 1.25 | 1.55 | 1.82 | 1.50 | 1.85 | 2.19 | 1.72 | 2.10 | 2.48 |
|  |  | 5.4 | 1.15 | 1.42 | 1.68 | 1.39 | 1.70 | 2.00 | 1.59 | 1.93 | 2.27 |
|  |  | 6.0 | 1.07 | 1.31 | 1.55 | 1.30 | 1.57 | 1.85 | 1.49 | 1.79 | 2.10 |
| Spruce – Pine – Fir (includes Spruce (all species except Coast Sitka Spruce), Jack Pine, Lodgepole Pine, Balsam Fir and Alpine Fir) | Select Structural | 2.4 | 2.33 | 2.82 | 3.15 | 2.77 | 3.45 | 3.85 | 3.12 | 3.96 | 4.47 |
|  |  | 3.0 | 1.94 | 2.46 | 2.82 | 2.31 | 2.92 | 3.45 | 2.61 | 3.29 | 3.96 |
|  |  | 3.6 | 1.68 | 2.11 | 2.55 | 2.00 | 2.51 | 3.02 | 2.27 | 2.83 | 3.40 |
|  |  | 4.2 | 1.49 | 1.86 | 2.24 | 1.78 | 2.22 | 2.66 | 2.03 | 2.51 | 2.99 |
|  |  | 4.8 | 1.35 | 1.68 | 2.00 | 1.62 | 2.00 | 2.39 | 1.84 | 2.27 | 2.69 |
|  |  | 5.4 | 1.24 | 1.53 | 1.82 | 1.49 | 1.83 | 2.17 | 1.70 | 2.08 | 2.46 |
|  |  | 6.0 | 1.15 | 1.42 | 1.68 | 1.39 | 1.70 | 2.00 | 1.59 | 1.93 | 2.27 |
|  | No. 1 and No. 2 | 2.4 | 2.06 | 2.38 | 2.67 | 2.52 | 2.92 | 3.26 | 2.93 | 3.38 | 3.78 |
|  |  | 3.0 | 1.85 | 2.13 | 2.38 | 2.26 | 2.61 | 2.92 | 2.61 | 3.03 | 3.38 |
|  |  | 3.6 | 1.68 | 1.95 | 2.18 | 2.00 | 2.38 | 2.66 | 2.27 | 2.76 | 3.09 |
|  |  | 4.2 | 1.49 | 1.80 | 2.02 | 1.78 | 2.20 | 2.46 | 2.03 | 2.51 | 2.86 |
|  |  | 4.8 | 1.35 | 1.68 | 1.88 | 1.62 | 2.00 | 2.30 | 1.84 | 2.27 | 2.67 |
|  |  | 5.4 | 1.24 | 1.53 | 1.78 | 1.49 | 1.83 | 2.17 | 1.70 | 2.08 | 2.46 |
|  |  | 6.0 | 1.15 | 1.42 | 1.68 | 1.39 | 1.70 | 2.00 | 1.59 | 1.93 | 2.27 |
| Northern Species (includes any Canadian species covered by the NLGA Standard Grading Rules) | Select Structural | 2.4 | 1.96 | 2.26 | 2.53 | 2.39 | 2.76 | 3.09 | 2.78 | 3.21 | 3.58 |
|  |  | 3.0 | 1.75 | 2.02 | 2.26 | 3.13 | 2.47 | 2.76 | 2.40 | 2.87 | 3.21 |
|  |  | 3.6 | 1.55 | 1.85 | 2.06 | 1.85 | 2.26 | 2.52 | 2.10 | 2.61 | 2.93 |
|  |  | 4.2 | 1.38 | 1.71 | 1.91 | 1.65 | 2.05 | 2.34 | 1.88 | 2.32 | 2.71 |
|  |  | 4.8 | 1.25 | 1.55 | 1.79 | 1.50 | 1.85 | 2.18 | 1.72 | 2.10 | 2.48 |
|  |  | 5.4 | 1.15 | 1.42 | 1.68 | 1.39 | 1.70 | 2.00 | 1.59 | 1.93 | 2.27 |
|  |  | 6.0 | 1.07 | 1.31 | 1.55 | 1.30 | 1.57 | 1.85 | 1.49 | 1.79 | 2.10 |
|  | No. 1 and No. 2 | 2.4 | 1.66 | 1.91 | 2.14 | 2.03 | 2.34 | 2.62 | 2.35 | 2.72 | 3.04 |
|  |  | 3.0 | 1.48 | 1.71 | 1.91 | 1.81 | 2.09 | 2.34 | 2.10 | 2.43 | 2.72 |
|  |  | 3.6 | 1.35 | 1.56 | 1.75 | 1.65 | 1.91 | 2.14 | 1.92 | 2.22 | 2.48 |
|  |  | 4.2 | 1.25 | 1.45 | 1.62 | 1.53 | 1.77 | 1.98 | 1.78 | 2.05 | 2.29 |
|  |  | 4.8 | 1.17 | 1.35 | 1.51 | 1.43 | 1.65 | 1.85 | 1.66 | 1.92 | 2.15 |
|  |  | 5.4 | 1.10 | 1.28 | 1.43 | 1.35 | 1.56 | 1.74 | 1.57 | 1.81 | 2.02 |
|  |  | 6.0 | 1.05 | 1.21 | 1.35 | 1.28 | 1.48 | 1.65 | 1.49 | 1.72 | 1.92 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |

Notes to Table A-10:

(1) Spans apply only where the floors serve residential areas as described in Table 4.1.6.3., or the uniformly distributed live load on the floors does not exceed that specified for residential areas as described in Table 4.1.6.3.

(2) Spans are clear spans between supports. For total span, add two bearing lengths.

(3) Provide minimum 89 mm of bearing.

(4) Supported length means half the sum of the joists spans on both sides of the beam.

(5) Straight line interpolation may be used for other supported lengths.

Table A-11

Maximum Spans for Glue-Laminated Floor Beams — 20f-E Grade(1)

Forming Part of Sentence 9.23.4.2.(3)

| Number of Storeys Supported | Beam Width, mm | Supported Length, m(6)(7) | Maximum Span, m(2) (3) (4) (5) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Beam Depth, mm |  |  |  |  |  |  |
|  |  |  | 228 | 266 | 304 | 342 | 380 | 418 | 456 |
| 1 | 80 | 2.4 | 4.32 | 5.04 | 5.76 | 6.48 | 7.20 | 7.92 | 8.64 |
|  |  | 3.0 | 3.87 | 4.51 | 5.15 | 5.80 | 6.44 | 7.09 | 7.73 |
|  |  | 3.6 | 3.53 | 4.12 | 4.70 | 5.29 | 5.88 | 6.47 | 7.06 |
|  |  | 4.2 | 3.27 | 3.81 | 4.36 | 4.90 | 5.44 | 5.99 | 6.53 |
|  |  | 4.8 | 3.06 | 3.57 | 4.07 | 4.58 | 5.09 | 5.60 | 6.11 |
|  |  | 5.4 | 2.88 | 3.36 | 3.84 | 4.32 | 4.80 | 5.28 | 5.76 |
|  |  | 6.0 | 2.73 | 3.19 | 3.64 | 4.10 | 4.56 | 5.01 | 5.47 |
|  | 130 | 2.4 | 5.51 | 6.43 | 7.35 | 8.26 | 9.18 | 10.10 | 11.02 |
|  |  | 3.0 | 4.93 | 5.75 | 6.57 | 7.39 | 8.21 | 9.03 | 9.86 |
|  |  | 3.6 | 4.50 | 5.25 | 6.00 | 6.75 | 7.50 | 8.25 | 9.00 |
|  |  | 4.2 | 4.16 | 4.86 | 5.55 | 6.25 | 6.94 | 7.64 | 8.33 |
|  |  | 4.8 | 3.90 | 4.54 | 5.19 | 5.84 | 6.49 | 7.14 | 7.79 |
|  |  | 5.4 | 3.67 | 4.28 | 4.90 | 5.51 | 6.12 | 6.73 | 7.35 |
|  |  | 6.0 | 3.48 | 4.07 | 4.65 | 5.23 | 5.81 | 6.39 | 6.97 |
| 2 | 80 | 2.4 | 3.28 | 3.83 | 4.37 | 4.92 | 5.47 | 6.01 | 6.56 |
|  |  | 3.0 | 2.93 | 3.42 | 3.91 | 4.40 | 4.89 | 5.38 | 5.87 |
|  |  | 3.6 | 2.68 | 3.12 | 3.57 | 4.02 | 4.46 | 4.91 | 5.36 |
|  |  | 4.2 | 2.48 | 2.89 | 3.31 | 3.72 | 4.13 | 4.54 | 4.96 |
|  |  | 4.8 | 2.32 | 2.71 | 3.09 | 3.48 | 3.86 | 4.25 | 4.64 |
|  |  | 5.4 | 2.19 | 2.55 | 2.91 | 3.28 | 3.64 | 4.01 | 4.37 |
|  |  | 6.0 | 2.07 | 2.42 | 2.77 | 3.11 | 3.46 | 3.80 | 4.15 |
|  | 130 | 2.4 | 4.18 | 4.88 | 5.57 | 6.27 | 6.97 | 7.66 | 8.36 |
|  |  | 3.0 | 3.74 | 4.36 | 4.99 | 5.61 | 6.23 | 6.85 | 7.48 |
|  |  | 3.6 | 3.41 | 3.98 | 4.55 | 5.12 | 5.69 | 6.26 | 6.83 |
|  |  | 4.2 | 3.16 | 3.69 | 4.21 | 4.74 | 5.27 | 5.79 | 6.32 |
|  |  | 4.8 | 2.96 | 3.45 | 3.94 | 4.43 | 4.93 | 5.42 | 5.91 |
|  |  | 5.4 | 2.79 | 3.25 | 3.72 | 4.18 | 4.64 | 5.11 | 5.57 |
|  |  | 6.0 | 2.64 | 3.08 | 3.53 | 3.97 | 4.41 | 4.85 | 5.29 |
| 3 | 80 | 2.4 | 2.75 | 3.21 | 3.66 | 4.12 | 4.58 | 5.04 | 5.50 |
|  |  | 3.0 | 2.46 | 2.87 | 3.28 | 3.69 | 4.10 | 4.51 | 4.92 |
|  |  | 3.6 | 2.24 | 2.62 | 2.99 | 3.37 | 3.74 | 4.11 | 4.49 |
|  |  | 4.2 | 2.08 | 2.42 | 2.77 | 3.12 | 3.46 | 3.81 | 4.15 |
|  |  | 4.8 | 1.94 | 2.27 | 2.59 | 2.91 | 3.24 | 3.56 | 3.89 |
|  |  | 5.4 | 1.83 | 2.14 | 2.44 | 2.75 | 3.05 | 3.36 | 3.66 |
|  |  | 6.0 | 1.74 | 2.03 | 2.32 | 2.61 | 2.90 | 3.19 | 3.48 |
|  | 130 | 2.4 | 3.50 | 4.09 | 4.67 | 5.25 | 5.84 | 6.42 | 7.01 |
|  |  | 3.0 | 3.13 | 3.66 | 4.18 | 4.70 | 5.22 | 5.74 | 6.27 |
|  |  | 3.6 | 2.86 | 3.34 | 3.81 | 4.29 | 4.77 | 5.24 | 5.72 |
|  |  | 4.2 | 2.65 | 3.09 | 3.53 | 3.97 | 4.41 | 4.85 | 5.30 |
|  |  | 4.8 | 2.48 | 2.89 | 3.30 | 3.72 | 4.13 | 4.54 | 4.95 |
|  |  | 5.4 | 2.34 | 2.72 | 3.11 | 3.50 | 3.89 | 4.28 | 4.67 |
|  |  | 6.0 | 2.22 | 2.58 | 2.95 | 3.32 | 3.69 | 4.06 | 4.43 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |

Notes to Table A-11:

(1) Spans apply only where the floors serve residential areas as described in Table 4.1.6.3., or the uniformly distributed live load on the floor does not exceed that specified for residential areas as described in Table 4.1.6.3.

(2	) Spans are valid for glued-laminated timber conforming to CAN/CSA-O122-M and CAN/CSA-O177-M.

(3) Spans are clear spans between supports. For total span, add two bearing lengths.

(4) Provide a minimum bearing length of 89 mm. (Alternatively, the bearing length may be designed in accordance with Part 4.)

(5) Top edge of beam assumed to be fully laterally supported by joists.

(6) Supported length means half the sum of the joist spans on both sides of the beam.

(7) Straight line interpolation may be used for other supported lengths.

Table A-12

Maximum Spans for Built-up Roof Ridge Beams — No. 1 or No. 2 Grade

Forming Part of Sentence 9.23.4.2.(4)

| Commercial Designation | Beam Size, mm | Maximum Span, m(1) (2) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Specified Snow Load, kPa |  |  |  |  |
|  |  | 1.0 | 1.5 | 2.0 | 2.5 | 3.0 |
| Douglas Fir – Larch (includes Douglas Fir and Western Larch) | 3 – 38 x 184 | 2.42 | 2.08 | 1.86 | 1.69 | 1.56 |
|  | 4 – 38 x 184 | 2.80 | 2.41 | 2.14 | 1.95 | 1.80 |
|  | 5 – 38 x 184 | 3.13 | 2.69 | 2.40 | 2.18 | 2.01 |
|  | 3 – 38 x 235 | 2.95 | 2.55 | 2.27 | 2.06 | 1.91 |
|  | 4 – 38 x 235 | 3.42 | 2.94 | 2.62 | 2.38 | 2.20 |
|  | 5 – 38 x 235 | 3.83 | 3.29 | 2.93 | 2.67 | 2.46 |
|  | 3 – 38 x 286 | 3.44 | 2.96 | 2.63 | 2.40 | 2.21 |
|  | 4 – 38 x 286 | 3.97 | 3.41 | 3.04 | 2.77 | 2.56 |
|  | 5 – 38 x 286 | 4.44 | 3.82 | 3.40 | 3.09 | 2.86 |
| Hem – Fir (includes Western Hemlock and Amabilis Fir) | 3 – 38 x 184 | 2.54 | 2.18 | 1.95 | 1.77 | 1.64 |
|  | 4 – 38 x 184 | 2.93 | 2.52 | 2.25 | 2.05 | 1.89 |
|  | 5 – 38 x 184 | 3.28 | 2.82 | 2.51 | 2.29 | 2.11 |
|  | 3 – 38 x 235 | 3.11 | 2.67 | 2.38 | 2.17 | 2.00 |
|  | 4 – 38 x 235 | 3.59 | 3.08 | 2.75 | 2.50 | 2.31 |
|  | 5 – 38 x 235 | 4.01 | 3.45 | 3.07 | 2.80 | 2.58 |
|  | 3 – 38 x 286 | 3.61 | 3.10 | 2.76 | 2.51 | 2.32 |
|  | 4 – 38 x 286 | 4.16 | 3.58 | 3.19 | 2.90 | 2.68 |
|  | 5 – 38 x 286 | 4.66 | 4.00 | 3.56 | 3.24 | 3.00 |
| Spruce – Pine – Fir (includes Spruce (all species except Coast Sitka Spruce), Jack Pine, Lodgepole Pine, Balsam Fir and Alpine Fir) | 3 – 38 x 184 | 2.63 | 2.26 | 2.02 | 1.83 | 1.69 |
|  | 4 – 38 x 184 | 3.04 | 2.61 | 2.33 | 2.12 | 1.96 |
|  | 5 – 38 x 184 | 3.40 | 2.92 | 2.60 | 2.37 | 2.19 |
|  | 3 – 38 x 235 | 3.22 | 2.77 | 2.46 | 2.24 | 2.07 |
|  | 4 – 38 x 235 | 3.72 | 3.20 | 2.85 | 2.59 | 2.39 |
|  | 5 – 38 x 235 | 4.16 | 3.57 | 3.18 | 2.90 | 2.68 |
|  | 3 – 38 x 286 | 3.73 | 3.21 | 2.86 | 2.60 | 2.40 |
|  | 4 – 38 x 286 | 4.31 | 3.71 | 3.30 | 3.01 | 2.78 |
|  | 5 – 38 x 286 | 4.82 | 4.15 | 3.69 | 3.36 | 3.10 |
| Northern Species (includes any Canadian species covered by the NLGA Standard Grading Rules) | 3 – 38 x 184 | 2.11 | 1.82 | 1.62 | 1.47 | 1.36 |
|  | 4 – 38 x 184 | 2.44 | 2.10 | 1.87 | 1.70 | 1.57 |
|  | 5 – 38 x 184 | 2.73 | 2.34 | 2.08 | 1.90 | 1.76 |
|  | 3 – 38 x 235 | 2.58 | 2.22 | 1.98 | 1.80 | 1.66 |
|  | 4 – 38 x 235 | 2.98 | 2.56 | 2.28 | 2.08 | 1.92 |
|  | 5 – 38 x 235 | 3.33 | 2.87 | 2.55 | 2.32 | 2.15 |
|  | 3 – 38 x 286 | 3.00 | 2.58 | 2.29 | 2.09 | 1.93 |
|  | 4 – 38 x 286 | 3.46 | 2.98 | 2.65 | 2.41 | 2.23 |
|  | 5 – 38 x 286 | 3.87 | 3.33 | 2.96 | 2.70 | 2.49 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 |

Notes to Table A-12:

(1) The spans are calculated based on a maximum supported length of 4.9 m where supported length means half the sum of the rafter, joist or truss span on both sides of the beam. Spans may be increased by 5% for supported lengths not more than 4.3 m, or by 10% for supported lengths not more than 3.7 m.

(2) Provide minimum 89 mm bearing.

Table A-13

Maximum Spans for Douglas Fir – Larch Lintels — No. 1 or No. 2 Grade Non-Structural Sheathing

Forming Part of Sentences 9.23.12.3.(1) and (3)

| Lintel Supporting | Lintel Size, mm(4) | Maximum Span, m(1) (2) (3) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Exterior Walls |  |  |  |  | Interior Walls |
|  |  | Specified Snow Load, kPa |  |  |  |  |  |
|  |  | 1.0 | 1.5 | 2.0 | 2.5 | 3.0 |  |
|  | 2 – 38 x 89 |  |  |  |  |  | 1.25 |
|  | 2 – 38 x 140 |  |  |  |  |  | 1.78 |
| Limited attic storage and ceiling | 2 – 38 x 184 | This Area Intentionally Left Blank |  |  |  |  | 2.17 |
|  | 2 – 38 x 235 |  |  |  |  |  | 2.65 |
|  | 2 – 38 x 286 |  |  |  |  |  | 3.08 |
|  | 2 – 38 x 89 | 1.25 | 1.07 | 0.96 | 0.87 | 0.80 | 0.87 |
|  | 2 – 38 x 140 | 1.78 | 1.53 | 1.36 | 1.24 | 1.15 | 1.24 |
| Roof and ceiling only | 2 – 38 x 184 | 2.17 | 1.86 | 1.66 | 1.51 | 1.40 | 1.51 |
|  | 2 – 38 x 235 | 2.65 | 2.28 | 2.03 | 1.85 | 1.71 | 1.85 |
|  | 2 – 38 x 286 | 3.08 | 2.64 | 2.35 | 2.14 | 1.98 | 2.14 |
|  | 2 – 38 x 89 | 0.96 | 0.88 | 0.82 | 0.77 | 0.73 | 0.68 |
|  | 2 – 38 x 140 | 1.37 | 1.26 | 1.17 | 1.10 | 1.04 | 0.97 |
| Roof, ceiling and 1 storey(5) | 2 – 38 x 184 | 1.67 | 1.53 | 1.42 | 1.34 | 1.26 | 1.18 |
|  | 2 – 38 x 235 | 2.04 | 1.88 | 1.74 | 1.63 | 1.54 | 1.44 |
|  | 2 – 38 x 286 | 2.37 | 2.18 | 2.02 | 1.90 | 1.79 | 1.67 |
|  | 2 – 38 x 89 | 0.86 | 0.81 | 0.77 | 0.73 | 0.70 | 0.61 |
|  | 2 – 38 x 140 | 1.23 | 1.16 | 1.09 | 1.04 | 0.99 | 0.87 |
| Roof, ceiling and 2 storeys(5) | 2 – 38 x 184 | 1.50 | 1.41 | 1.33 | 1.27 | 1.21 | 1.06 |
|  | 2 – 38 x 235 | 1.84 | 1.72 | 1.63 | 1.55 | 1.48 | 1.30 |
|  | 2 – 38 x 286 | 2.13 | 2.00 | 1.89 | 1.80 | 1.72 | 1.51 |
|  | 2 – 38 x 89 | 0.81 | 0.77 | 0.73 | 0.71 | 0.68 | 0.57 |
|  | 2 – 38 x 140 | 1.15 | 1.10 | 1.05 | 1.01 | 0.97 | 0.82 |
| Roof, ceiling and 3 storeys(5) | 2 – 38 x 184 | 1.40 | 1.33 | 1.28 | 1.22 | 1.18 | 1.00 |
|  | 2 – 38 x 235 | 1.71 | 1.63 | 1.56 | 1.50 | 1.44 | 1.22 |
|  | 2 – 38 x 286 | 1.99 | 1.89 | 1.81 | 1.74 | 1.67 | 1.41 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |

Notes to Table A-13:

(1) Spans are calculated based on a maximum supported joist or rafter length of 4.9 m and a maximum supported truss length of 9.8 m. Spans may be increased by 5% for supported lengths not more than 4.3 m, or by 10% for supported lengths not more than 3.7 m. Supported length means half the span of the longest supported member.

(2)	 If floor joists span the full width of the building without support, lintel spans shall be reduced by 15% for Roof, ceiling and one storey, by 20% for Roof, ceiling and two storeys, and by 25% for Roof, ceiling and three storeys.

(3)	 For ends of lintels fully supported by the wall, provide minimum 38 mm of bearing for lintel spans up to 3 m, or minimum 76 mm or bearing for lintel spans greater than 3 m.

(4) A single piece of 89 mm thick lumber may be used in lieu of 2 pieces of 38 mm thick lumber on edge.

(5) Spans apply only where the floors serve residential areas as described in Table 4.1.6.3., or the uniformly distributed live load on the floor does not exceed that specified for residential areas as described in Table 4.1.6.3.

Table A-14

Maximum Spans for Douglas Fir  – Larch Lintels — No. 1 or No. 2 Grade Structural Sheathing(1)

Forming Part of Sentences 9.23.12.3.(1) and (3)

| Lintel Supporting | Lintel Size, mm(5) | Maximum Span, m(2)(3)(4) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Exterior Walls |  |  |  |  |
|  |  | Specified Snow Load, kPa |  |  |  |  |
|  |  | 1.0 | 1.5 | 2.0 | 2.5 | 3.0 |
|  | 2 – 38 x 89 | 1.46 | 1.25 | 1.12 | 1.02 | 0.94 |
|  | 2 – 38 x 140 | 2.08 | 1.79 | 1.59 | 1.45 | 1.34 |
| Roof and ceiling only | 2 – 38 x 184 | 2.53 | 2.18 | 1.94 | 1.76 | 1.63 |
|  | 2 – 38 x 235 | 3.09 | 2.66 | 2.37 | 2.16 | 1.99 |
|  | 2 – 38 x 286 | 3.59 | 3.09 | 2.75 | 2.50 | 2.31 |
|  | 2 – 38 x 89 | 1.12 | 1.03 | 0.96 | 0.90 | 0.85 |
|  | 2 – 38 x 140 | 1.60 | 1.47 | 1.37 | 1.28 | 1.21 |
| Roof, ceiling and 1 storey(6) | 2 – 38 x 184 | 1.95 | 1.79 | 1.66 | 1.56 | 1.47 |
|  | 2 – 38 x 235 | 2.39 | 2.19 | 2.03 | 1.91 | 1.80 |
|  | 2 – 38 x 286 | 2.77 | 2.54 | 2.36 | 2.21 | 2.09 |
|  | 2 – 38 x 89 | 1.01 | 0.95 | 0.90 | 0.85 | 0.81 |
|  | 2 – 38 x 140 | 1.44 | 1.35 | 1.28 | 1.21 | 1.16 |
| Roof, ceiling and 2 storeys(6) | 2 – 38 x 184 | 1.75 | 1.64 | 1.55 | 1.48 | 1.41 |
|  | 2 – 38 x 235 | 2.14 | 2.01 | 1.90 | 1.81 | 1.73 |
|  | 2 – 38 x 286 | 2.49 | 2.33 | 2.21 | 2.10 | 2.00 |
|  | 2 – 38 x 89 | 0.94 | 0.90 | 0.86 | 0.82 | 0.79 |
|  | 2 – 38 x 140 | 1.35 | 1.28 | 1.22 | 1.18 | 1.13 |
| Roof, ceiling and 3 storeys(6) | 2 – 38 x 184 | 1.64 | 1.56 | 1.49 | 1.43 | 1.38 |
|  | 2 – 38 x 235 | 2.00 | 1.91 | 1.82 | 1.75 | 1.68 |
|  | 2 – 38 x 286 | 2.32 | 2.21 | 2.11 | 2.03 | 1.95 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 |

Notes to Table A-14:

(1) A minimum 9.5 mm thick structural panel conforming to CSA O121-M, CSA O151-M, CAN/CSA-O325.0 or CAN/CSA-O437.0 shall be fastened with at least 2 rows of fasteners conforming to Table 9.23.3.5 to the exterior face of the lintel, and a single row to the top plates and studs.

(2) Spans are calculated based on a maximum supported joist or rafter length of 4.9 m and a maximum supported truss length of 9.8 m. Spans may be increased by 5% for supported lengths not more than 4.3 m, or by 10% for supported lengths not more than 3.7 m. Supported length means half the span of the longest supported members.

(3) If floor joists span the full width of the building without support, lintels spans shall be reduced by 15% for Roof, ceiling and 1 storey, by 20% for Roof, ceiling and 2 storeys, and by 25% for Roof, ceiling and three storeys.

(4) For ends of lintels fully supported by walls, provide minimum 38 mm of bearing for lintel spans up to 3 m, or minimum 76 mm of bearing for lintel spans greater than 3 m.

(5) A single piece of 89 mm thick lumber may be used in lieu of 2 pieces of 38 mm thick lumber on edge.

(6) Spans apply only where the floors serve residential areas as described in Table 4.1.6.3., or the uniformly distributed live load on the floor does not exceed that specified for residential areas as described in Table 4.1.6.3.

Table A-15

Maximum Spans for Hem – Fir Lintels — No. 1 or No. 2 Grade — Non-Structural Sheathing

Forming Part of Sentences 9.23.12.3.(1) and (3)

| Lintel Supporting | Lintel Size, mm (4) | Maximum Span, m(1) (2) (3) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Exterior Walls |  |  |  |  | Interior Walls |
|  |  | Specified Snow Load, kPa |  |  |  |  |  |
|  |  | 1.0 | 1.5 | 2.0 | 2.5 | 3.0 |  |
|  | 2 – 38 x 89 |  |  |  |  |  | 1.31 |
|  | 2 – 38 x 140 |  |  |  |  |  | 1.87 |
| Limited attic storage and ceiling | 2 – 38 x 184 | This Area Intentionally Left Blank |  |  |  |  | 2.27 |
|  | 2 – 38 x 235 |  |  |  |  |  | 2.78 |
|  | 2 – 38 x 286 |  |  |  |  |  | 3.23 |
|  | 2 – 38 x 89 | 1.31 | 1.13 | 1.00 | 0.91 | 0.84 | 0.91 |
|  | 2 – 38 x 140 | 1.87 | 1.61 | 1.43 | 1.30 | 1.20 | 1.30 |
| Roof and ceiling only | 2 – 38 x 184 | 2.27 | 1.95 | 1.74 | 1.58 | 1.42 | 1.58 |
|  | 2 – 38 x 235 | 2.78 | 2.39 | 2.13 | 1.92 | 1.71 | 1.92 |
|  | 2 – 38 x 286 | 3.23 | 2.77 | 2.47 | 2.17 | 1.94 | 2.17 |
|  | 2 – 38 x 89 | 1.01 | 0.93 | 0.86 | 0.81 | 0.76 | 0.69 |
|  | 2 – 38 x 140 | 1.44 | 1.32 | 1.23 | 1.14 | 1.05 | 0.95 |
| Roof, ceiling and 1 storey(5) | 2 – 38 x 184 | 1.75 | 1.61 | 1.47 | 1.34 | 1.23 | 1.12 |
|  | 2 – 38 x 235 | 2.14 | 1.96 | 1.76 | 1.60 | 1.48 | 1.35 |
|  | 2 – 38 x 286 | 2.49 | 2.22 | 2.00 | 1.82 | 1.69 | 1.55 |
|  | 2 – 38 x 89 | 0.91 | 0.85 | 0.80 | 0.76 | 0.72 | 0.60 |
|  | 2 – 38 x 140 | 1.29 | 1.21 | 1.13 | 1.05 | 0.98 | 0.82 |
| Roof, ceiling and 2 storeys(5) | 2 – 38 x 184 | 1.57 | 1.44 | 1.33 | 1.24 | 1.16 | 0.98 |
|  | 2 – 38 x 235 | 1.90 | 1.73 | 1.60 | 1.49 | 1.40 | 1.19 |
|  | 2 – 38 x 286 | 2.15 | 1.97 | 1.82 | 1.70 | 1.60 | 1.37 |
|  | 2 – 38 x 89 | 0.85 | 0.81 | 0.77 | 0.74 | 0.69 | 0.55 |
|  | 2 – 38 x 140 | 1.21 | 1.14 | 1.06 | 1.00 | 0.95 | 0.76 |
| Roof, ceiling and 3 storeys(5) | 2 – 38 x 184 | 1.43 | 1.33 | 1.25 | 1.18 | 1.12 | 0.91 |
|  | 2 – 38 x 235 | 1.72 | 1.60 | 1.50 | 1.42 | 1.35 | 1.10 |
|  | 2 – 38 x 286 | 1.95 | 1.82 | 1.72 | 1.63 | 1.55 | 1.27 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |

Notes to Table A-15:

(1) Spans are calculated based on a maximum supported joist or rafter length of 4.9 m and a maximum supported truss length of 9.8 m. Spans may be increased by 5% for supported lengths not more than 4.3 m, or by 10% for supported lengths not more than 3.7 m. Supported length means half the span of the longest supported member.

(2) If floor joists span the full width of the building without support, lintels spans shall be reduced by 15% for Roof, ceiling and 1 storey, by 20% for Roof, ceiling and 2 storeys, and by 25% for Roof, ceiling and 3 storeys.

(3) For ends of lintels fully supported by walls, provide minimum 38 mm of bearing for lintel spans up to 3 m, or minimum 76 mm of bearing for lintel spans greater than 3 m.

(4) A single piece of 89 mm thick lumber may be used in lieu of 2 pieces of 38 mm thick lumber on edge.

(5) Spans apply only where the floors serve residential areas as described in Table 4.1.6.3., or the uniformly distributed live load on the floor does not exceed that specified for residential areas as described in Table 4.1.6.3.

Table A-16

Maximum Spans for Hem – Fir Lintels — No. 1 or No. 2 Grade — Structural Sheathing(1)

Forming Part of Sentences 9.23.12.3.(1) and (3)

| Lintel Supporting | Lintel Size mm,(5) | Maximum Span, m(2) (3) (4) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Exterior Walls |  |  |  |  |
|  |  | Specified Snow Load, kPa |  |  |  |  |
|  |  | 1.0 | 1.5 | 2.0 | 2.5 | 3.0 |
|  | 2 – 38 x 89 | 1.47 | 1.29 | 1.17 | 1.07 | 0.98 |
|  | 2 – 38 x 140 | 2.18 | 1.88 | 1.67 | 1.52 | 1.40 |
| Roof and ceiling only | 2 – 38 x 184 | 2.65 | 2.28 | 2.03 | 1.85 | 1.71 |
|  | 2 – 38 x 235 | 3.25 | 2.79 | 2.49 | 2.26 | 2.08 |
|  | 2 – 38 x 286 | 3.77 | 3.24 | 2.88 | 2.62 | 2.35 |
|  | 2 – 38 x 89 | 1.18 | 1.08 | 1.00 | 0.94 | 0.89 |
|  | 2 – 38 x 140 | 1.68 | 1.54 | 1.43 | 1.34 | 1.27 |
| Roof, ceiling and 1 storey(6) | 2 – 38 x 184 | 2.05 | 1.88 | 1.74 | 1.63 | 1.49 |
|  | 2 – 38 x 235 | 2.50 | 2.30 | 2.13 | 1.94 | 1.78 |
|  | 2 – 38 x 286 | 2.91 | 2.66 | 2.42 | 2.20 | 2.03 |
|  | 2 – 38 x 89 | 1.06 | 0.99 | 0.94 | 0.89 | 0.85 |
|  | 2 – 38 x 140 | 1.51 | 1.42 | 1.34 | 1.27 | 1.19 |
| Roof, ceiling and 2 storeys(6) | 2 – 38 x 184 | 1.84 | 1.73 | 1.62 | 1.50 | 1.40 |
|  | 2 – 38 x 235 | 2.25 | 2.11 | 1.93 | 1.79 | 1.68 |
|  | 2 – 38 x 286 | 2.61 | 2.38 | 2.19 | 2.03 | 1.91 |
|  | 2 – 38 x 89 | 0.99 | 0.94 | 0.90 | 0.86 | 0.83 |
|  | 2 – 38 x 140 | 1.41 | 1.34 | 1.28 | 1.22 | 1.15 |
| Roof, ceiling and 3 storeys(6) | 2 – 38 x 184 | 1.72 | 1.62 | 1.52 | 1.43 | 1.35 |
|  | 2 – 38 x 235 | 2.09 | 1.94 | 1.81 | 1.71 | 1.62 |
|  | 2 – 38 x 286 | 2.37 | 2.20 | 2.06 | 1.94 | 1.84 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 |

Notes to Table A-16:

(1) A minimum 9.5 mm thick structural panel conforming to CSA O121-M, CSA O151-M, CAN/CSA-O325.0 or CAN/CSA-O437.0 shall be fastened with at least 2 rows of fasteners conforming to Table 9.23.3.5 to the exterior face of the lintel, and a single row to the top plates and studs.

(2) Spans are calculated based on a maximum supported joist or rafter length of 4.9 m and a maximum supported truss length of 9.8 m. Spans may be increased by 5% for supported lengths not more than 4.3 m, or by 10% for supported lengths not more than 3.7 m. Supported length means half the span of the longest supported member.

(3) If floor joists span the full width of the building without support, lintels spans shall be reduced by 15% for Roof, ceiling and 1 storey, by 20% for Roof, ceiling and 2 storeys, and by 25% for Roof, ceiling and 3 storeys.

(4) For ends of lintels fully supported by walls, provide minimum 38 mm of bearing for lintel spans up to 3 m, or minimum 76 mm of bearing for lintel spans greater than 3 m.

(5) A single piece of 89 mm thick lumber may be used in lieu of 2 pieces of 38 mm thick lumber on edge.

(6) Spans apply only where the floors serve residential areas as described in Table 4.1.6.3., or the uniformly distributed live load on the floor does not exceed that specified for residential areas as described in Table 4.1.6.3.

Table A-17

Maximum Spans for Spruce – Pine – Fir Lintels — No. 1 or No. 2 Grade Non-Structural Sheathing

Forming Part of Sentences 9.23.12.3.(1) and (3)

| Lintel Supporting | Lintel Size, mm (4) | Maximum Span, m(1) (2) (3) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Exterior Walls |  |  |  |  | Interior Walls |
|  |  | Specified Snow Load, kPa |  |  |  |  |  |
|  |  | 1.0 | 1.5 | 2.0 | 2.5 | 3.0 |  |
|  | 2 – 38 x 89 |  |  |  |  |  | 1.27 |
|  | 2 – 38 x 140 |  |  |  |  |  | 1.99 |
| Limited attic storage and ceiling | 2 – 38 x 184 | This Area Intentionally Left Blank |  |  |  |  | 2.51 |
|  | 2 – 38 x 235 |  |  |  |  |  | 3.07 |
|  | 2 – 38 x 286 |  |  |  |  |  | 3.57 |
|  | 2 – 38 x 89 | 1.27 | 1.11 | 1.01 | 0.93 | 0.87 | 0.93 |
|  | 2 – 38 x 140 | 1.93 | 1.66 | 1.48 | 1.35 | 1.25 | 1.35 |
| Roof and ceiling only | 2 – 38 x 184 | 2.35 | 2.02 | 1.80 | 1.64 | 1.52 | 1.64 |
|  | 2 – 38 x 235 | 2.88 | 2.47 | 2.20 | 2.01 | 1.84 | 2.01 |
|  | 2 – 38 x 286 | 3.34 | 2.87 | 2.56 | 2.33 | 2.09 | 2.33 |
|  | 2 – 38 x 89 | 1.05 | 0.96 | 0.89 | 0.84 | 0.79 | 0.74 |
|  | 2 – 38 x 140 | 1.49 | 1.37 | 1.27 | 1.19 | 1.13 | 1.02 |
| Roof, ceiling and 1 storey(5) | 2 – 38 x 184 | 1.82 | 1.67 | 1.55 | 1.44 | 1.33 | 1.20 |
|  | 2 – 38 x 235 | 2.22 | 2.04 | 1.89 | 1.73 | 1.59 | 1.45 |
|  | 2 – 38 x 286 | 2.58 | 2.36 | 2.15 | 1.96 | 1.81 | 1.66 |
|  | 2 – 38 x 89 | 0.94 | 0.88 | 0.83 | 0.79 | 0.76 | 0.64 |
|  | 2 – 38 x 140 | 1.34 | 1.26 | 1.19 | 1.13 | 1.06 | 0.88 |
| Roof, ceiling and 2 storeys(5) | 2 – 38 x 184 | 1.63 | 1.53 | 1.44 | 1.33 | 1.25 | 1.05 |
|  | 2 – 38 x 235 | 1.99 | 1.87 | 1.72 | 1.60 | 1.50 | 1.27 |
|  | 2 – 38 x 286 | 2.31 | 2.12 | 1.96 | 1.82 | 1.71 | 1.45 |
|  | 2 – 38 x 89 | 0.88 | 0.83 | 0.80 | 0.77 | 0.74 | 0.59 |
|  | 2 – 38 x 140 | 1.25 | 1.19 | 1.14 | 1.08 | 1.02 | 0.81 |
| Roof, ceiling and 3 storeys(5) | 2 – 38 x 184 | 1.52 | 1.44 | 1.35 | 1.27 | 1.21 | 0.97 |
|  | 2 – 38 x 235 | 1.86 | 1.73 | 1.62 | 1.53 | 1.45 | 1.17 |
|  | 2 – 38 x 286 | 2.11 | 1.96 | 1.84 | 1.74 | 1.66 | 1.35 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |

Notes to Table A-17:

(1) Spans are calculated based on a maximum supported joist or rafter length of 4.9 m and a maximum supported truss length of 9.8 m. Spans may be increased by 5% for supported lengths not more than 4.3 m, or by 10% for supported lengths not more than 3.7 m. Supported length means half the span of the longest supported member.

(2) If floor joists span the full width of the building without support, lintels spans shall be reduced by 15% for Roof, ceiling and 1 storey, by 20% for Roof, ceiling and 2 storeys, and by 25% for Roof, ceiling and 3 storeys.

(3) For ends of lintels fully supported by walls, provide minimum 38 mm of bearing for lintel spans up to 3 m, or minimum 76 mm or bearing for lintel spans greater than 3 m.

(4) A single piece of 89 mm thick lumber may be used in lieu of 2 pieces of 38 mm thick lumber on edge.

(5) Spans apply only where the floors serve residential areas as described in Table 4.1.6.3., or the uniformly distributed live load on the floor does not exceed that specified for residential areas as described in table 4.1.6.3.

Table A-18

Maximum Spans for Spruce – Pine – Fir Lintels — No. 1 or No. 2 Grade Structural Sheathing(1)

Forming Part of Sentences 9.23.12.3.(1) and (3)

| Lintel Supporting | Lintel Size, mm (5) | Maximum Span, m(2) (3) (4) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Exterior Walls |  |  |  |  |
|  |  | Specified Snow Load, kPa |  |  |  |  |
|  |  | 1.0 | 1.5 | 2.0 | 2.5 | 3.0 |
|  | 2 – 38 x 89 | 1.40 | 1.23 | 1.11 | 1.03 | 0.97 |
|  | 2 – 38 x 140 | 2.21 | 1.93 | 1.73 | 1.57 | 1.45 |
| Roof and ceiling only | 2 – 38 x 184 | 2.75 | 2.36 | 2.10 | 1.92 | 1.77 |
|  | 2 – 38 x 235 | 3.36 | 2.89 | 2.57 | 2.34 | 2.16 |
|  | 2 – 38 x 286 | 3.90 | 3.35 | 2.99 | 2.72 | 2.51 |
|  | 2 – 38 x 89 | 1.16 | 1.08 | 1.01 | 0.96 | 0.92 |
|  | 2 – 38 x 140 | 1.74 | 1.60 | 1.48 | 1.39 | 1.32 |
| Roof, ceiling and 1 storey(6) | 2 – 38 x 184 | 2.12 | 1.95 | 1.81 | 1.69 | 1.60 |
|  | 2 – 38 x 235 | 2.59 | 2.38 | 2.21 | 2.07 | 1.93 |
|  | 2 – 38 x 286 | 3.01 | 2.76 | 2.56 | 2.38 | 2.19 |
|  | 2 – 38 x 89 | 1.09 | 1.03 | 0.97 | 0.92 | 0.88 |
|  | 2 – 38 x 140 | 1.56 | 1.47 | 1.39 | 1.32 | 1.26 |
| Roof, ceiling and 2 storeys(6) | 2 – 38 x 184 | 1.90 | 1.79 | 1.69 | 1.61 | 1.51 |
|  | 2 – 38 x 235 | 2.33 | 2.19 | 2.07 | 1.94 | 1.81 |
|  | 2 – 38 x 286 | 2.70 | 2.54 | 2.37 | 2.20 | 2.05 |
|  | 2 – 38 x 89 | 1.02 | 0.97 | 0.93 | 0.89 | 0.86 |
|  | 2 – 38 x 140 | 1.46 | 1.39 | 1.33 | 1.28 | 1.23 |
| Roof, ceiling and 3 storeys(6) | 2 – 38 x 184 | 1.78 | 1.69 | 1.62 | 1.54 | 1.46 |
|  | 2 – 38 x 235 | 2.17 | 2.07 | 1.96 | 1.84 | 1.74 |
|  | 2 – 38 x 286 | 2.52 | 2.38 | 2.22 | 2.09 | 1.98 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 |

Notes to Table A-18:

(1) A minimum 9.5 mm thick structural panel conforming to CSA O121-M, CSA O151-M, CAN/CSA-O325.0 or CAN/CSA-O437.0 shall be fastened with at least 2 rows of fasteners conforming to Table 9.23.3.5 to the exterior face of the lintel, and a single row to the top plates and studs.

(2) Spans are calculated based on a maximum supported joist or rafter length of 4.9 m and a maximum supported truss length of 9.8 m. Spans may be increased by 5% for supported lengths not more than 4.3 m, or by 10% for supported lengths not more than 3.7 m. Supported length means half the span of the longest supported member.

(3) If roof joists span the full width of the building without support, lintels spans shall be reduced by 15% for roof, ceiling and one storey, by 20% for roof, ceiling and two storeys, and by 25% for roof, ceiling and three storeys.

(4) For ends of lintels fully supported by walls, provide minimum 38 mm of bearing for lintel spans up to 3 m, or minimum 76 mm of bearing for lintel spans greater than 3 m.

(5) A single piece of 89 mm thick lumber may be used in lieu of 2 pieces of 38 mm thick lumber on edge.

(6) Spans apply only where the floors serve residential areas as described in Table 4.1.6.3., or the uniformly distributed live load on the floor does not exceed that specified for residential areas as described in Table 4.1.6.3.

Table A-19

Maximum Spans for Built-up Lintels — Roof and Ceiling Load Only — No. 1 or No. 2 Grade

Forming Part of Sentences 9.23.12.3.(1) and (3)

| Commercial Designation | Lintel Size, mm | Maximum Span, m(1) (2) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Specified Snow Load, kPa |  |  |  |  |
|  |  | 1.0 | 1.5 | 2.0 | 2.5 | 3.0 |
|  | 3 – 38 x 184 | 2.76 | 2.38 | 2.12 | 1.93 | 1.78 |
|  | 4 – 38 x 184 | 3.19 | 2.74 | 2.44 | 2.22 | 2.05 |
| Douglas Fir – Larch (includes Douglas Fir and | 5 – 38 x 184 | 3.57 | 3.07 | 2.73 | 2.49 | 2.30 |
| Western larch) | 3 – 38 x 235 | 3.38 | 2.90 | 2.59 | 2.35 | 2.18 |
|  | 4 – 38 x 235 | 3.90 | 3.35 | 2.99 | 2.72 | 2.51 |
|  | 5 – 38 x 235 | 4.36 | 3.75 | 3.34 | 3.04 | 2.81 |
|  | 3 – 38 x 286 | 3.92 | 3.37 | 3.00 | 2.73 | 2.52 |
|  | 4 – 38 x 286 | 4.53 | 3.89 | 3.47 | 3.15 | 2.91 |
|  | 5 – 38 x 286 | 5.06 | 4.35 | 3.87 | 3.53 | 3.26 |
|  | 3 – 38 x 184 | 2.90 | 2.49 | 2.22 | 2.02 | 1.87 |
|  | 4 – 38 x 184 | 3.35 | 2.88 | 2.56 | 2.33 | 2.15 |
|  | 5 – 38 x 184 | 3.73 | 3.22 | 2.86 | 2.61 | 2.41 |
| Hem – Fir (includes Western | 3 – 38 x 235 | 3.54 | 3.05 | 2.71 | 2.47 | 2.28 |
| Hemlock and Amabilis Fir) | 4 – 38 x 235 | 4.09 | 3.52 | 3.13 | 2.85 | 2.63 |
|  | 5 – 38 x 235 | 4.57 | 3.93 | 3.50 | 3.19 | 2.95 |
|  | 3 – 38 x 286 | 4.11 | 3.53 | 3.15 | 2.87 | 2.62 |
|  | 4 – 38 x 286 | 4.75 | 4.08 | 3.63 | 3.31 | 3.06 |
|  | 5 – 38 x 286 | 5.31 | 4.56 | 4.06 | 3.70 | 3.42 |
|  | 3 – 38 x 184 | 3.00 | 2.58 | 2.30 | 2.09 | 1.93 |
|  | 4 – 38 x 184 | 3.30 | 2.88 | 2.62 | 2.42 | 2.23 |
|  | 5 – 38 x 184 | 3.55 | 3.10 | 2.82 | 2.62 | 2.46 |
| Spruce – Pine – Fir (includes Spruce (all species | 3 – 38 x 235 | 3.67 | 3.15 | 2.81 | 2.56 | 2.36 |
| except Coast Sitka Spruce), | 4 – 38 x 235 | 4.21 | 3.64 | 3.24 | 2.95 | 2.73 |
| Jack Pine, Lodgepole Pine, Balsam Fir and | 5 – 38 x 235 | 4.54 | 3.96 | 3.60 | 3.30 | 3.05 |
| Alpine Fir) | 3 – 38 x 286 | 4.26 | 3.66 | 3.26 | 2.97 | 2.74 |
|  | 4 – 38 x 286 | 4.92 | 4.23 | 3.76 | 3.43 | 3.17 |
|  | 5 – 38 x 286 | 5.49 | 4.73 | 4.21 | 3.83 | 3.54 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 |

Notes to Table A-19:

(1) Spans are calculated based on a maximum supported length of 4.9 m. Spans may be increased by 15% for supported lengths not more than 3.7 m, or by 35% for supported lengths not more than 2.4 m. Supported length means half span of the trusses, roof joists or rafters supported by the lintel plus the length of the overhang beyond the lintel.

(2) For ends of lintels fully supported by the wall, provide minimum 38 mm of bearing for lintel spans up to 3 m, or minimum 76 mm of bearing for lintel spans greater than 3 m.

Table A-20

Maximum Spans for Glued-Laminated Timber Lintels 
20f-E Stress Grade — Exterior Walls — Roof and Ceiling Load Only

Forming part of Sentences 9.23.12.3.(1) and (3)

| Lintel Size, mm | Maximum Span, m(1) (2) (3) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Specified Snow Load, kPa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 1.0 |  |  | 1.5 |  |  | 2.0 |  |  | 2.5 |  |  | 3.0 |  |  |
|  | Supported length m(4) (5) |  |  | Supported length m(4) (5) |  |  | Supported length m(4) (5) |  |  | Supported length m(4) (5) |  |  | Supported length m(4) (5) |  |  |
|  | 2.4 | 3.6 | 4.8 | 2.4 | 3.6 | 4.8 | 2.4 | 3.6 | 4.8 | 2.4 | 3.6 | 4.8 | 2.4 | 3.6 | 4.8 |
| 130 x 304 | 6.23 | 5.63 | 5.24 | 5.63 | 5.09 | 4.73 | 5.24 | 4.73 | 4.40 | 4.95 | 4.48 | 4.17 | 4.73 | 4.28 | 3.87 |
| 80 x 380 | 6.52 | 5.89 | 5.48 | 5.89 | 5.32 | 4.96 | 5.48 | 4.96 | 4.52 | 5.19 | 4.69 | 4.11 | 4.96 | 4.39 | 3.80 |
| 130 x 342 | 6.80 | 6.15 | 5.72 | 6.15 | 5.56 | 5.17 | 5.72 | 5.17 | 4.81 | 5.41 | 4.89 | 4.55 | 5.17 | 4.67 | 4.35 |
| 80 x 418 | 7.00 | 6.33 | 5.89 | 6.33 | 5.72 | 5.32 | 5.89 | 5.32 | 4.96 | 5.57 | 5.03 | 4.52 | 5.32 | 4.81 | 4.18 |
| 130 x 380 | 7.36 | 6.65 | 6.19 | 6.65 | 6.01 | 5.59 | 6.19 | 5.59 | 5.21 | 5.86 | 5.29 | 4.92 | 5.59 | 5.06 | 4.70 |
| 80 x 456 | 7.48 | 6.76 | 6.29 | 6.76 | 6.10 | 5.68 | 6.29 | 5.68 | 5.29 | 5.95 | 5.37 | 4.93 | 5.68 | 5.13 | 4.56 |
| 130 x 418 | 7.91 | 7.15 | 6.65 | 7.15 | 6.46 | 6.01 | 6.65 | 6.01 | 5.59 | 6.29 | 5.68 | 5.29 | 6.01 | 5.43 | 5.05 |
| 80 x 494 | 7.94 | 7.17 | 6.68 | 7.17 | 6.48 | 6.03 | 6.68 | 6.03 | 5.61 | 6.31 | 5.71 | 5.31 | 6.03 | 5.45 | 4.94 |
| 80 x 532 | 8.39 | 7.58 | 7.06 | 7.58 | 6.85 | 6.38 | 7.06 | 6.38 | 5.93 | 6.67 | 6.03 | 5.61 | 6.38 | 5.76 | 5.32 |
| 130 x 456 | 8.44 | 7.63 | 7.10 | 7.63 | 6.89 | 6.41 | 7.10 | 6.41 | 5.97 | 6.71 | 6.07 | 5.65 | 6.41 | 5.80 | 5.39 |
| Column 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |

Notes to Table A-20:

(1) Spans are valid for glued-laminated timber conforming to CAN/CSA-O122-M and CAN/CSA-O177-M.

(2) Provide minimum 89 mm bearing. (Alternatively, the bearing length may be calculated in accordance with Part 4.)

(3) Top edge of lintel assumed to be fully laterally supported.

(4) Supported length means half the length of trusses or rafters, plus the length of overhang beyond the wall.

(5) For intermediate supported lengths, straight line interpolation may be used.

O. Reg. 403/97, Part 9; O. Reg. 22/98, ss. 19-31; O. Reg. 278/99, ss. 19-26; O. Reg. 593/99, s. ; O. Reg. 597/99, s. 1; O. Reg. 283/01, s. 5; O. Reg. 23/04, s. 5; O. Reg. 349/06, ss. 22, 23.

Part 10
Change of Use

| Section | 10.1. | General |
| --- | --- | --- |
|  | 10.1.1. | Scope |
| Section | 10.2. | Classification of Existing Buildings |
|  | 10.2.1. | Classification |
| Section | 10.3. | Requirements |
|  | 10.3.1. | General |
|  | 10.3.2. | Performance Level |
| Section | 10.4. | Compliance Alternatives And Alternative Measures |
|  | 10.4.1. | Compliance Alternatives |
|  | 10.4.2. | Alternative Measures |

Part 10
Change of Use

Section 10.1. General

10.1.1. Scope

10.1.1.1.  Scope

(1)  The scope of this Part shall be as described in Section 2.1.

10.1.1.2.  Change in Major Occupancy

(1)  The following changes of use shall also be deemed to be a change in major occupancy for the purposes of this Part:

(a)	a suite of a Group C major occupancy is converted into more than one suite of Group C major occupancy,

(a.1)	a suite or part of a suite of a Group A, Division 2 or a Group A, Division 4 major occupancy is converted to a gaming premise,

(b)	a farm building or part of a farm building is changed to a major occupancy, and

(c)	the use of a building or part of a building is changed and the previous major occupancy of the building or part of the building cannot be determined.

10.1.1.3.  Definitions

(1)  In this Part, the following words and terms have the meaning that they are given in Article 11.1.1.2.:

Building system

Section 10.2. Classification of Existing Buildings

10.2.1. Classification

10.2.1.1.  Classification of Major Occupancy

(1)  Every existing building or part thereof shall be classified according to its major occupancy in accordance with the requirements of Subsection 3.1.2.

10.2.1.2.  Classification According to Construction and Occupancy

(1)  For the purposes of this Part, existing buildings shall be classified as to their construction and occupancy as provided for in Sentence 11.2.1.1.(1).

10.2.1.3.  Building Size and Construction

(1)  The requirements of Articles 3.2.2.20. to 3.2.2.83. do not apply to this Part.

Section 10.3. Requirements

10.3.1. General

10.3.1.1.  General

(1)  Except as provided in Section 10.4., a building or part of a building subject to a change of major occupancy shall conform to the requirements of Subsection 3.2.6., Sections 3.7., 3.11., 3.11A., 9.5. and 9.7., Subsection 9.10.16., Sections 9.31. and 9.32., and Subsections 9.34.1., 9.34.2. and 9.34.3. as they apply to the new major occupancy that the building or part of a building is to support.

10.3.2. Performance Level

10.3.2.1.  General

(1)  The performance level of a building after the change of major occupancy shall not be less than the performance level prior to the change of major occupancy.

(2)  For the purposes of Sentence (1), reduction of performance level shall be determined in accordance with Article 10.3.2.2.

10.3.2.2.  Reduction in Performance Level

(1)  Except as provided in Sentence (2), the performance level of a building or part of a building is reduced where the existing structural floor and roof framing systems and their supporting members are not adequate to support the proposed dead loads and live loads of the new major occupancy that the building is to support.

(2)  The inadequacy of the existing structural floor or roof framing system and its supporting members to support the proposed dead loads and live loads does not reduce the performance level of the building if the portion of the floor affected by the proposed loads is restricted to the loading it will support and signs stating the restrictions are posted.

(3)  Except as provided in Section 10.4., the performance level of a building or part of a building is reduced where the early warning and evacuation systems requirements of the building do not meet the early warning and evacuation systems requirements set out in Table 10.3.2.2.A. for the new major occupancy that the building is to support.

Table 10.3.2.2.A.

For Evaluation of Early Warning/Evacuation

Forming Part of Sentence 10.3.2.2.(3)

| EW/EVAC Evaluation | Compliance Alternative(1) |
| --- | --- |
| Early Warning and Evacuation to be checked against | EARLY WARNING (a) Compliance alternatives as listed may be used. EVACUATION (b) Compliance alternatives as listed to access to exit and exit widths, number of exits, door release hardware, and travel distance may be used. |
| (a) access to exit widths based on occupant load in Subsection 3.3.1. or 9.9.3.; |  |
| (b) exit widths based on occupant load in Subsection 3.4.3. or 9.9.3.; |  |
| (c) exit signs in Subsection 3.4.5. or 9.9.10.; |  |
| (d) lighting of exits, lighting of access to exits and emergency lighting in |  |
| Subsection 3.2.7. or 9.9.11.; |  |
| (e) fire alarm system in Subsection 3.2.4. or 9.10.17.; |  |
| (f) smoke alarms in 9.10.18.; |  |
| (g) travel distance and number of exits in other Parts of the Code; |  |
| (h) smoke control measures, and at least one elevator to permit transport of firefighters to all floors in hotels whose floor level is more than 18 m high, measured between grade and floor level of the top storey as per Subsection 3.2.6., and |  |
| (i) door release hardware requirements in Articles 3.3.1.12. and 3.4.6.15., and |  |
| deficiencies shall be upgraded. |  |
| Column 1 | 2 |

Note to Table 10.3.2.2.A.:

(1) See Tables 11.5.1.1.A., 11.5.1.1.B., 11.5.1.1.C., 11.5.1.1.D/E and 11.5.1.1.F. for compliance alternatives that may be used.

(4)  Except as provided in Sentence (5), the performance level of an existing building is reduced where a change in use will result in a change of the major occupancy of all or part of an existing building to another major occupancy of a greater hazard index.

(5)  Except as provided in Sentence (6), if the hazard index of the new major occupancy is greater than the hazard index of the existing major occupancy, the performance level is not reduced where the hazard index of the new major occupancy is not greater than the construction index of the existing building.

(6)  Small or medium sized existing buildings as determined in Tables 11.2.1.1.B. to N. facing multiple streets may be assigned a hazard index credit of 1, which may be subtracted from the hazard index of the new major occupancy provided

(a)	the building does not contain a Group B, Division 1, a Group C, or a Group F, Division 1 occupancy, and

(b)	fire fighting access complying with Articles 3.2.5.1., 3.2.5.2., 3.2.5.3., 3.2.5.4. and 3.2.5.5. or Subsection 9.10.9., or an approved alternative measure is provided from all streets.

(7)  Except as provided in Sentence (8), the performance level of a building or part of a building is reduced in an existing building constructed of combustible construction where

(a)	the occupancy is changed to a residential occupancy in all or part of the building, and

(b)	if the building was new, it would have been required to be constructed of noncombustible construction.

(8)  A change in the occupancy of a building or part of a building to a residential occupancy does not reduce the performance level of the building or part of the building where

(a)	the building is sprinklered, and

(b)	the building does not exceed 6 storeys in building height.

(9)  The performance level of a building or part of a building is reduced where the new major occupancy in an existing building of multiple occupancy is not separated from adjoining major occupancies by fire separations having fire-resistance ratings conforming to Article 3.1.3.1., Subsection 9.10.9. or Table 10.3.2.2.B.

Table 10.3.2.2.B.(1)

Additional Upgrading for Multiple Major Occupancies

Forming Part of Sentence 10.3.2.2.(9)

| New Major Occupancy | Code Requirements | Compliance Alternative |  |
| --- | --- | --- | --- |
| All(2) | Table 3.1.3.1. and Subsection 9.10.9. | For Existing Buildings | If Sprinklered |
|  | Where: | Reduce to | Reduce to |
|  | 1 h rating required | 45 min | 30 min |
|  | 2 h rating required | 1.5 h | 1 h |
|  | 3 h rating required | 2 h | 1.5 h |
| Column 1 | 2 | 3 |  |

Notes to Table 10.3.2.2.B.:

(1) For buildings with multiple major occupancies only, where there is a change in major occupancy.

(2) See Sentence 10.3.2.2.(9).

(10)  The performance level of a building is reduced where the building after the change of major occupancy will not comply with Articles 3.1.3.1. or 9.10.9.12.

(11)  The performance level of a building or part of a building is reduced where, after a change of major occupancy

(a)	the total daily design sanitary sewage flow of the new major occupancy, calculated in accordance with Article 8.2.1.3., exceeds the capacity of any component of a sewage system serving the building, or

(b)	the type or amount of sanitary sewage which will, under the new major occupancy, be discharged to a sewage system serving the building is prohibited by Article 8.1.3.1.

Section 10.4.  Compliance Alternatives And Alternative Measures

10.4.1. Compliance Alternatives

10.4.1.1.  Substitution

(1)  Except as provided in Sentence (3), a compliance alternative to a requirement contained in Part 3, 4, 5, 6 or 7 which is shown in Tables 11.5.1.1.A., 11.5.1.1.B., 11.5.1.1.C., 11.5.1.1.D/E. or 11.5.1.1.F. may be substituted for the requirement where the chief building official is satisfied that compliance with the requirement is impracticable because

(a)	of structural or construction difficulties, or

(b)	it is detrimental to the preservation of a heritage building.

(2)  Except as provided in Sentence (3), a compliance alternative to a requirement contained in Part 9 shown in Tables 11.5.1.1.C., 11.5.1.1.D/E. or 11.5.1.1.F. may be substituted for the requirement without satisfying the chief building official that the requirement is impracticable.

(3)  Where the building has been in existence for less than five years, compliance alternatives may only be used in respect of requirements of the Code which are referenced in Sentences 10.3.2.2.(3), (5) and Table 10.3.2.2.B.

10.4.2. Alternative Measures

10.4.2.1.  Substitution

(1)  Except as permitted in Sentence (2), an alternative measure to

(a)	a requirement of Part 3, 4, 5, 6, 7 or 9 of the Code, or

(b)	a compliance alternative,

may be substituted for the requirement or the compliance alternative, as the case may be, where the chief building official is satisfied that compliance with the requirement or the compliance alternative, as the case may be, is impracticable because

(c)	of structural or construction difficulties, or

(d)	it is detrimental to the preservation of a heritage building.

(2)  Where the building has been in existence for less than five years, alternative measures may only be used in respect of requirements of the Code which are referenced in Sentence 10.3.2.2.(3), (5) and Table 10.3.2.2.B.

O. Reg. 403/97, Part 10; O. Reg. 22/98, s. 32; O. Reg. 205/00, ss. 5, 6.

Part 11
Renovation

| Section | 11.1. | General |
| --- | --- | --- |
|  | 11.1.1. | Scope |
|  | 11.1.2. | Application |
| Section | 11.2. | Classification of Existing Buildings |
|  | 11.2.1. | Classification |
| Section | 11.3. | Proposed Construction |
|  | 11.3.1. | New and Existing Building Systems |
|  | 11.3.2. | Extension of Buildings |
|  | 11.3.3. | Renovation |
|  | 11.3.4. | Plumbing |
| Section | 11.4. | Performance Level Evaluation and Compensating Construction |
|  | 11.4.1. | General |
|  | 11.4.2. | Reduction in Performance Level |
|  | 11.4.3. | Compensating Construction |
| Section | 11.5. | Compliance Alternatives and Alternative Measures |
|  | 11.5.1. | Compliance Alternatives |
|  | 11.5.2. | Alternative Measures |

Part 11
Renovation

Section 11.1. General

11.1.1. Scope

11.1.1.1.  Scope

(1)  The scope of this Part shall be as described in Section 2.1.

11.1.1.2.  Definitions

(1)  In this Part

Building system means a combination of elements or components that form a complete major division of construction in the design of a building or part of a building, including a structural or framing system, a waterproofing system, a drainage system, an exterior cladding system, a roofing system, a window system, a partition system, a corridor system, a stair system, a fire alarm and detection system, a sprinkler system or a heating, ventilation or air conditioning system, a foundation system, a standpipe and hose system, a flooring system, a plumbing system, a sewage system or an electrical system.

11.1.2. Application

11.1.2.1.  Extension, Material Alteration or Repair

(1)  Where an existing building is subject to extension, material alteration or repair

(a)	the proposed construction shall comply with Section 11.3., and

(b)	the performance level of the building shall be evaluated and compensating construction shall be undertaken in accordance with Section 11.4.

Section 11.2. Classification of Existing Buildings

11.2.1. Classification

11.2.1.1.  Construction Index and Hazard Index

(1)  The proposed construction will result in the change of major occupancy of all or part of an existing building to another major occupancy, the building shall be classified as to its

(a)	construction on the basis of construction index as provided for in this Part including Table 11.2.1.1.A., and

(b)	occupancy on the basis of hazard index as provided for in this Part including Tables 11.2.1.1.B. to 11.2.1.1.N.

(2)  Small or medium sized existing buildings as determined in Tables 11.2.1.1.B. to 11.2.1.1.N. facing multiple streets may be assigned a hazard index credit of 1, which may be subtracted from the hazard index of the proposed major occupancy to reduce the additional upgrading required by Table 11.4.3.4.A. provided

(a)	the building does not contain a Group B, Division 1; a Group C, or a Group F, Division 1 occupancy, and

(b)	fire fighting access complying with Articles 3.2.5.1., 3.2.5.2., 3.2.5.3., 3.2.5.4. and 3.2.5.5. or Subsection 9.10.19., or an approved alternative measure, is provided from all streets.

(3)  The requirements of Articles 3.2.2.20. to 3.2.2.83. do not apply to this Part.

11.2.1.2.  Multiple Occupancies

(1)  The classification of an existing building of multiple occupancy under Article 11.2.1.1. shall be applied according to Articles 3.2.2.5. to 3.2.2.8.

11.2.1.3.  Prohibition of Occupancy Combinations

(1)  Nothing in this Part relieves an applicant from complying with the requirements of Articles 3.1.3.2. or 9.10.9.12.

Section 11.3. Proposed Construction

11.3.1. New and Existing Building Systems

11.3.1.1.  Material Alteration or Repair of a Building System

(1)  Where an existing building system is materially altered or repaired, the performance level of the building after the material alteration or repair shall be at least equal to the performance level of the building prior to the material alteration or repair.

11.3.1.2.  New Building Systems and Extension of Existing Building Systems

(1)  Except as provided in Article 11.3.3.1. and Section 11.5., the design and construction of a new building system or the extension of an existing building system, shall comply with all other Parts of the Code.

11.3.2. Extension of Buildings

11.3.2.1.  Portion of Extended Buildings

(1)  Where an existing building is extended

(a)	this Part applies to the existing portion of the building, and

(b)	the extended portion of the building shall comply with all other Parts of the Code.

11.3.3. Renovation

11.3.3.1.  Basic Renovation

(1)  Except as provided in Sentence (2) and Article 11.3.3.2., construction may be carried out to maintain the existing performance level of all or part of an existing building, by the reuse, relocation or extension of the same or similar materials or components, to retain the existing character, structural uniqueness, heritage value, or aesthetic appearance of all or part of the building if, the construction will not adversely affect the early warning and evacuation systems, fire separations, the structural adequacy or create an unhealthy environment in the building.

(2)  Construction in respect of a hotel may only be carried out in accordance with Sentence (1) provided that the construction will be in conformance with Part 9 of the Ontario Fire Code made under the Fire Marshals Act.

11.3.3.2.  Extensive Renovation

(1)  Except as provided in Subsection 11.5.2., where existing interior walls or ceilings or floor assemblies or roof assemblies are substantially removed in an existing building and new interior walls, ceilings, or floor assemblies are installed in the building, structural and fire-resistance elements shall be constructed in compliance with the requirements of the other Parts of the Code.

11.3.4. Plumbing

11.3.4.1.  Existing Plumbing System

(1)  Notwithstanding Subsections 11.3.1., 11.3.2., 11.3.3., where an existing plumbing system is extended or subject to material alteration or repair, the construction of plumbing shall comply with Part 7.

Section 11.4. Performance Level Evaluation and Compensating Construction

11.4.1. General

11.4.1.1.  Performance Level

(1)  The performance level of a building after construction shall not be less than the performance level of the building prior to construction.

(2)  For the purposes of Sentence (1), reduction of performance level shall be determined in accordance with Subsection 11.4.2.

(3)  Where the proposed construction would reduce the performance level of an existing building, compensating construction shall be required in conformance with Subsection 11.4.3.

11.4.2. Reduction in Performance Level

11.4.2.1.  Structural

(1)  The performance level of an existing building is reduced where after proposed construction in all or part of an existing building

(a)	the major occupancy will change to a different major occupancy,

(b)	the occupant load will increase by more than 15%, or

(c)	the live load will increase due to change in use within the same major occupancy,

and the existing structural floor and roof framing systems and their supporting members after the construction are not adequate to support the proposed dead loads and live loads.

11.4.2.2.  Increase in Occupant Load

(1)  Except as required in Sentences 11.4.2.5.(2) and (3), the performance level of an existing building is reduced where the proposed construction will increase the occupant load of an existing building by more than 15 per cent.

(2)  The performance level of an existing building is reduced where proposed construction will increase the occupant load by 15% or less and the new occupant load will be more than 15% above the occupant load for which a fire alarm system is required under Sentence 3.2.4.1.(2).

(3)  The performance level of an existing building is reduced where proposed construction will increase the occupant load by 15% or less and the new occupant load will be more than 15% above the existing exit capacity as required under Article 3.4.3.4.

11.4.2.3.  Change of Major Occupancy

(1)  Except as required in Sentence 11.4.2.5.(4), the performance level of an existing building is reduced where proposed construction will result in

(a)	the change of the major occupancy of all or part of an existing building to another major occupancy of a greater hazard index,

(b)	the conversion of a suite of a Group C major occupancy into more than one suite of Group C major occupancy,

(b.1)	a suite or part of a suite of a Group A, Division 2 or a Group A, Division 4 major occupancy is converted to a gaming premise,

(c)	the change of a farm building or part of a farm building to a major occupancy, or

(d)	the change in use of a building or part of a building where the previous major occupancy of the building or part of the building cannot be determined.

(2)  For the purposes of this Article and Sentences 11.4.2.1.(1) and 11.4.2.5.(4), the changes of use set out in Clauses (1)(b) to (d) shall also be deemed to constitute a change in major occupancy.

(3)  The performance level of an existing building is reduced where the early warning and evacuation systems requirements of other Parts of the Code for the proposed major occupancy exceed those of the existing building.

(4)  The performance level of an existing building is reduced where the proposed major occupancy in the building is not separated from the adjoining major occupancies by fire separations having fire-resistance ratings conforming to Tables 3.1.3.1. and 11.4.3.4.B.

(5)  The performance level of an existing building is reduced where the occupancy of all or part of an existing building of combustible construction is changed to a new major occupancy that would require the building, if it were a new building, to be constructed of noncombustible construction.

11.4.2.4.  Plumbing

(1)  The performance level of an existing building is reduced where the existing building is extended or subject to material alteration or repair, and plumbing in the existing building is adversely affected by the extension, alteration or repair.

11.4.2.5.  Sewage Systems

(1)  The performance level of an existing building is reduced where the existing building is extended or subject to material alteration or repair and a sewage system serving the existing building is adversely affected by the extension, alteration or repair of the existing building.

(2)  Except as provided in Sentence (3), the performance level of an existing building is reduced where proposed construction will increase the occupant load of an existing building, and the new occupant load will result in the total daily design sanitary sewage flow of the building, calculated in accordance with Article 8.2.1.3., exceeding the capacity of any component of a sewage system serving the building.

(3)  The performance level of an existing dwelling unit is reduced where proposed construction which

(a)	increases the number of bedrooms in the dwelling unit,

(b)	exceeds 15 per cent of the finished area of the dwelling unit, or

(c)	adds new plumbing fixtures to the dwelling unit,

will result in the total daily design sanitary sewage flow of the dwelling unit, calculated in accordance with Article 8.2.1.3., exceeding the capacity of any component of a sewage system serving the dwelling unit.

(4)  The performance level of an existing building is reduced where proposed construction will result in the change of a major occupancy of all or part of the existing building to another major occupancy and

(a)	the total daily design sanitary sewage flow of the proposed major occupancy, calculated in accordance with Article 8.2.1.3., exceeds the capacity of any component of a sewage system serving the building, or

(b)	the type or amount of sanitary sewage which will, under the proposed major occupancy, be discharged to a sewage system serving the building, is prohibited by Article 8.1.3.1.

11.4.3. Compensating Construction

11.4.3.1.  General

(1)  Where the performance level of an existing building is reduced under Subsection 11.4.2., compensating construction shall be carried out in accordance with this Subsection.

(2)  Except as provided in Sentence (3) compensating construction required under this Subsection applies to the part of the building being altered and shall include

(a)	fire separations, with the required fire-resistance ratings, separating the part being altered from the floor areas immediately above and below and from the immediate adjacent areas, and

(b)	access to exits and exits from the building, where the alteration adversely affects the exit system of the building.

(3)  Compensating construction required under this Subsection applies to the existing building systems that are adversely affected by the proposed construction.

11.4.3.2.  Structural

(1)  Where the performance level of an existing building is reduced under Sentence 11.4.2.1.(1)

(a)	remedial measures shall be taken to support the proposed loads, or

(b)	the portion of the floor affected by the proposed loads shall be restricted to the loading it will support and signs stating the restrictions shall be posted.

11.4.3.3.  Increase in Occupant Load

(1)  Where the performance level of an existing building is reduced under Sentences 11.4.2.2.(1), (2) or (3) the building shall be evaluated, and the early warning and evacuation systems shall be upgraded, in conformance with the applicable requirements of Table 11.4.3.3.

(2)  Sentence (1) does not apply in a Group C occupancy where the new total occupant load is

(a)	14 persons or less in a boarding, lodging or rooming house, except that where the occupant load is between 10 and 15 persons, an interconnected system of smoke alarms in corridors near stairways is required, or

(b)	16 persons or less in a building containing residential suites which are dwelling units, except that where the occupant load is between 10 and 17 persons, an interconnected system of smoke alarms in corridors near stairways is required.

(3)  Where the performance level of an existing building is reduced under Sentence 11.4.2.2.(1), additional construction shall be required in order that the building or part of the building subject to the increase in occupant load conforms to the requirements of Articles 3.7.4.2. and 9.31.1.1.

11.4.3.4.  Change in Major Occupancy

(1)  Where the performance level of an existing building is reduced under Sentence 11.4.2.3.(1), additional upgrading shall be required in conformance with Table 11.4.3.4.A. and so that the construction index of the building is increased to at least equal the hazard index of the new major occupancy that the building is to support.

(2)  Where the performance level of an existing building is reduced under Sentence 11.4.2.3.(1), additional construction shall be required in order that the building or part of the building subject to change of major occupancy conforms to the requirements of Subsection 3.2.6., Sections 3.7., 3.11, 3.11A., 9.5., and 9.7., Subsections 9.10.16., Sections 9.31. and 9.32., and Subsections 9.34.1., 9.34.2., and 9.34.3. as they apply to the new major occupancy that the building or part of the building is to support.

(3)  Where the performance level of an existing building is reduced under Sentence 11.4.2.3.(3), the building shall be evaluated, and the early warning and evacuation systems shall be upgraded, in conformance with the applicable requirements of Table 11.4.3.3.

(4)  Where the performance level of an existing building is reduced under Sentence 11.4.2.3.(4), upgrading of those systems shall be required in conformance with the applicable requirements of Article 3.1.3.1. and Table 11.4.3.4.B.

(5)  Where the performance level is reduced under Sentence 11.4.2.3.(5) the requirement for noncombustible construction is satisfied if the building is sprinklered.

11.4.3.5.  Plumbing

(1)  Where the performance level of an existing building is reduced under Sentence 11.4.2.4.(1), upgrading of plumbing in the existing building which is adversely affected by the extension, alteration or repair shall be required in conformance with Part 7.

11.4.3.6.  Sewage Systems

(1)  Where the performance level of an existing building is reduced under Article 11.4.2.5., upgrading of a sewage system which is adversely affected by the construction, increase in occupant load, increase in the total daily design sanitary sewage flow or change in amount or type of sanitary sewage shall be required in conformance with Part 8.

Section 11.5. Compliance Alternatives and Alternative Measures

11.5.1. Compliance Alternatives

11.5.1.1.  Compliance Alternatives

(1)  A compliance alternative shown in Tables 11.5.1.1.A., 11.5.1.1.B., 11.5.1.1.C., 11.5.1.1.D/E. or 11.5.1.1.F. may be substituted for a requirement contained in Part 3, 4, 5, 6, 7 or 8 where the chief building official is satisfied that compliance with the requirement is impracticable because

(a)	of structural or construction difficulties, or

(b)	it is detrimental to the preservation of a heritage building.

(2)  A compliance alternative shown in Tables 11.5.1.1.A., 11.5.1.1.B., 11.5.1.1.C., 11.5.1.1.D/E. or 11.5.1.1.F. may be substituted for a requirement contained in Part 9 without satisfying the chief building official that compliance with the requirement is impracticable.

11.5.2. Alternative Measures

11.5.2.1.  Alternative Measures

(1)  An alternative measure may be utilized where the chief building official is satisfied that

(a)	compliance with the requirement of Part 3, 4, 5, 6, 7, 8 or 9 of the Code or with the compliance alternative, as the case may be, is impracticable because

(i)	of structural or construction difficulties, or

(ii)	it is detrimental to the preservation of a heritage building, and

(b)	the performance level of the building after the use of the alternative measure shall not be less than the performance level of the building prior to construction.

Table 11.2.1.1.A.

Construction Index

Forming Part of Sentence 11.2.1.1.(1)

| Fire-Resistance Rating |  |  | Type of Construction | C.I.(2) |
| --- | --- | --- | --- | --- |
| Floors over Basement | Other Floors | Roof |  |  |
| 3 h | 3 h | 1.5 h | Noncombustible | 8 (1) |
| 2 h | 2 h | 1 h | Noncombustible | 7 |
| 1 h | 1 h | 45 min | Noncombustible | 6 |
| 45 min | 45 min | 0 h | Noncombustible | 5 |
| 45 min | 45 min | 45 min | Heavy Timber | 5 |
| 45 min | 45 min | 45 min | Combustible | 5 |
| 45 min | 0 h | 0 h | Noncombustible | 4 |
| 45 min | 45 min | 0 h | Combustible | 4 |
| 30 min | 0 h | 0 h | Noncombustible | 3 |
| 30 min | 30 min | 0 h | Combustible | 3 |
| 0 h | 30 min | 0 h | Combustible | 2 |
| 0 h | 0 h | 0 h | Combustible | 1 (1) |
| Column 1 | 2 | 3 | 4 | 5 |

Notes to Table 11.2.1.1.A.:

(1) C.I. of 1 is lowest fire protection performance level and C.I. of 8 is highest.

(2) Take highest rating for C.I. from Table 11.2.1.1.A. for existing building.

Table 11.2.1.1.B.

Hazard Index

Forming Part of Sentences 11.2.1.1.(1) and (2)

| Group A Division 1 | Occupancy H.I.(5) |  |  |  |  | (1) (2) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Small | Medium |  |  | Large |  |  |
| Dinner Theatres | 4 | 5 |  |  | 6 |  |  |
| Live Theatres | 4 | 5 |  |  | 6 |  |  |
| Motion Picture Theatres | 4 | 5 |  |  | 6 |  |  |
| Opera Houses | 4 | 5 |  |  | 6 |  |  |
| Television Studios (With Audience) | 4 | 5 |  |  | 6 |  |  |
| Column 1 | 2 | 3 |  |  | 4 |  |  |

Notes to Table 11.2.1.1.B.:

(1)

| Building Size (Maximum)(2) (3) |  |
| --- | --- |
| — 300 occupant load maximum / 1 storey | Small |
| — 600 m2 / 600 occupant load maximum / 1 storey with less than 40% 2 storey (6) | Medium |
| — Any area / not exceeding 18 m in building height | Large |
| — Over 18 m in building | H.I. = 7 |

(2) Sizes are based on building area and building height.

(3) Building size is based on the existing building facing one street.

(4) For existing buildings facing multiple streets see Sentence 11.2.1.1.(2) and Table 11.4.3.4.A.

(5) Take lowest rating for H.I. from Table for major occupancy change.

(6) Building may have less than 40% of its area as 2 storey for purposes as described in Clauses 3.2.2.21.(1)(b) and (c).

Table 11.2.1.1.C.

Hazard Index

Forming Part of Sentences 11.2.1.1.(1) and (2)

| Group A Division 2 | Occupancy H.I.(5) |  |  |  | (1) (2) |
| --- | --- | --- | --- | --- | --- |
|  | Small | Medium |  | Large |  |
| Art Galleries | 3 | 4 |  | 6 |  |
| Auditoria | 3 | 4 |  | 6 |  |
| Billiard Halls, Amusement Arcades | 3 | 4 |  | 6 |  |
| Bowling Alleys | 3 | 4 |  | 6 |  |
| Churches | 3 | 4 |  | 6 |  |
| Clubs, Lodges (Non-Residential) | 3 | 4 |  | 6 |  |
| Community Halls | 3 | 4 |  | 6 |  |
| Concert Halls | 3 | 4 |  | 6 |  |
| Court Rooms | 3 | 4 |  | 6 |  |
| Dance Halls | 3 | 4 |  | 6 |  |
| Daycare Centres | 3 | 4 |  | 6 |  |
| Exhibition Halls (Without Sales) | 3 | 4 |  | 6 |  |
| Exhibition Halls (With Sales) | 3 See Group E |  |  |  |  |
| Gaming Premise | 3 | 4 | 6 |  |  |
| Gymnasia (Multi-Purpose) | 3 | 4 | 6 |  |  |
| Gymnasia (Athletic) | 3 | 4 | 6 |  |  |
| Lecture Halls | 3 | 4 | 6 |  |  |
| Libraries | 3 | 4 | 6 |  |  |
| Licensed Beverage Establishments | 3 | 4 | 6 |  |  |
| Licensed Clubs, Lodges | 3 | 4 | 6 |  |  |
| Museums | 3 | 4 | 6 |  |  |
| Passenger Stations/Depots | 3 | 4 | 6 |  |  |
| Public Heritage Buildings | 3 | — | — |  |  |
| Recreational Piers | 3 | 4 | 6 |  |  |
| Restaurants | 3 | 4 | 6 |  |  |
| School, Colleges | 3 | 4 | 6 |  |  |
| Undertaking Premises | 3 | 4 | 6 |  |  |
| Column 1 | 2 | 3 | 4 |  |  |

Notes to Table 11.2.1.1.C.:

(1)

| Building Size (Maximum) (2) (3) |  |
| --- | --- |
| — 400 m2 / 1 storey | Small |
| — 250 m2 / 3 storey (Public Heritage Building) | Small |
| — 800 m2 / 2 storey | Medium |
| — Any area / not exceeding 18 m in building height | Large |
| — Over 18 m in building height | H.I. = 7 |

(2) Sizes are based on building area and building height.

(3) Building size is based on the existing building facing one street.

(4) For existing buildings facing multiple streets see Sentence 11.2.1.1.(2) and Table 11.4.3.4.A.

(5) Take lowest rating for H.I. from Table for major occupancy change.

(6) Building exceeding 3 storeys in building height and which are combustible shall be sprinklered.

Table 11.2.1.1.D.

Hazard Index

Forming Part of Sentences 11.2.1.1.(1) and (2)

| Group A Division 3 | Occupancy H.I.(5) |  |  | (1) (2) |
| --- | --- | --- | --- | --- |
|  | Small | Medium | Large |  |
| Arenas (No Occupancy On Activity Surface) | 3 | 4 | 6 |  |
| Armouries (No Occupancy On Activity Surface) | 3 | 4 | 6 |  |
| Enclosed Stadia or Grandstand | 3 | 4 | 6 |  |
| Ice Rinks (No Occupancy On Activity Surface) | 3 | 4 | 6 |  |
| Indoor Swimming Pools | 3 | 4 | 6 |  |
| Column 1 | 2 | 3 | 4 |  |

Notes to Table 11.2.1.1.D.:

(1)

| Building Size (Maximum) (2) (3) |  |
| --- | --- |
| — 1000 m2 / 1 storey | Small |
| — 2000 m2 / 2 storey | Medium |
| — Any area / not exceeding 18 m in building height | Large |
| — Over 18 m in building height | H.I. = 7 |

(2) Sizes are based on building area and building height.

(3) Building size is based on the existing building facing one street.

(4) For existing buildings facing multiple streets see Sentence 11.2.1.1.(2) and Table 11.4.3.4.A.

(5) Take lowest rating for H.I. from Table for major occupancy change.

Table 11.2.1.1.E.

Hazard Index

Forming Part of Sentences 11.2.1.1.(1) and (2)

| Group A Division 4 | Occupancy H.I.(5) |  |  | (1) (2) |
| --- | --- | --- | --- | --- |
|  | Small | Medium | Large |  |
| Amusement Park Structures | 2 | 3 | 5 |  |
| Bleachers | 1 | 3 | 5 |  |
| Grandstands (Open) | 1 | 3 | 5 |  |
| Reviewing Stands | 1 | 3 | 5 |  |
| Stadia (Open) | 1 | 3 | 5 |  |
| Column 1 | 2 | 3 | 4 |  |

Notes to Table 11.2.1.1.E.:

(1)

| Building Size (Maximum) (2) (3) |  |
| --- | --- |
| — 2500 occupant load max./min. limiting distance of 6 m (combustible) | Small |
| — 15,000 occupant load maximum (with roof at least ½ rating if combustible) | Medium |
| — Unlimited occupant load | Large |

(2) Sizes are based on building area and building height.

(3) Building size is based on the existing building facing one street.

(4) For existing buildings facing multiple streets see Sentence 11.2.1.1.(2) and Table 11.4.3.4.A.

(5) Take lowest rating for H.I. from Table for major occupancy change.

Table 11.2.1.1.F.

Hazard Index

Forming Part of Sentences 11.2.1.1.(1) and (2)

| Group B Division 1 | Occupancy H.I.(3)(5) |  |  | (1) (2) |
| --- | --- | --- | --- | --- |
|  | Small | Medium | Large |  |
| Detention Facilities (Minimum Security) (4) | 4 | 5 | 6 |  |
| Detention Facilities (All other types of security) | 6 | 6 | 7 |  |
| Police Station with Detention | 3 | — | — |  |
| Column 1 | 2 | 3 | 4 |  |

Notes to Table 11.2.1.1.F.:

(1)

| Building Size (Maximum)(2) |  |
| --- | --- |
| — Any area / 1 storey | Small |
| — 600 m2 / 1 storey (Police Station with Detention) | Small |
| — Any area (noncombustible) / 2 storey | Medium |
| — Any area (noncombustible); 500 m2 (combustible) / 2 storey | Large |
| — Over 18 m in building height (noncombustible) | H.I. = 7 |
| — Over 500 m2 (combustible) / over 2 storey | H.I. = 7 |

(2) Sizes are based on building area and building height.

(3) When the size of a building falls into more than one category, the H.I. for the least restrictive is permitted to be used.

(4) Minimum security — means occupants free to exit building in a fire emergency.

(5) Detention occupancy with any H.I. shall be sprinklered.

Table 11.2.1.1.G.

Hazard Index

Forming Part of Sentences 11.2.1.1.(1) and (2)

| Group B Division 2 | Occupancy H.I. (5) (7) |  |  |  | (1) (2) |
| --- | --- | --- | --- | --- | --- |
|  | Small | Medium | Large |  |  |
| Hospital, Nursing home, Geriatric, Sanatorium (6) (Immobile) | 4 | 5 | 7 |  |  |
| Hospital, Nursing Home, Geriatric, Sanatorium (6) (Non-Ambulatory) | 4 | 5 | 6 |  |  |
| Hospital, Nursing Home, Geriatric, Sanatorium (6) (Ambulatory) | 3 | 4 | 6 |  |  |
| Psychiatric Hospitals (Maximum Confinement) | 4 | 5 | 7 |  |  |
| Psychiatric Hospitals (Minimum Confinement) | 3 | 4 | 6 |  |  |
| Police Station With Detention | 3 | 3 | — |  |  |
| Column 1 | 2 | 3 | 4 |  |  |

Notes to Table 11.2.1.1.G.:

(1)

| Building Size (Maximum)(2)(3) |  |
| --- | --- |
| — 250 m2 / 1 storey | Small |
| — 600 m2 /1 storey (Police Station with Detention) | Small |
| — 500 m2 / 2 storey; 1000 m2 / 1 storey | Medium |
| — Any area (noncombustible); 500 m2 (combustible) / 2 storey | Medium |
| — Any area /not exceeding 18 m in building height | Large |
| — Over 18 m in building height | H.I. = 7 |

(2) Sizes are based on building area and building height.

(3) Building size is based on the existing building facing one street.

(4) For existing buildings facing multiple streets see Sentence 11.2.1.1.(2) and Table 11.4.3.4.A.

(5) When the size of a building falls into more than one category, the H.I. for the least restrictive is permitted to be used.

(6) Immobile — means patients attached to life support systems and cannot be moved. Non-Ambulatory — means patients confined to bed and require transportation. Ambulatory — means patients may walk on their own.

(7) Care and treatment occupancy with any H.I. shall be sprinklered.

Table 11.2.1.1.H.

Hazard Index

Forming Part of Sentences 11.2.1.1.(1) and (2)

| Group B Division 3 | Occupancy H.I.(4)(5) |  |  | (1) (2) |
| --- | --- | --- | --- | --- |
|  | Small | Medium | Large |  |
| Residential care facilities (Ambulatory) (Non-Ambulatory) | 3 4 | 4 5 | 6 6 |  |
| Children Custodial Homes | 3 | 4 | 6 |  |
| Convalescent Homes (Ambulatory) (Non-Ambulatory) | 3 4 | 4 5 | 6 6 |  |
| Orphanages | 3 | 4 | 6 |  |
| Sanatoria Without Detention Quarter (Min. Confinement) (Max. Confinement) | 3 4 | 4 5 | 6 6 |  |
| Group Homes For Developmentally Handicapped Residents (Min. Confinement) (Max. Confinement) | 3 4 | 4 5 | 6 6 |  |
| Column 1 | 2 | 3 | 4 |  |

Notes to Table 11.2.1.1.H.:

(1)

| Building Size (Maximum)(2)(3) |  |
| --- | --- |
| — 600 m2 / 1 storey | Small |
| — 500 m2 / 2 storey; 1000 m2 / 1 storey | Medium |
| — Any area /not exceeding 18 m in building height | Large |
| — Over 18 m in building height | H.I. = 7 |

(2) Sizes are based on building area and building height.

(3) Building sizes is based on the existing building facing one street.

(4) When the size of a building falls into more than one category, the H.I. for the least restrictive is permitted to be used.

(5) Care occupancy with any H.I. shall be sprinklered.

Table 11.2.1.1.I.

Hazard Index

Forming Part of Sentences 11.2.1.1.(1) and (2)

| Group C | Occupancy H.I.(4) |  |  |  | (1) (2) |
| --- | --- | --- | --- | --- | --- |
|  | Small | Medium |  | Large |  |
| Apartments | 3 | 4 |  | 6 |  |
| Boarding Houses/Group Homes | 3 | — |  | — |  |
| Clubs, Residential | 3 | 4 |  | 6 |  |
| Colleges, Residential | 3 | 4 |  | 6 |  |
| Convents | 3 | 4 |  | 6 |  |
| Dormitories/Hostels | 3 | 4 |  | 6 |  |
| Hotels | 3 | 5 |  | 6 |  |
| Houses, S.F. | 2 | 2 |  | — |  |
| Live / Work Units | 4 | 5 |  | 7 |  |
| Lodging Houses | 3 | — |  | — |  |
| Monasteries | 3 | 4 |  | 6 |  |
| Public Heritage Buildings | 3 | — |  | — |  |
| Rectories | 2 | — |  | — |  |
| Retirement Homes | 3 | 4 |  | 6 |  |
| Rooming Houses | 3 | — |  | — |  |
| Schools, Residential | 3 | 4 |  | 6 |  |
| Column 1 | 2 | 3 |  | 4 |  |

Notes to Table 11.2.1.1.I.:

(1)

| Building Size (Maximum)(2)(3) |  |
| --- | --- |
| — 600 m2 / 3 storey | Small |
| — 250 m2 / 3 storey (Public Heritage Building) | Small |
| — 2000 m2 / not exceeding 6 storeys | Medium |
| — Any area / not exceeding 36 m in building height | Large |
| — Over 36 m in building height | H.I. = 7 |
| — Hotels over 18 m high, measured between grade and the floor level of the top storey | H.I. = 7 |

(2) Sizes are based on building area and building height.

(3) Building exceeding 3 storeys in building height and which are combustible shall be sprinklered.

(4) Take lowest rating for H.I. from Table for major occupancy change.

Table 11.2.1.1.J.

Hazard Index

Forming Part of Sentences 11.2.1.1.(1) and (2)

| Group D | Occupancy H.I.(5) |  |  | (1) (2) |
| --- | --- | --- | --- | --- |
|  | Small | Medium | Large |  |
| Advertising and Sales Offices | 3 | 3 | 5 |  |
| Automatic Bank Deposit | 3 | 4 | 5 |  |
| Barber/Hairdresser Shops | 3 | 4 | 5 |  |
| Beauty Parlours | 3 | 4 | 5 |  |
| Branch Banks | 3 | 4 | 5 |  |
| Car Rental Premises | 3 | 3 | 5 |  |
| Chiropractic Offices | 3 | 4 | 5 |  |
| Communications Offices (Telephone E.) | 3 | 4 | 5 |  |
| Communications Offices (Telex) | 3 | 4 | 5 |  |
| Communications Offices (Courier) | 3 | 3 | 5 |  |
| Computer Centres | 3 | 4 | 5 |  |
| Construction Offices | 3 | 3 | 5 |  |
| Costume Rental Premises | 3 | 4 | 5 |  |
| Dental Offices (Denture Clinic) | 3 | 4 | 5 |  |
| Dental Offices (General) | 3 | 4 | 5 |  |
| Dental Offices (Surgical/Anaesthesia) | 4 | 5 | 6 |  |
| Dry Cleaning Depots | 3 | 4 | 5 |  |
| Dry Cleaning Premises (Self-Serve) | 4 | 4 | 5 |  |
| Health/Fitness Clubs | 3 | 4 | 5 |  |
| Laundries (Self-Serve) | 4 | 4 | 5 |  |
| Massage Parlours | 3 | 4 | 5 |  |
| Medical Offices (Examination) | 3 | 4 | 5 |  |
| Medical Offices (Surgical/Anaesthesia) | 4 | 5 | 6 |  |
| Offices (Business) | 3 | 3 | 5 |  |
| Offices (Charitable) | 3 | 3 | 5 |  |
| Offices (Legal/Accounting) | 3 | 3 | 5 |  |
| Offices/Studios (Design) | 3 | 4 | 5 |  |
| Pharmacy Offices | 3 | 4 | 5 |  |
| Photographic Studios | 3 | 4 | 5 |  |
| Physiotherapy Offices | 3 | 4 | 5 |  |
| Police Stations (No Detention) | 3 | 4 | 5 |  |
| Printing and Duplicating | 4 | 5 | 6 |  |
| Public Heritage Buildings | 3 | — | — |  |
| Public Saunas | 3 | 4 | 5 |  |
| Radio Stations (No Audience) | 3 | 4 | 5 |  |
| Small Tool Rental Premises | 3 | 4 | 5 |  |
| Suntan Parlours | 3 | 4 | 5 |  |
| Veterinary Offices | 3 | 4 | 5 |  |
| Column 1 | 2 | 3 | 4 |  |

Notes to Table 11.2.1.1.J.:

(1)

| Building Size (Maximum) (2) (3) |  |
| --- | --- |
| — 800 m2 / 2 storey | Small |
| — 250 m2 / 3 storey (Public Heritage Building) | Small |
| — 1600 m2 / 3 storey | Medium |
| — Any area / not exceeding 18 m in building height | Large |
| — Over 18 m, but not exceeding 36 m in building height | H.I. = 6 |
| — Over 36 m in building height | H.I. = 7 |

(2) Sizes are based on building area and building height.

(3) Building size is based on the existing building facing one street.

(4) For existing buildings facing multiple streets see Sentence 11.2.1.1.(2) and Table 11.4.3.4.A.

(5) When the size of a building falls into more than one category, the H.I. for the least restrictive is permitted to be used.

Table 11.2.1.1.K.

Hazard Index

Forming Part of Sentences 11.2.1.1.(1) and (2)

| Group E | Occupancy H.I.(5) |  |  |  |  | (1) (2) |
| --- | --- | --- | --- | --- | --- | --- |
|  | Small |  | Medium |  | Large |  |
| Automotive/Hardware Department Stores | 4 |  | 5 |  | 7 |  |
| China Shops | 3 |  | 4 |  | 6 |  |
| Department Stores | 4 |  | 5 |  | 7 |  |
| Electrical Stores (Fixtures) | 3 |  | 3 |  | 5 |  |
| Exhibition Halls (With Sales) | 4 |  | 5 |  | 7 |  |
| “Fast Food” Outlets | 3 |  | 4 |  | 5 |  |
| Feed And Seed Stores | 4 |  | 5 |  | 7 |  |
| Flea Markets | 4 |  | 5 |  | 7 |  |
| Flower Shops | 3 |  | 4 |  | 6 |  |
| “Food” and Vegetable Markets | 3 |  | 4 |  | 6 |  |
| Garden Shops | 3 |  | 4 |  | 6 |  |
| “Gas” Bars | 4 |  | 5 |  | 7 |  |
| Gift Shops | 3 |  | 4 |  | 6 |  |
| Home Improvement Stores | 4 |  | 5 |  | 7 |  |
| Kitchen/Bathroom Cupboards Stores | 3 |  | 4 |  | 6 |  |
| Plumbing Stores (Fixtures/Accessories) | 3 |  | 3 |  | 5 |  |
| “Pop” Shops | 3 |  | 4 |  | 6 |  |
| Public Heritage Buildings | 3 |  | — |  | — |  |
| Rentals (See “D”) | — |  | — |  | — |  |
| Restaurants (Not More Than 30 Persons) | 3 |  | 4 |  | 5 |  |
| Shopping Malls | 4 |  | 5 |  | 7 |  |
| Stationary/Office Supply Stores | 3 |  | 4 |  | 6 |  |
| Stores (Art) | 3 |  | 4 |  | 6 |  |
| Stores (Baked Goods) | 3 |  | 4 |  | 6 |  |
| Stores (Beer) | 3 |  | 4 |  | 6 |  |
| Stores (Book) | 3 |  | 4 |  | 6 |  |
| Stores (Camera) | 3 |  | 4 |  | 6 |  |
| Stores (Candy) | 3 |  | 4 |  | 6 |  |
| Stores (Clothing) | 3 |  | 4 |  | 6 |  |
| Stores (Drugs) | 4 |  | 4 |  | 6 |  |
| Stores (Electronic) | 3 |  | 4 |  | 6 |  |
| Stores (Floor Coverings) | 4 |  | 5 |  | 7 |  |
| Stores (Food) | 3 |  | 3 |  | 6 |  |
| Stores (Furniture/Appliances) | 3 |  | 4 |  | 6 |  |
| Stores (Hardware) | 4 |  | 5 |  | 7 |  |
| Stores (Health) | 4 |  | 4 |  | 6 |  |
| Stores (Hobby) | 3 |  | 4 |  | 6 |  |
| Stores (Jewellery) | 3 |  | 3 |  | 5 |  |
| Stores (Paint/Wallpaper) | 4 |  | 5 |  | 7 |  |
| Stores (Pet) | 3 |  | 4 |  | 6 |  |
| Stores (Records/Tapes) | 3 |  | 4 |  | 6 |  |
| Stores (Spirits) | 4 |  | 5 |  | 7 |  |
| Stores (Toys) | 4 |  | 5 |  | 7 |  |
| Stores (Variety) | 4 |  | 4 |  | 6 |  |
| Stores (Video Sales/Rental) | 3 |  | 4 |  | 6 |  |
| Supermarkets | 3 |  | 4 |  | 6 |  |
| Column 1 | 2 |  | 3 |  | 4 |  |

Notes to Table 11.2.1.1.K.:

(1)

| Building Size (Maximum) (2) (3) |  |
| --- | --- |
| — 600 m2 / 2 storey | Small |
| — 250 m2 / 3 storey (Public Heritage Building) | Small |
| — 800 m2 / 3 storey | Medium |
| — Any area / up to 18 m in building height | Large |
| — Over 18 m in building height | H.I. = 7 |

(2) Sizes are based on building area and building height.

(3) Building size is based on the existing building facing one street.

(4) For existing buildings facing multiple streets see Sentence 11.2.1.1.(2) and Table 11.4.3.4.A.

(5) When the size of a building falls into more than one category, the H.I. for the least restrictive is permitted to be used.

(6) All buildings 1,500 m2 and over are to be sprinklered.

Table 11.2.1.1.L.

Hazard Index

Forming Part of Sentences 11.2.1.1.(1) and (2)

| Group F Division 1 | Occupancy H.I.(3) |  |  |  |  | (1) (2) |
| --- | --- | --- | --- | --- | --- | --- |
|  | Small |  | Medium |  | Large |  |
| Ammunition Manufacturing and Storage | 3 |  | 6 |  | 8 |  |
| Black Powder Manufacturing and Storage | 3 |  | 6 |  | 8 |  |
| Bulk Plants for Flammable Liquids | 3 |  | 6 |  | 8 |  |
| Bulk Storage Warehouse (Hazardous Substances) | 3 |  | 6 |  | 8 |  |
| Cereal and Feed Mills | 3 |  | 6 |  | 8 |  |
| Chemical Manufacturing/ Processing Plant | 3 |  | 6 |  | 8 |  |
| Distilleries | 3 |  | 6 |  | 8 |  |
| Dry Cleaning Plants (Flammable) | 3 |  | 6 |  | 8 |  |
| Explosives Manufacturing and Storage | 3 |  | 6 |  | 8 |  |
| Fertilizer Manufacturing Plants | 3 |  | 6 |  | 8 |  |
| Fireworks Manufacturing and Storage | 3 |  | 6 |  | 8 |  |
| Flour Mills | 3 |  | 6 |  | 8 |  |
| Gas (Flammable) Compressor Stations | 3 |  | 6 |  | 8 |  |
| Gas (Flammable) Manufacturing and Storage | 3 |  | 6 |  | 8 |  |
| Grain Elevators | 3 |  | 6 |  | 8 |  |
| Lacquer Factories | 3 |  | 6 |  | 8 |  |
| Loading Areas (for all Group F, Division 1) | 3 |  | 6 |  | 8 |  |
| Mattress Factories (High Fire Load) | 3 |  | 6 |  | 8 |  |
| Paint/Varnish/Pyroxylin Factories | 3 |  | 6 |  | 8 |  |
| Petrochemical Plants | 3 |  | 6 |  | 8 |  |
| Refineries | 3 |  | 6 |  | 8 |  |
| Rubber Processing Plants | 3 |  | 6 |  | 8 |  |
| Spray Painting Operations | 3 |  | 6 |  | 8 |  |
| Waste Paper Processing Plants (Dry) | 3 |  | 6 |  | 8 |  |
| Column 1 | 2 |  | 3 |  | 4 |  |

Notes to Table 11.2.1.1.L.:

(1)

| Building Size (Maximum) (2) |  |
| --- | --- |
| — 400 m2 / 2 storey | Small |
| — 600 m2 / 4 storey | Medium |
| — 1500 m2 / 4 storey | Large |

(2) Sizes are based on building area and building height.

(3) When the size of a building falls into more than one category, the H.I. for the least restrictive is permitted to be used.

(4) All buildings 1,500 m2 and over are to be sprinklered.

(5) All floor assemblies shall be fire separations.

Table 11.2.1.1.M.

Hazard Index

Forming Part of Sentences 11.2.1.1.(1) and (2)

| Group F Division 2 | Occupancy H.I.(5) |  |  |  |  |  | (1) (2) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Small |  | Medium |  | Large |  |  |
| Aircraft Hangars | 3 |  | 5 |  | 6 |  |  |
| Abattoirs | 3 |  | 4 |  | 5 |  |  |
| Bakeries | 3 |  | 5 |  | 6 |  |  |
| Body Shops | 3 |  | 5 |  | 6 |  |  |
| Candy Plants | 3 |  | 4 |  | 5 |  |  |
| COLD STORAGE PLANTS Combustible Insulation Flammable Refrigerant Combustible Packaging | 3 |  | 5 |  | 7 |  |  |
| Combustible Insulation Flammable Refrigerant Noncombustible Packaging | 3 |  | 5 |  | 6 |  |  |
| Combustible Insulation Non-Flammable Refrigerant Noncombustible Packaging | 3 |  | 4 |  | 5 |  |  |
| Noncombustible Insulation Non-Flammable Refrigerant Noncombustible Packaging | 2 |  | 3 |  | 4 |  |  |
| Dry Cleaning Establishments (non-flammable or non-explosive) | 3 |  | 4 |  | 5 |  |  |
| Electrical Substations | 3 |  | 4 |  | 5 |  |  |
| Factories (High Fire Load) | 3 |  | 5 |  | 6 |  |  |
| Freight Depots (High Fire Load) | 3 |  | 5 |  | 6 |  |  |
| Helicopter Landings (on roof) | 3 |  | 4 |  | 5 |  |  |
| Laboratories (High Fire Load) | 3 |  | 5 |  | 6 |  |  |
| Laundries (not self-serve) | 3 |  | 4 |  | 5 |  |  |
| Manufacturer Sales (High Fire Load) | 3 |  | 5 |  | 6 |  |  |
| Mattress Factories | 3 |  | 4 |  | 5 |  |  |
| Meat Packing Plants | 3 |  | 4 |  | 5 |  |  |
| Packaging Manufacturers (Cellulose) | 3 |  | 4 |  | 5 |  |  |
| Packaging Manufacturers (Noncombustible) | 2 |  | 3 |  | 4 |  |  |
| Packaging Manufacturers (Plastics) | 3 |  | 5 |  | 6 |  |  |
| Paper Processing Plants (Wet) | 3 |  | 5 |  | 6 |  |  |
| Planing Mills | 3 |  | 5 |  | 6 |  |  |
| Printing Plants | 3 |  | 4 |  | 5 |  |  |
| Public Heritage Buildings | 3 |  | 3 |  | — |  |  |
| Repair Garages | 3 |  | 5 |  | 6 |  |  |
| Sample Display Rooms (High Fire Load) | 3 |  | 5 |  | 6 |  |  |
| Self-Service Storage Buildings | 3 |  | 4 |  | 5 |  |  |
| Service Stations (no spray painting) | 3 |  | 5 |  | 6 |  |  |
| Storage Rooms (High Fire Load) | 3 |  | 5 |  | 6 |  |  |
| Television Studios (no audience) | 3 |  | 4 |  | 5 |  |  |
| Tire Storage | 3 |  | 5 |  | 6 |  |  |
| Warehouses (High Fire Load) | 3 |  | 5 |  | 6 |  |  |
| Welding Shops | 3 |  | 5 |  | 6 |  |  |
| Wholesale Rooms (High Fire Load) | 3 |  | 5 |  | 6 |  |  |
| Wood Working Factories | 3 |  | 5 |  | 6 |  |  |
| Workshops (High Fire Load) | 3 |  | 5 |  | 6 |  |  |
| Column 1 | 2 |  | 3 |  | 4 |  |  |

Notes to Table 11.2.1.1.M.:

(1)

| Building Size (Maximum) (2)(3) |  |
| --- | --- |
| — 600 m2 / 2 storey | Small |
| — 800 m2 / 4 storey | Medium |
| — 600 m2 / 3 storey (Public Heritage Building) | Medium |
| — 1500 m2 / 6 storey not exceeding 18 m in building height | Large |
| — Over 18 m in building height | H.I. = 7 |

(2) Sizes are based on building area and building height.

(3) Building size is based on the existing building facing one street.

(4) For existing buildings facing multiple streets see Sentence 11.2.1.1.(2) and Table 11.4.3.4.A.

(5) When the size of a building falls into more than one category, the H.I. for the least restrictive is permitted to be used.

(6) All buildings 1,500 m2 and over are to be sprinklered.

Table 11.2.1.1.N.

Hazard Index

Forming Part of Sentences 11.2.1.1.(1) and (2)

| Group F Division 3 | Occupancy H.I.(5) |  |  |  | (1) (2) |
| --- | --- | --- | --- | --- | --- |
|  | Small | Medium | Large |  |  |
| Creameries | 2 | 2 | 3 |  |  |
| Factories (Low Fire Load) | 2 | 3 | 4 |  |  |
| Freight Depots (Low Fire Load) | 2 | 3 | 4 |  |  |
| Laboratories (Low Fire Load) | 2 | 3 | 4 |  |  |
| Manufacturers Sales (Low Fire Load) | 2 | 3 | 4 |  |  |
| Power Plants | 3 | 4 | 5 |  |  |
| Public Heritage Buildings | 3 | 3 | — |  |  |
| Sample Display Rooms (Low Fire Load) | 2 | 3 | 4 |  |  |
| Storage Garages | 2 | 3 | 4 |  |  |
| Storage Rooms (Low Fire Load) | 2 | 3 | 4 |  |  |
| Warehouses (Low Fire Load) | 2 | 3 | 4 |  |  |
| Wholesale Rooms (Low Fire Load) | 2 | 3 | 4 |  |  |
| Workshops (Low Fire Load) | 2 | 3 | 4 |  |  |
| Column 1 | 2 | 3 | 4 |  |  |

Notes to Table 11.2.1.1.N.:

(1)

| Building Size (Maximum) (2) (3) |  |
| --- | --- |
| — 800 m2 / 2 storey | Small |
| — 1200 m2 / 4 storey | Medium |
| — 600 m2 / 3 storey (Public Heritage Building) | Medium |
| — Any area / 6 storey not exceeding 18 m in building height | Large |
| — Over 18 m, but not exceeding 36 m in building height | H.I. = 5 |
| — Over 36 m in building height | H.I. = 6 |

(2) Sizes are based on building area and building height.

(3) Building size is based on the existing building facing one street.

(4) For existing buildings facing multiple streets see Sentence 11.2.1.1.(2) and Table 11.4.3.4.A.

(5) When the size of a building falls into more than one category, the H.I. for the least restrictive is permitted to be used.

Table 11.4.3.3.

For Evaluation and Upgrading of Early Warning/Evacuation

Forming Part of Sentences 11.4.3.3.(1) and (2)

| Notes | EW/EVAC, Evaluation and Upgrading | Part 11 Compliance Alternative (1) |
| --- | --- | --- |
| (2) | Early Warning and Evaluation to be checked against | EARLY WARNING (a) Compliance alternatives as listed may be used. EVACUATION (b) Compliance alternatives as listed to access to exit and exit widths, number of exits, door release hardware, and travel distance may be used. |
|  | (a) access to exit widths based on occupant load in Subsection 3.3.1. or 9.9.3.; |  |
|  | (b) exit widths based on occupant load in Subsection 3.4.3. or 9.9.3.; |  |
|  | (c) exit signs in Subsection 3.4.5. or 9.9.10.; |  |
|  | (d) lighting of exits, lighting of access to exits and emergency lighting in Subsection 3.2.7. or 9.9.11.; |  |
|  | (e) fire alarm system in Subsection 3.2.4. or 9.10.17.; |  |
|  | (f) smoke alarms in Subsection 9.10.18.; |  |
|  | (g) travel distance and number of exits in other Parts of the Code; and |  |
|  | (h) door release hardware requirements in Articles 3.3.1.12. and 3.4.6.15., |  |
|  | and deficiencies shall be upgraded. |  |
| (3) | Early Warning and Evaluation to be checked against | EARLY WARNING (a) Compliance alternatives as listed may be used. EVACUATION (b) Compliance alternatives as listed to access to exit and exit widths, number of exits, door release hardware, and travel distance may be used. |
|  | (a) access to exit widths based on occupant load in Subsection 3.3.1. or 9.9.3.; |  |
|  | (b) exit widths based on occupant load in Subsection 3.4.3. or 9.9.3.; |  |
|  | (c) exit signs in Subsection 3.4.5. or 9.9.10.; |  |
|  | (d) lighting of exits, lighting of access to exits and emergency lighting in Subsection in Subsection 3.2.7. or 9.9.11.; |  |
|  | (e) fire alarm system in Subsection 3.2.4. or 9.10.17.; |  |
|  | (f) smoke alarms in Subsection 9.10.18.; |  |
|  | (g) travel distance and number of exits in other Parts of the Code; |  |
|  | (h) smoke control measures, and at least one elevator to permit transport of firefighters to all floors in hotels whose floor level is more than 18 m high measured between grade and floor level of the top storey as per Subsection 3.2.6.; and |  |
|  | (i) door release hardware requirements in Articles 3.3.1.12. and 3.4.6.15., |  |
|  | and deficiencies shall be upgraded. |  |
| Column 1 | 2 | 3 |

Notes to Table 11.4.3.3.:

(1) See Table 11.5.1.1.A., 11.5.1.1.B., 11.5.1.1.C., 11.5.1.1.D/E. And 11.5.1.1.F. for Compliance alternatives that may be used.

(2) Applies to change of major occupancy to one of equal or lesser hazard.

(3) Applies to change of major occupancy to one of greater hazard, and to increase in occupant load greater than 15%.

Table 11.4.3.4.A.

Additional Upgrading

Forming Part of Sentence 11.4.3.4.(1)

| New Major Occupancy (H.I.) Number (3) | Increase of C.I. to Equal H.I. to Support New Major Occupancy | Additional Required Upgrading | Part 11 Alternative Compliance | Comments |
| --- | --- | --- | --- | --- |
| H.I.2 | C.I. 1 to 2 | Comply with Table 11.2.1.1.A. ratings for C.I. of 2 | (a) Provide Early Warning system or (b) Comply with any A.C.’s in Col. 4. |  |
| H.I.3 | C.I. (1 or 2) to 3 | Comply with Table 11.2.1.1.A. ratings for C.I. of 3 | (a) Provide Early Warning system or (b) Comply with any A.C.’s in Col. 4. | Combustible to Combustible only. |
| H.I.4 | C.I. (1,2 or 3) to 4 | Comply with Table 11.2.1.1.A. ratings for C.I. of 4 | Provide sprinklers in locations where assemblies do not comply with Table 11.2.1.1.A. | Combustible to Combustible. Noncombustible to Noncombustible. |
| H.I.5 | C.I. 4 to 5 | Comply with Table 11.2.1.1.A. ratings for C.I. of 5 | Provide sprinklers in locations where assemblies do not comply with Table 11.2.1.1.A. |  |
| H.I.5 | C.I. (1,2 or 3) to 5 | Comply with Table 11.2.1.1.A. ratings for C.I. of 5 | Provide sprinklers in locations where assemblies do not comply with Table 11.2.1.1.A. | Combustible to Combustible. Noncombustible to Noncombustible. |
| H.I.6 | C.I. 5 (Noncombustible) to 6 | Comply with Table 11.2.1.1.A. ratings for C.I. of 6 | (a) Provide sprinkler system, plus 45 min roof rating. |  |
| H.I.6 | C.I. 5 (Heavy timber) to 6 | Comply with A.C. | (b) Provide sprinkler system. |  |
| H.I.6 | C.I. 5 (Combustible) to 6 | Comply with A.C. | (c) Provide 1 h rating plus sprinkler system. |  |
| H.I.6 | C.I. (3 or 4) to 6* | Comply with Table 11.2.1.1.A. ratings for C.I. of 6 | (d) Provide sprinkler system, plus 45 min rating. | *For Noncombustible construction only. |
| H.I.6 | C.I. (1, 2, 3 or 4) to 6** | Comply with A.C. | (e) Provide 1 h rating plus sprinkler system. | **For Combustible construction only. |
| H.I.7 | C.I. 6 to 7 | Comply with Table 11.2.1.1.A. ratings for C.I. of 7 | (a) Provide sprinkler system. |  |
| H.I.7 | C.I. (3, 4 or 5) to 7* | Comply with Table 11.2.1.1.A. ratings for C.I. of 7 | (b) Provide 1 h rating plus sprinkler system. | *For Noncombustible construction only. |
| H.I.8 | C.I. 7 to 8 | Comply with Table 11.2.1.1.A. ratings for C.I. of 8 | (a) Provide sprinkler system. |  |
| H.I.8 | C.I. 6 to 8 | Comply with Table 11.2.1.1.A. ratings for C.I. of 8 | (b) Provide supervised sprinkler system. |  |
| H.I.8 | C.I. (3, 4 or 5) to 8* | Comply with Table 11.2.1.1.A. ratings for C.I. of 8 | (d) Provide sprinkler system, plus 1 h rating. | *For Noncombustible construction only. |
| Column 1 | 2 | 3 | 4 | 5 |

Notes to Table 11.4.3.4.A.:

(1) One asterisk (*) refers to Noncombustible construction.

(2) Two asterisks (**) refers to Combustible construction.

(3) Group B, occupancy with any H.I. shall be sprinklered.

Table 11.4.3.4.B.(1)

Additional Upgrading for Multiple Major Occupancies

Forming Part of Sentences 11.4.2.3.(4) and 11.4.3.4.(3)

| New Major Occupancy | Code Requirements | Part 11 Compliance Alternative |  |
| --- | --- | --- | --- |
| All (2) | Table 3.1.3.1. and Subsection 9.10.9 | For Existing Building | If Sprinklered |
|  | Where: | Reduce to | Reduce to |
|  | 1 h rating required | 45 min | 30 min |
|  | 2 h rating required | 1.5 h | 1 h |
|  | 3 h rating required | 2 h | 1.5 h |
| Column 1 | 2 | 3 |  |

Notes to Table 11.4.3.4.B.:

(1) For buildings with multiple major occupancies only, where there is a change in major occupancy.

(2) See Section 11.4.

Table 11.5.1.1.A.

Compliance Alternatives for Assembly Occupancies

Forming Part of Article 11.5.1.1.

| NUMBER | PART 3 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| A1 | 3.1.4.6. | Existing heavy timber construction acceptable where construction is within 90% of member sizes listed in Part 3. |
| A2 | 3.1.5.2.; 3.1.5.3.; 3.1.5.4.; 3.1.5.6. | Existing acceptable. |
| A3 | 3.1.5.7.; 3.1.5.8.; 3.1.5.9.; 3.1.5.10. | Except for exposed foamed plastics, existing acceptable. To match existing, materials may be added from on or off site. |
| A4 | 3.1.5.14.; 3.1.5.15. 3.1.5.20.; 3.1.5.16.; 3.1.5.22. | Existing acceptable. |
| A5 | 3.1.7.1. | Fire-resistance ratings may also be used where they are based on: |
|  |  | 1. HUD No. 8 Guideline on Fire Ratings of Archaic Materials and Assemblies. |
|  |  | 2. Fire Endurance of Protected Steel Columns and Beams, DBR Technical Paper No. 194. |
|  |  | 3. Fire Endurance of Unit Masonry Walls, DBR Technical Paper No. 207. |
|  |  | 4. Fire Endurance of Light-Framed and Miscellaneous Assemblies, DBR Technical Paper No. 222. |
| A6 | 3.1.7.5.(3) | Existing assemblies required to be of noncombustible construction may be supported by combustible construction having at least the same fire-resistance rating as that supported. |
| A7 | 3.1.8.5.(2) | (a) Existing functional and sound doors in existing buildings that are either hollow metal or kalamein and containing wired glass at least 6 mm thick and conforming to Sentence 3.1.8.14.(2) are permitted in lieu of doors not required to exceed 45 min, |
|  |  | (b) all existing functional and sound hollow metal or kalamein doors which carry existing 1.5 h labels are acceptable in lieu of current 1.5 h labels and may contain wired glass panels not exceeding 0.0645 m2, at least 6 mm thick and conforming to Sentence 3.1.8.14.(2), and |
|  |  | (c) every fire door, window assembly or glass block used as a closure in a required fire separation shall be installed in conformance with good engineering practice. |
| A8 | 3.1.8.7.; 3.1.8.8.; 3.1.8.9. | Fire dampers or fire stop flaps are not required to be installed in existing ducts at penetrations of existing fire separations. |
| A9 | 3.1.8.10.(1) | Existing 45 mm solid core wood doors acceptable. |
| A10 | 3.1.8.10.(1) | Existing functionally operable self-closing devices acceptable. |
| A11 | 3.1.8.13. | Existing functionally operable latching devices, excluding draw bolts, are acceptable. |
| A12 | 3.1.8.14. | Existing transoms or sidelights located in required fire separations may be retained if wired glass at least 6 mm thick is securely fixed to a steel frame with steel stops. Operable transoms shall be fixed closed. |
| A13 | 3.1.8.15.; 3.1.8.16., 3.1.8.17. | Existing acceptable. |
| A14 | 3.1.11. | Where the concealed space is being materially altered, smoke or heat detection in that space in lieu of firestops and tied into fire alarm system is acceptable. |
| A15 | 3.1.13.10. | Existing acceptable. |
| A16 | 3.2.2.17.(1)(b)and (c) | Existing sprinkler systems need not comply. |
| A17 | 3.2.3. | Existing windows. |
|  |  | (a) Existing windows in walls may be relocated to another part of the wall, provided the existing opening is blocked up to provide the same fire rating for the wall, and the projection of the new opening, at a right angle to the property line onto another building, lies not closer than 300 mm from a window in such other building, where the “opposite” window is less than 2 400 mm from the opposite new opening, and |
|  |  | (b) Except relocation of units, shall be restricted to the same fire compartment and shall conform to the requirements of Articles 3.2.3.13. or 9.10.12.4. where applicable, or |
|  |  | (c) Where a building does not satisfy the requirements of Subsection 3.2.3. for the amount of openings facing a yard or space that does not have sufficient limiting distance, such existing openings are allowed to be relocated provided: |
|  |  | (i) such openings are not increased in size and they are protected with wired glass in steel frames conforming to Sentence 3.1.8.14.(2), or |
|  |  | (ii) the building is sprinklered. |
| A18 | 3.2.4. | (a) Existing fire alarm system may remain except that Article 3.2.4.5. does not apply where the “Fire Safety Plan” (as described in Subsection 2.8.2. of the Ontario Fire Code) for the building addresses the intent of Subsection 3.2.4. (i.e., “stage” system, electrical supervision, detection as required, Fire Department connection and emergency power supply), and |
|  |  | (b) extension of an existing system must ensure continuity and compatibility, and integrity of the system. |
| A19 | 3.2.5.3.(1) and (2) | Existing acceptable. |
| A20 | 3.2.5.5.; 3.2.5.6.;3.2.5.4. | Existing acceptable provided the building is sprinklered. |
| A21 | 3.2.5.7. | Does not apply, except where a change in major occupancy occurs from a lesser hazard index. |
| A22 | 3.2.5.13. | Existing sprinkler systems in existing buildings that do not conform to NFPA 13 may be altered, added to, or extended from the existing system without complying with NFPA 13, provided the system is operational and adequate with respect to coverage, water supply and controls, and provided the system is evaluated by a qualified designer. |
| A23 | 3.2.6. Additional requirements for high buildings | Reserved |
| A24 | 3.2.9. | (a) Does not apply to buildings 6 storeys and less. |
|  |  | (b) Does not apply to sprinklered buildings. |
| A25 | 3.3.1.5. | One egress door is allowed where the occupant load is not greater than 100 persons, provided floor area is sprinklered and travel distance does not exceed 25 m. |
| A26 | 3.3.1.9. | Existing width of public corridors of not less than 914 mm is acceptable. |
| A27 | 3.3.1.9.(8) | An existing dead-end corridor is permitted where the occupant load is not greater than 20 persons, provided travel distance is not greater than 6 m plus corridor width to “exit choice” point. |
| A28 | 3.3.1.10.; 3.3.1.11. | Existing door swings may remain in heritage buildings, existing or being restored, with no change in major occupancy and with occupant load no greater than 100. |
| A29 | 3.3.1.12. | Existing doors may remain in a heritage building, existing or being restored, with no change in major occupancy. |
| A30 | 3.3.1.18. | Existing stained, etched, bevelled, leaded or figured glass acceptable. |
| A31 | 3.3.2.12. | Reserved |
| A32 | 3.3.5.4.(1); 3.3.5.7.(1) to (3) | Need not comply where a gasketed door and self closer are provided in the existing fire separation. |
| A33 | 3.4.1.5. (1) | Existing acceptable. |
| A34 | 3.4.1.5.(2) | Existing acceptable provided the existing guard is not less than 914 mm. |
| A35 | 3.4.1.8. | Existing stained, etched, bevelled, leaded or figured glass acceptable. |
| A36 | 3.4.2.5.(1) | Existing travel distance acceptable where floor area is sprinklered and where there is no change in major occupancy. |
| A37 | 3.4.3.1.(2) | Existing width of exits acceptable provided the occupant load in not more than 15% above the exit capacity. |
| A38 | 3.4.3.3.(1) | Need not comply where there is no increase in occupant load. |
| A39 | 3.4.3.5. | Existing acceptable. |
| A40 | 3.4.3.6. | Existing headroom clearance of not less than 1 980 mm is acceptable. |
| A41 | 3.4.4.4.(7) | Existing washrooms opening directly into an exit stairwell shall be separated from the exit stairwell by a 45 min closure. |
| A42 | 3.4.5.1.(2) and (7) | Existing illuminated legible exit signs are acceptable. |
| A43 | 3.4.6.2. | Existing acceptable, if visually apparent. |
| A44 | 3.4.6.3. | Existing acceptable. |
| A45 | 3.4.6.4.(2) to (8) | Existing acceptable. |
| A46 | 3.4.6.5.(2), (4) and (5) | Existing acceptable. |
| A47 | 3.4.6.6.(1) | Existing acceptable. |
| A48 | 3.4.6.7.; 3.4.6.8. | Existing acceptable. |
| A49 | 3.4.6.10.(1), (2) and (4) | Existing acceptable. |
| A50 | 3.4.6.11. | Existing acceptable in public heritage buildings or a change in occupancy with no increase in occupant load. |
| A51 | 3.4.6.15.(2) and (3) | Existing functionally operable panic hardware acceptable. |
| A52 | 3.4.7.2. | Combustible fire escapes which are protected from fire in accordance with Sentence 3.2.3.13.(2) are permitted or may be reconstructed or recreated (as in the case of a heritage building). |
| A53 | 3.5.1. | Existing acceptable. |
| A54 | 3.6.2.1.(5) | Existing fire separation of not less than 30 min is acceptable. |
| A55 | 3.6.2.3. | Existing acceptable where explosion-resistant construction or venting is provided. |
| A56 | 3.6.2.7. | Existing acceptable. |
| A57 | 3.6.2.8.(1) | 2 h fire separation acceptable. |
| A58 | 3.6.3.1.(1) to (5) | 45 min fire separation acceptable. |
| A59 | 3.6.3.3.(1) to (5) and (8) | Existing acceptable. |
| A60 | 3.6.3.3.(9) | 1 h if sprinklered. |
| A61 | 3.6.3.3.(10) | Existing acceptable. |
| A62 | 3.6.3.4. | Existing acceptable. |
| A63 | 3.6.4. | Existing acceptable. |
| A64 | 3.7.1.3.(3) | 2.1.m is acceptable. |
| A65 | 3.7.2.1.(3) | The minimum glass areas my be reduced by 50%. |
| A66 | 3.7.4.2. | Where the occupant load is increased by more than 15% above the capacity of the existing facilities, facilities to be added to accommodate the increase. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 4 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| A67 | 4.1.9. | The requirements under this Subsection do not apply. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 8 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| A68 | 8.2.1.4. | Existing clearances acceptable where: a sewage system is replaced with another sewage system within the same class; and, the capacity of the replacement sewage system does not exceed the capacity of the existing sewage system. |
| A69 | 8.2.1.4. | Existing clearances are acceptable where a replacement sewage system requires lesser clearances than those required in Part 8 for the existing sewage system. |
| Col. 1 | 2 | 3 |

Table 11.5.1.1.B.

Compliance Alternatives for Care or Detention Occupancies

Forming Part of Article 11.5.1.1.

| NUMBER | PART 3 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| B1 | 3.1.5.2.; 3.1.5.3.; 3.1.5.4.; 3.1.5.6. | Existing acceptable. |
| B2 | 3.1.5.7.; 3.1.5.8.; 3.1.5.9.; 3.1.5.10. | Except for exposed foamed plastics, existing acceptable. |
| B3 | 3.1.5.13.; 3.1.5.14.; 3.1.5.15.; 3.1.5.16.; 3.1.5.20.; 3.1.5.22. | Existing acceptable. |
| B4 | 3.1.7.1. | Fire-resistance ratings may also be used where they are based on: |
|  |  | 1. HUD No. 8 Guideline on Fire Ratings of Archaic Materials and Assemblies. |
|  |  | 2. Fire Endurance of Protected Steel Columns and Beams, DBR Technical Paper No. 194. |
|  |  | 3. Fire Endurance of Unit Masonry Walls, DBR Technical Paper No 207. |
|  |  | 4. Fire Endurance of Light-Framed and Miscellaneous Assemblies, DBR Technical Paper No. 222. |
| B5 | 3.1.7.5.(3) | Existing assemblies required to be of noncombustible construction may be supported by combustible construction having at least the same fire-resistance rating as that supported. |
| B6 | 3.1.8.5.(2) | (a) Existing functional and sound doors in existing buildings that are either hollow metal or kalamein and containing wired glass at least 6 mm thick and conforming to Sentence 3.1.8.14.(2) are permitted in lieu of doors not required to exceed 45 min, |
|  |  | (b) all existing functional and sound hollow metal or kalamein doors which carry existing 1.5 h labels are acceptable in lieu of current 1.5 h labels and may contain wired glass panels not exceeding 0.0645 m2, at least 6 mm thick and conforming to Sentence 3.1.8.14.(2), and |
|  |  | (c) every fire door, window assembly or glass block used as a closure in a required fire separation shall be installed in conformance with good engineering practice. |
| B7 | 3.1.8.7.; 3.1.8.8.; 3.1.8.9. | Fire dampers or fire stop flaps are not required to be installed in existing ducts at penetrations of existing fire separations. |
| B8 | 3.1.8.10.(1) | For existing unlabelled doors in existing buildings, at least 45 mm solid core wood or metal clad are acceptable. |
| B9 | 3.1.8.11.(1) | Existing functionally operable self-closing devices acceptable, including devices with “pause” hardware. |
| B10 | 3.1.8.12.(1) and (2) | Between patient or inmate rooms, and corridors, existing “pause” type self-closing devices may be used as hold-open devices where functionally operable. |
| B11 | 3.1.8.13. | Existing functionally operable latching devices, excluding draw bolts, are acceptable. |
| B12 | 3.1.8.14.(1) and (2) | Except in zone or exit fire separations not required to be greater than 1 h, existing wired glass installations may be acceptable provided they are set in steel or metal-clad frames. |
| B13 | 3.1.8.14.(3) | Existing glass block acceptable. |
| B14 | 3.1.8.15.; 3.1.8.16.; 3.1.8.17. | Existing acceptable. |
| B15 | 3.1.9.5.(1) and (2) | Existing openings in existing ceiling membranes to remain. Existing openings may be moved to another location in the same ceiling provided the aggregate area of openings does not increase and are not cumulative, and the existing opening is blocked up to provide the same rating as the ceiling assembly. |
| B16 | 3.1.11. | Where the concealed space is being materially altered, provide smoke or heat detection in that space in lieu of firestops and tie into fire alarm system. |
| B17 | 3.1.14.; 3.1.15. | Existing roof assemblies and roof coverings acceptable. |
| B18 | 3.2.3. | Existing windows |
|  |  | (a) Existing windows in walls may be relocated to another part of the wall, provided the existing opening is blocked up to provide the same fire rating for the wall, and the projection of the new opening, at a right angle to the property line onto another building, lies no closer than 300 mm from a window in such other building, where the “opposite” window is less than 2 400 mm from the opposite new opening, and |
|  |  | (b) except relocation of units, to be restricted to the same fire compartment and shall conform to the requirements of Articles 3.2.3.13. or 9.10.12.4. where applicable, or |
|  |  | (c) where a building does not satisfy the requirements of Subsection 3.2.3. for the amount of openings facing a yard or space that does not have sufficient limiting distance, such existing openings are allowed to be relocated provided: |
|  |  | (i) such openings are not increased in size and they are protected with wired glass in steel frames conforming to Sentence 3.1.8.14.(2), or |
|  |  | (ii) the building is sprinklered. |
| B19 | 3.2.4. | (a) Existing fire alarm system may remain except that Article 3.2.4.5. does not apply where the “Fire Safety Plan” (as described in Subsection 2.8.2. of the Ontario Fire Code) for the building addresses the intent of Subsection 3.2.4. (i.e. “stage” system, electrical supervision, detection as required, Fire Department connection, and emergency power supply), and |
|  |  | (b) extension of an existing system must ensure continuity and compatibility, and integrity of the system. |
| B20 | 3.2.5.1.; 3.2.5.2. | Existing access to an existing occupancy acceptable. Where the existing building is changed to a “B” occupancy, existing access may be acceptable. |
| B21 | 3.2.5.3.(1) | Existing acceptable, except where a change in occupancy occurs to a “B1” or “B2” occupancy. |
| B22 | 3.2.5.3.(2) | Existing acceptable. |
| B23 | 3.2.5.4.; 3.2.5.5.; 3.2.5.6. | Existing access route to existing occupancy is acceptable if the building is sprinklered. Where existing building is changed to a “B” occupancy, access route shall be provided. |
| B24 | 3.2.5.7.; 3.2.5.18. | Does not apply except where a change in occupancy occurs to a “B1” or “B2” occupancy, where occupants are not normally evacuated from the building. |
| B25 | 3.2.5.13. | Existing sprinkler systems in existing buildings that do not conform to NFPA 13 may be altered, added to, or extended from the existing system without complying with NFPA 13, provided the system is operational and adequate with respect to coverage, water supply and controls, and provided the system is evaluated by a qualified designer. |
| B26 | 3.2.6. Additional requirements for high buildings | Reserved |
| B27 | 3.2.9. | Does not apply except where a change in occupancy occurs to a Group B occupancy, where occupants are not normally evacuated from the building. |
| B28 | 3.3.1.5.(1)(c); Table 3.3.1.5. | Column 2 to read: 100 m2 for “B1” and “B2” (sleeping rooms) and 200 m2 for “B2” (other rooms). |
| B29 | 3.3.1.9. | Existing width of public corridors of not less than 914 mm is acceptable, except as provided in Sentence 3.3.3.3.(2). |
| B30 | 3.3.1.10.; 3.3.1.11. | Existing door swings may remain in heritage buildings, existing or being restored, with no change in major occupancy and with occupant load no greater than 100. |
| B31 | 3.3.1.12. | Existing doors acceptable. |
| B32 | 3.3.1.15. | Existing acceptable. |
| B33 | 3.3.1.16. | Existing non-conforming capacities of access to exits are acceptable, provided that the excessive capacity is no greater than 15%, and |
|  |  | (a) corridor separations are rated to Code plus early warning system provided, or |
|  |  | (b) there are sprinklers, plus smoke alarms in suites. |
| B34 | 3.3.1.17. | Existing acceptable. |
| B35 | 3.3.1.18. | Existing stained, etched, bevelled, leaded or figured glass acceptable. |
| B36 | 3.3.3.3.(1) | Existing dead end corridors acceptable with 30 min fire separation of corridor plus sprinklering of floor area, provided the occupant load is not greater than 10 persons and travel distance not greater than 6 m plus corridor width to “exit choice” point. |
| B37 | 3.3.3.7. | 45 min fire separation acceptable. |
| B38 | 3.3.5.5.(1); 3.3.5.8.(1) and (3) | Need not comply where a gasketed door and self closer are provided in the existing fire separation. |
| B39 | 3.4.1.8. | Existing stained, etched, bevelled, leaded or figured glass acceptable. |
| B40 | 3.4.2.5.(1) | Existing travel distance acceptable where floor area is sprinklered and provided fire separations comply with Part 3 of the Code. |
| B41 | 3.4.3.1.(2) | Existing acceptable provided there is no change in occupancy to a “B2” or “B3“. |
| B42 | 3.4.3.5. | Existing acceptable. |
| B43 | 3.4.3.6. | Existing headroom clearance of not less than 1 980 mm is acceptable. |
| B44 | 3.4.5.1.(2) and (7) | Existing illuminated legible exit signs are acceptable. |
| B45 | 3.4.6.2. | Existing acceptable, if visually apparent. |
| B46 | 3.4.6.3.(1) | Existing acceptable with a rise of no greater than 3.7 m. |
| B47 | 3.4.6.3.(2) | Existing acceptable provided there is no change in occupancy to a “B2” or “B3“. |
| B48 | 3.4.6.4.(2) to (9) | Existing acceptable. |
| B49 | 3.4.6.5.(2) to (5) | Existing acceptable. |
| B50 | 3.4.6.6.(1) | Existing acceptable. |
| B51 | 3.4.6.7. | Existing acceptable. |
| B52 | 3.4.6.8. | Existing acceptable where there is no change in major occupancy or increase in occupant load greater than 15%. |
| B53 | 3.4.6.10.(1), (2) and (4) | Existing acceptable. |
| B54 | 3.4.6.11. | Existing acceptable in public heritage buildings. |
| B55 | 3.4.6.15.(2) and (3) | Existing functionally operable panic hardware acceptable. |
| B56 | 3.4.6.17.(1)(c) | Existing access to existing occupancy is acceptable. Where the existing building is changed to a “B” occupancy, existing access may be acceptable. |
| B57 | 3.4.7.2. | Combustible fire escapes which are protected from fire in accordance with Sentence 3.2.3.13.(2) are permitted or may be reconstructed or recreated (as in the case of a heritage building). Where serving non-ambulatory persons, minimum width shall be 1 100 mm. |
| B58 | 3.5.1. | Existing acceptable, except where building is classified under Subsection 3.2.6. |
| B59 | 3.6.2.1.(5) | 45 min fire separation acceptable. |
| B60 | 3.6.2.7. | Existing acceptable. |
| B61 | 3.6.2.8.(1) | 2 h fire separation acceptable. |
| B62 | 3.6.3.1.(1) to (5) | 45 min fire separation acceptable. |
| B63 | 3.6.3.3.(1), (3), (4)(a), (5) and (10) | Existing acceptable. |
| B64 | 3.6.3.3.(2)(a) | 45 min fire separation acceptable. |
| B65 | 3.6.4. | Existing acceptable, except where a change in occupancy occurs to a Group B occupancy. |
| B66 | 3.7.1.3.(1) | Existing acceptable. |
| B67 | 3.7.2.1.(2) | The minimum glass areas my be reduced by 50%. |
| B68 | 3.7.4.2. | Where the occupant load is increased by more than 15% above the capacity of the existing facilities, facilities to be added to accommodate the increase. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 4 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| B69 | 4.1.9. | The requirements under this Subsection do not apply. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 8 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| B70 | 8.2.1.4. | Existing clearances acceptable where: a sewage system is replaced with another sewage system within the same class; and, the capacity of the replacement sewage system does not exceed the capacity of the existing sewage system. |
| B71 | 8.2.1.4. | Existing clearances are acceptable where a replacement sewage system requires lesser clearances than those required in Part 8 for the existing sewage system. |
| Col. 1 | 2 | 3 |

Table 11.5.1.1.C.

Compliance Alternatives for Residential Occupancies

Forming Part of Article 11.5.1.1.

| NUMBER | PART 3 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| C1 | 3.1.4.6. | Existing heavy timber construction acceptable where construction is within 90% of member sizes listed in Part 3. |
| C2 | 3.1.5.2.; 3.1.5.3.; 3.1.5.4.; 3.1.5.6. | Existing acceptable. |
| C3 | 3.1.5.7.; 3.1.5.8.; 3.1.5.9.; 3.1.5.10. | Except for exposed foamed plastics, existing acceptable. To match existing, materials may be added from on or off site. |
| C4 | 3.1.5.13.; 3.1.5.14.; 3.1.5.15.; 3.1.5.16.; 3.1.5.20.; 3.1.5.22. | Existing acceptable. |
| C5 | 3.1.7.1. | Fire-resistance ratings may also be used where they are based on: |
|  |  | 1. HUD No. 8 Guideline on Fire Ratings of Archaic Materials and Assemblies. |
|  |  | 2. Fire Endurance of Protected Steel Columns and Beams, DBR Technical Paper No. 194. |
|  |  | 3. Fire Endurance of Unit Masonry Walls, DBR Technical Paper No. 207. |
|  |  | 4. Fire Endurance of Light-Framed and Miscellaneous Assemblies, DBR Technical Paper No. 222. |
| C6 | 3.1.7.5.(3) | Existing assemblies required to be of noncombustible construction may be supported by combustible construction having at least the same fire-resistance rating as that supported. |
| C7 | 3.1.8.1.(2); 3.1.8.6.(1) and (2) | Existing functional closures are acceptable and may be relocated within the same existing fire separation. |
| C8 | 3.1.8.5.(2) | (a) Existing functional and sound doors in existing buildings that are either hollow metal or kalamein and containing wired glass at least 6 mm thick and conforming to Sentence 3.1.8.14.(2) are permitted in lieu of doors not required to exceed 45 min, |
|  |  | (b) all existing functional and sound hollow metal or kalamein doors which carry existing 1.5 h labels are acceptable in lieu of current 1.5 h labels and may contain wired glass panels not exceeding 0.0645 m2, at least 6 mm thick and conforming to Sentence 3.1.8.14.(2), and |
|  |  | (c) every fire door, window assembly or glass block used as a closure in a required fire separation shall be installed in conformance with good engineering practice. |
| C9 | 3.1.8.7.; 3.1.8.8.; 3.1.8.9. | Except for hotels, fire dampers or fire stop flaps are not required to be installed in existing ducts at penetrations of existing fire separations. |
| C10 | 3.1.8.10.(1) | For existing unlabeled doors in existing buildings, at least 45 mm solid core wood or metal clad are acceptable. Except for residential occupancies, existing closure rating of 20 min will not be required where the entire floor area is sprinklered. |
| C11 | 3.1.8.13. | Existing functionally operable latching devices, excluding draw bolts, are acceptable. |
| C12 | 3.1.8.14. | Existing transoms or sidelights located in fire separations not required to be greater than 1 h may be retained if wired glass, at least 6 mm thick, is securely fixed to a wood frame of at least 50 mm thickness with steel stops. Operable transoms shall be fixed closed. |
| C13 | 3.1.8.15.; 3.1.8.16.; 3.1.8.17. | Existing acceptable. |
| C14 | 3.1.11. | Where the concealed space is being materially altered, provide smoke or heat detection in that space in lieu of firestops and tie into fire alarm system. |
| C15 | 3.2.2.17.(1)(b) and (c) | Existing sprinkler systems in 1 storey buildings need not comply. |
| C16 | 3.2.3. | Existing windows |
|  |  | (a) Existing windows in walls may be relocated to another part of the wall, provided the existing opening is blocked up to provide the same fire rating for the wall, and the projection of the new opening, at a right angle to the property line onto another building, lies not closer than 300 mm from a window in such other building, where the “opposite” window is less than 2 400 mm from the opposite new opening, and |
|  |  | (b) Except relocation of units, shall be restricted to the same fire compartment and shall conform to the requirements of Articles 3.2.3.13. or 9.10.12.4. where applicable, or |
|  |  | (c) Where a building does not satisfy the requirements of Subsection 3.2.3. for the amount of openings facing a yard or space that does not have sufficient limiting distance, such existing openings are allowed to be relocated provided: |
|  |  | (i) such openings are not increased in size and they are protected with wired glass in steel frames conforming to Sentence 3.1.8.14.(2), or |
|  |  | (ii) the building is sprinklered. |
| C17 | 3.2.4. | (a) Existing fire alarm system may remain except that Article 3.2.4.5. does not apply where the “Fire Safety Plan” (as described in Subsection 2.8.2. of the Ontario Fire Code) for the building addresses the intent of Subsection 3.2.4. (i.e. “stage” system, electrical supervision, detection as required, Fire Department connection, and emergency power supply), and |
|  |  | (b) extension of an existing system must ensure continuity and compatibility, and integrity of the system. |
| C18 | 3.2.4.21. | Such smoke alarms may be battery operated. |
| C19 | 3.2.5.1.; 3.2.5.2. | Existing acceptable. |
| C20 | 3.2.5.3.(1) | Existing access acceptable. |
| C21 | 3.2.5.3.(2) | Existing acceptable. |
| C22 | 3.2.5.4.; 3.2.5.5.; 3.2.5.6. | (a) For buildings 6 storeys and less, existing access to existing occupancy is acceptable, and |
|  |  | (b) Where existing building is changed to a “C” occupancy, an access route shall be provided, or the existing access is acceptable provided the building is sprinklered. |
| C23 | 3.2.5.7. | Existing water supply and hydrants are acceptable in buildings up to 6 storeys in building height. |
| C24 | 3.2.5.13. | Existing sprinkler systems in existing buildings that do not conform to NFPA 13 may be altered, added to, or extended from the existing system without complying with NFPA 13, provided the system is operational and adequate with respect to coverage, water supply and controls, and provided the system is evaluated by a qualified designer. |
| C25 | 3.2.6. Additional requirements for high buildings | Reserved |
| C26 | 3.2.9. | Does not apply to buildings 4 storeys and less. For existing buildings over 4 storeys in building height, existing standpipe and hose systems water supply is acceptable provided it can deliver a minimum flow rate of 265 L/min for 30 min at 345 kPa (gauge) at the two highest and most remote hose valves, with not less than 132 L/min from each of the two simultaneously. |
| C27 | 3.3.1.4.(1); 3.3.4.2.(1) | 30 min is acceptable to separate corridors or exits in buildings not exceeding 6 storeys in building height, except that 45 min is required for exits in buildings exceeding 3 storeys in building height. For buildings exceeding 6 storeys in building height, 30 min is acceptable where smoke detectors are installed in corridors, except 1 h is required in exits. 30 min is acceptable to separate public corridors, exits or suites in hotels, provided fire detectors are installed in every room in a suite and in every room not located in a suite, other than corridors, washrooms, closets in suites, saunas, refrigerated areas and swimming pools. |
| C28 | 3.3.1.5.(1)(c); Table 3.3.1.5. | In Column 2, maximum area of room or suite to be unlimited. |
| C29 | 3.3.1.9. | Existing width of public corridors of not less than 914 mm is acceptable. |
| C30 | 3.3.1.10.; 3.3.1.11. | Existing door swings may remain in heritage buildings, existing or being restored, with no change in major occupancy and with occupant load no greater than 100. |
| C31 | 3.3.1.12. | Existing doors acceptable, provided not less than 600 mm wide. |
| C32 | 3.3.1.15. | Existing curved or spiral stairs acceptable. |
| C33 | 3.3.1.16. | Existing non-conforming capacities of access to exits are acceptable, provided that the excessive capacity is no greater than 15%, |
|  |  | (a) corridor fire separations are to be rated to Code plus early warning system provided, or |
|  |  | (b) there are sprinklers, plus smoke alarms in suites. |
| C34 | 3.3.1.17. | Does not apply to heritage buildings. |
| C35 | 3.3.1.18. | Existing stained, etched, bevelled, leaded or figured glass acceptable. |
| C36 | 3.3.4.2.(2)(a) (b) (c) | 30 min fire separation acceptable. 45 min fire separation acceptable. 1.5 h fire separation acceptable. |
| C37 | 3.3.4.4.(5) and (6) | For buildings 6 storeys and less, doorway from dwelling unit will be permitted to open directly into exit stairway or interior corridor served by a single exit if a fire alarm system complying with Subsection 3.2.4. is installed and the dwelling unit has a second and separate means of egress. |
| C38 | 3.3.5.5.(1) and 3.3.5.8.(3) | Need not comply where a gasketed door and self closer are provided in the existing fire separation. |
| C39 | 3.4.1.4. | Except for hotels, the following types of exits may also be used for buildings not over 6 storeys in building height |
|  |  | (a) connected balconies, which connect across firewalls, or connect to another exit, or with access to ground level. |
|  |  | (b) areas of refuge where fire service rescue is possible and that comply with Measure L of Sentences (4) to (10), (18) and (20)(a), (b) and (d) in the Supplementary Guideline. |
| C40 | 3.4.1.8. | Existing stained, etched, bevelled, leaded or figured glass acceptable. |
| C41 | 3.4.2.5.(1) | Existing travel distance acceptable where floor area is sprinklered and provided fire separations comply with Part 3 of the Code. |
| C42 | 3.4.3.1.(2) | Existing width of exits acceptable provided the occupant load is not more than 15% above the exit capacity. |
| C43 | 3.4.3.5. | Except for heritage buildings, existing acceptable, provided not less than 800 mm. |
| C44 | 3.4.3.6. | Existing headroom clearance of not less than 1 980 mm is acceptable. |
| C45 | 3.4.4.1.(1) | Except for exits, no rating required where floor areas are spinklered. |
| C46 | 3.4.4.1. | Fire separations of exits permitted in buildings: — 30 min, up to 3 storeys in building height; — 45 min, in hotels up to 3 storeys in building height; — 45 min, up to 6 storeys in building height; — 1 h, over 6 storeys in building height. |
| C47 | 3.4.4.4.(7) | Existing washrooms opening directly into an exit stairwell shall be separated from the exit stairwell by a 45 min closure. |
| C48 | 3.4.5.1.(2) and (7) | Existing illuminated legible exit signs are acceptable. |
| C49 | 3.4.6.1. | Existing acceptable. |
| C50 | 3.4.6.2. | Existing acceptable, if visually apparent. |
| C51 | 3.4.6.3.(1) and (2) | Existing acceptable with rise no greater than 3.7 m. |
| C52 | 3.4.6.3.(3) and (4) | Existing acceptable. |
| C53 | 3.4.6.4.(2) and (8) | Existing acceptable. |
| C54 | 3.4.6.5. (2) and (4) | Existing acceptable. |
| C55 | 3.4.6.6.(1) | Existing acceptable. |
| C56 | 3.4.6.7.; 3.4.6.8. | Existing acceptable. |
| C57 | 3.4.6.9.(2) to (6) | Existing acceptable. |
| C58 | 3.4.6.10.(1) and (2) | Existing acceptable. |
| C59 | 3.4.6.11. | Existing acceptable in heritage buildings provided the occupant load is not more than 60. |
| C60 | 3.4.6.15.(1) to (3) | Existing functionally operable panic hardware acceptable. |
| C61 | 3.4.7.2. | Combustible fire escapes which are protected from fire in accordance with Sentence 3.2.3.13.(2) are permitted or may be reconstructed or recreated (as in the case of a heritage building). |
| C62 | 3.5.1. | Existing acceptable except where building is classified under Subsection 3.2.6. |
| C63 | 3.6.2.1.(5) | 45 min fire separation acceptable. |
| C64 | 3.6.2.3. | Existing acceptable where explosion-resistant construction or venting is provided. |
| C65 | 3.6.2.7. | Existing acceptable. |
| C66 | 3.6.2.8.(1) | 2 h fire separation acceptable. |
| C67 | 3.6.3.1.(1) to (5) | 45 min fire separation acceptable up to 6 storeys. |
| C68 | 3.6.3.3.(2) | Where 2 h fire separation is required,1 h is acceptable. Except for linen discharge rooms where 1 h fire separation is required, 45 min is acceptable. |
| C69 | 3.6.3.3.(4) and (5) | Existing sizes acceptable. |
| C70 | 3.6.3.3.(9) | Where 2 h fire separation is required, 1 h is acceptable. |
| C71 | 3.6.4.2. | Ceiling fire separation need not be fire-resistance rated where sprinklering, subject to C.A. C24, of fire compartments on both sides of vertical fire separation is provided and where such fire separation is not required to exceed 1 h. |
| C72 | 3.6.4.3.(1) | Existing to meet flame-spread rating of 25 or to be sprinklered. |
| C73 | 3.6.4.4.; 3.6.4.5.; 3.6.4.6. | Existing access acceptable. |
| C74 | 3.7.1.1.(2) | Minimum room height shall be not less than 1 950 mm over the required floor area and any location that would normally be used as a means of egress. |
| C75 | 3.7.2.1. | (a) Where windows are not used as means of egress and where they do not conflict with ventilation requirements, the minimum glass areas as shown in Table 9.7.1.2. may be reduced by 50%, or |
|  |  | (b) an existing room converted to an interior room, created by an addition, shall not require a window, provided there is an opening in a dividing wall occupying not less than 30% of the separating plane to an adjoining room, where the adjoining room has a minimum of 5% window area of the combined floor areas, and provided the required ventilation for the combined rooms is maintained. |
| C76 | 3.7.4.2. | Where the occupant load is increased by more than 15% above the capacity of the existing facilities, facilities to be added to accommodate the increase. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 4 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| C77 | 4.1.9. | The requirements under this Subsection do not apply. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 6 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| C78 | 6.2.3.2.; 6.2.3.5.; 6.2.3.6.; 6.2.3.12. | Existing acceptable. |
| C79 | 6.2.3.13.(2) | In a building containing not more than four dwelling units, the existing heating or air conditioning system may be altered to serve more than one dwelling unit provided smoke alarms are installed in each dwelling unit and provided a smoke detector is installed in the supply or return air duct system serving the entire building which would turn off the fuel supply and electrical power to the heating system upon activation of such detector. |
| C80 | 6.2.3.17. | Existing openings, grilles and diffusers acceptable. |
| C81 | 6.2.4.2.(1); 6.2.4.5.(1) to (3) | Existing acceptable. |
| C82 | 6.2.4.5.(10) | Where the duct system is being altered, lesser amounts and extent of insulation will be permitted. |
| C82.1 | 6.2.5A.3.(1) | Carbon monoxide detectors may be battery operated or plugged into an electrical outlet. |
| C83 | 6.2.9.2. | Existing acceptable. |
| C84 | 6.3.1. | Existing acceptable, provided products of combustion are safely vented. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 8 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| C84.1 | 8.2.1.4. | Existing clearances acceptable where: a sewage system is replaced with another sewage system within the same class; and, the capacity of the replacement sewage system does not exceed the capacity of the existing sewage system. |
| C84.2 | 8.2.1.4. | Existing clearances are acceptable where a replacement sewage system requires lesser clearances than those required in Part 8 for the existing sewage system. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 9 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| C85 | 9.3.2.1. | Sound used lumber may be acceptable for reuse without a grade stamp provided that: |
|  |  | (a) visual examination shows no excessive weakening by holes, notches, nail splits or other damage, |
|  |  | (b) where the grade or species is unknown, the minimum grade shall apply for span table use, and |
|  |  | (c) lumber has not been subjected to termite infestation. |
| C86 | 9.5.3.1. | In detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, |
|  |  | (a) minimum room height shall not be less than 1 950 mm over the required floor area and in any location that would normally be used as a means of egress, or |
|  |  | (b) minimum room height shall not be less than 2 030 mm over at least 50% of the required floor area, provided that any part of the floor having a clear height of less than 1 400 mm shall not be considered in computing the required floor area. |
| C87 | 9.6.3.1. | Doors may be lesser heights to suit ceiling heights. |
| C88 | 9.6.3.2. | Except where required in 9.9.2.7. existing acceptable, provided not less than 600 mm. |
| C89 | 9.6.5. | Existing acceptable. |
| C90 | 9.6.6.2.; 9.6.6.3. | Existing doors and sidelights being reused or relocated need not conform if identified or protected. |
| C91 | 9.7.1.2. | (a) Where windows are not used as a means of egress and where they do not conflict with ventilation requirements, the minimum glass areas as shown in Table 9.7.1.2. may be reduced by 50%, and |
|  |  | (b) an existing room converted to an interior room created by an addition shall not require a window, provided there is an opening in a dividing wall occupying not less than 30% of the separating plane to an adjoining room where the adjoining room has a minimum of 5% window area of the combined floor areas, and provided the required ventilation for the combined room is maintained. |
| C92 | 9.7.1.3. | In detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, existing acceptable, where there is direct access to the exterior. |
| C93 | 9.7.1.7. | Existing acceptable. |
| C94 | 9.7.5.1. | Existing acceptable, if marked to indicate their existence and position. |
| C95 | 9.8.1. to 9.8.4. | Replacement or extension of existing stair systems shall be exempt from the provisions of these Articles, except that they shall have: |
|  |  | (a) a minimum width between wall faces of 700 mm, and |
|  |  | (b) a minimum clear height over tread nosing of or landing 1 800 mm. |
| C96 | 9.8.5.2. | Existing curved or spiral stairs are acceptable. |
| C97 | 9.8.5.3. | Where a stair complies with Subsection 9.8.3., an extension to a stair may contain two sets of winders provided that they are separated by at least 3 treads or a landing. |
| C98 | 9.8.6. | Existing ramps acceptable, where practical. |
| C99 | 9.8.7. | Existing handrails acceptable, unless considered unsafe by chief building official. |
| C100 | 9.8.8. | Existing guards acceptable, unless considered unsafe by chief building official. |
| C101 | 9.8.9.5.(2) | Existing acceptable. |
| C102 | 9.9.2.2. | Except for hotels, the following types of exits may also be used: |
|  |  | (a) connected balconies, which connect across firewalls, or connect to another exit, or with access to ground level, |
|  |  | (b) areas of refuge approved by the chief building official, where fire service rescue is possible, or |
|  |  | (c) combustible or noncombustible exterior stairways or fire escapes which are protected in accordance with Sentence 3.2.3.13.(2). These may be reconstructed or recreated (as in the case of a heritage building). |
| C103 | 9.9.2.6. | Existing acceptable, provided that the enclosure has a 45 min fire-resistance rating. |
| C104 | 9.9.2.7. | Except for hotels, existing acceptable. |
| C105 | 9.9.3.2. | (a) In a building containing not more than four dwelling units, the width of every exit facility may be as the existing, but not less than 800 mm, or |
|  |  | (b) In a building containing more than four dwelling units, the width of every exit facility may be as the existing, but not less than 900 mm. |
| C106 | 9.9.3.3. | (a) In a building containing not more than four dwelling units, the minimum width of a public corridor may be 800 mm, or |
|  |  | (b) In a building containing more than four dwelling units, the minimum width of a public corridor may be 900 mm. |
| C107 | 9.9.3.4. | Existing headroom clearance of not less than 1 950 mm is acceptable. |
| C108 | 9.9.4.2. | Except as permitted in C122, in a building containing not more than four dwelling units or suites, one exit need not be separated from the remainder of the building at the first storey where there are one or more other exits complying with C109. |
| C109 | 9.9.4.2.(1) and (2) | 30 min fire separation acceptable. |
| C110 | 9.9.5.4. | Existing acceptable. |
| C111 | 9.9.5.8. | Existing acceptable provided minimum 45 min fire separation and where explosion-resistant construction or venting is provided. |
| C112 | 9.9.6.2. | Except for hotels, existing acceptable. |
| C113 | 9.9.6.3. | Existing headroom clearance of not less than 1 950 mm is acceptable, with existing door heights to be acceptable. |
| C114 | 9.9.6.4. | Existing door widths and heights are acceptable, provided exit widths and heights conform to C.A.’s C105 and C107. |
| C115 | 9.9.6.5. | Existing door swings acceptable. Existing acceptable in public heritage buildings, where approved by chief building official. |
| C116 | 9.9.6.6.(1) | Where exit doors open onto a landing, they shall not extend beyond the face of the first riser. |
| C117 | 9.9.6.10. | Existing functionally operable passage or panic hardware acceptable. |
| C118 | 9.9.7.3.(1)(a) | Maximum area of existing room or suite does not apply. |
| C119 | 9.9.7.4. | Except as provided in C122, in detached houses, semi-detached houses, townhouses row houses containing not more than two dwelling units, requirement applies. |
| C120 | 9.9.8.2.(1) | Existing travel distance acceptable where floor area is sprinklered and provided fire separations comply with Part 9 of the Code. |
| C121 | 9.9.8.5. | In a building containing not more than four dwelling units or suites, existing glazed solid wood doors to lobby may remain in lieu of new 20 minute doors, provided the fire separations for the floor above or below are provided as per C.A. C132, and a second means of egress from the dwelling units complies with the Code requiremen |
| C122 | 9.9.9. | In detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, exit requirements are acceptable if at least one of the following conditions exists: |
|  |  | (a) a door, including a sliding door, that opens directly to the exterior from a dwelling unit, serves only that dwelling unit and has reasonable access to ground level, and the dwelling units are equipped with smoke alarms installed in conformance with Subsection 9.10.18., |
|  |  | (b) an exit that is accessible to more than one dwelling unit and provides the only means of egress from each dwelling unit, provided that the means of egress is separated from the remainder of the building and common areas by a fire separation having a 30 min fire-resistance rating and provided further that the required access to exit from any dwelling unit cannot be through another dwelling unit, service room or other occupancy, and both dwelling units and common areas are provided with smoke alarms installed in conformance with Subsection 9.10.18. and are interconnected, or |
|  |  | (c) access to an exit from one dwelling unit which leads through another dwelling unit where |
|  |  | (i) an additional means of escape is provided through a window that conforms to the following: |
|  |  | - the sill height is not more than 1 000 mm above or below adjacent ground level, |
|  |  | - the window can be opened from the inside without the use of tools, |
|  |  | - the window has an individual unobstructed open portion having a minimum area of 0.38 m2 with no dimension less than 460 mm, |
|  |  | - the sill height does not exceed 900 mm above the floor or fixed steps, |
|  |  | - where the window opens into a window well, a clearance of not less than 1 000 mm shall be provided in front of the window, and |
|  |  | - smoke alarms are installed in every dwelling unit and in common areas in conformance with Subsection 9.10.18. and are interconnected, |
|  |  | (ii) an additional means of escape is provided through a window that conforms to the following: |
|  |  | - a casement window not less than 1 060 mm high, 560 mm wide, with a sill height not more than 900 mm above the inside floor, |
|  |  | - the sill height of the window is not more than 5 m above adjacent ground level, and |
|  |  | - smoke alarms are installed in every dwelling unit and in common areas in conformance with Subsection 9.10.18. and are interconnected, or |
|  |  | (iii) the building is sprinklered and the dwelling units are equipped with smoke alarms installed in conformance with Subsection 9.10.18. |
| C123 | 9.9.10. | In detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, the requirements under this Subsection do not apply. |
| C124 | 9.9.10.6. | Existing illuminated legible signs are acceptable for exit signs, if approved by chief building official. |
| C125 | 9.9.11. | In detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, the requirements under this Subsection apply only where the condition described in (b) of C122 exists. |
| C126 | 9.10.1.1. | Assemblies required to be of noncombustible construction may be supported by combustible construction having at least the same fire-resistance rating as that supported. |
| C127 | 9.10.1.3.(8) | Existing installations acceptable subject to C.A.’s C23, C24 and C26. |
| C128 | 9.10.3. | Fire-resistance ratings may also be used where they are based on: |
|  |  | 1. HUD No. 8 Guideline on Fire Ratings of Archaic Materials and Assemblies. |
|  |  | 2. Fire Endurance of Protected Steel Columns and Beams, DBR Technical Paper No. 194. |
|  |  | 3. Fire Endurance of Unit Masonry Walls, DBR Technical Paper No. 207. |
|  |  | 4. Fire Endurance of Light-Framed and Miscellaneous Assemblies, DBR Technical Paper No. 222. |
| C129 | 9.10.5.1. | Existing openings in existing wall or ceiling membranes to remain. Existing openings may be moved to another location in the same wall or ceiling, provided the aggregate area of openings does not increase and are not accumulative, and the existing opening is blocked up to provide the same rating as the existing wall or ceiling assembly. |
| C130 | 9.10.6.2. | Existing heavy timber construction acceptable where construction is within 90% of member sizes listed in Part 3. |
| C131 | 9.10.7. | Existing acceptable for heritage buildings, subject to approval of chief building official. |
| C132 | 9.10.8.1.; 9.10.8.3.; 9.10.8.7. | (a) Except as provided in (b) and (c), 30 min rating is acceptable. |
|  |  | (b) In detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, 15 min horizontal fire separation is acceptable where |
|  |  | (i) smoke alarms are installed in every dwelling unit and in common areas in conformance with Subsection 9.10.18., and |
|  |  | (ii) smoke alarms are interconnected. |
|  |  | (c) In detached houses, semi-detached houses townhouses and row houses containing not more than two dwelling units, the fire- resistance rating of the fire separation is waived where the building is sprinklered. |
| C133 | 9.10.9.7.; 9.10.9.9. | Existing acceptable in existing fire separations. |
| C134 | 9.10.9.10.(1) | Ceiling fire separation need not be fire-resistance rated where sprinklering, subject to C.A. C24, of fire compartments on both sides of vertical fire separation is provided and where such fire separation is not required to exceed 1 h. |
| C135 | 9.10.9.11.(1) | Except for hotels, 30 min fire separation acceptable. |
| C136 | 9.10.9.11.(2) | In lieu of the 2 h fire separation, sprinklers may be used in the mercantile occupancy or medium hazard industrial occupancy, with a 1 h fire separation. |
| C137 | 9.10.9.14.(1), (3); 9.10.9.15.(1) | (a) Except as provided in (b) and (c), 30 min fire separation is acceptable, |
|  |  | (b) In detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, 15 min horizontal fire separation is acceptable where |
|  |  | (i) smoke alarms are installed in every dwelling unit and in common areas in conformance with Subsection 9.10.18., and |
|  |  | (ii) smoke alarms are interconnected, |
|  |  | (c) in detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, the fire-resistance rating of the fire separation is waived where the building is sprinklered. |
| C138 | 9.10.10.3. | (a) except as provided in (b) and (c) and in Articles 9.10.10.5. and 9.10.10.6., 30 min fire separation is acceptable, |
|  |  | (b) in detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, the fire-resistance rating of the vertical fire separation is waived where |
|  |  | (i) smoke alarms are installed in every dwelling unit and in common areas in conformance with Subsection 9.10.18., and |
|  |  | (ii) smoke alarms are interconnected, |
|  |  | (c) in detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, the fire-resistance rating of the vertical fire separation is waived where service rooms are sprinklered. |
| C139 | 9.10.11.2.(1) | In detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, a party wall with 1 h fire-resistance rating is acceptable. |
| C140 | 9.10.13.1 | Existing functional closures are acceptable subject to C.A. C8. and C141. |
| C141 | 9.10.13.1. | In detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, existing unlabelled doors at least 45 mm solid core wood or metal clad are acceptable. For existing closures, ratings of 20 min will not be required where the entire floor area is sprinklered. |
| C142 | 9.10.13.2.(1) | In a building containing not more than four dwelling units or suites, existing glazed solid wood doors to corridors may remain in lieu of new 20 min doors, provided they are not located in a dead end corridor. |
| C143 | 9.10.13.3. | Existing acceptable provided that wood door frames are secured with hinge screws going through frame into the stud. |
| C144 | 9.10.13.5. | Existing wired glass acceptable. Existing transoms or sidelights located in required fire separations may be retained if wired glass at least 6 mm thick is securely fixed to a wood frame of at least 50 mm thickness with steel stops. Operable transoms shall be fixed closed. |
| C145 | 9.10.13.6. | Existing steel door frames acceptable. |
| C146 | 9.10.13.7. | Existing glass block acceptable. |
| C147 | 9.10.13.8. | Existing sizes acceptable. |
| C148 | 9.10.13.9. | Existing operable latches acceptable. |
| C149 | 9.10.13.10.(1) | Existing functionally operable self-closing devices acceptable. |
| C150 | 9.10.13.11. | Existing operable self-releasing electromagnetic hold-open device acceptable, and except for hotels, fusible link hold-open devices acceptable. |
| C151 | 9.10.13.12. | Existing swings acceptable. |
| C152 | 9.10.13.13.(1) | In a building containing not more than four dwelling units, the existing heating or air conditioning system may be altered to serve more than one dwelling unit provided smoke alarms are installed in each dwelling unit and provided a smoke detector is installed in the supply or return air duct system serving the entire building which would turn off the fuel supply and electrical power to the heating system upon activation of such detector. |
| C153 | 9.10.13.13.(1) | In detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, existing acceptable. |
| C154 | 9.10.13.14.; 9.10.5.1. | In a building containing not more than four dwelling units, the existing heating or air conditioning system may be altered to serve more than one dwelling unit provided smoke alarms are installed in each dwelling unit and provided a smoke detector is installed in the supply or return air duct system serving the entire building which would turn off the fuel supply and electrical power to the heating system upon activation of such detector. |
| C155 | 9.10.5.1. | In detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, existing acceptable. |
| C156 | 9.10.14.1. | Existing windows |
|  |  | (a) Existing windows in walls may be relocated to another part of the wall, provided the existing opening is blocked up to provide the same fire rating for the wall, and the projection of the new opening, at a right angle to the property line onto another building, lies no closer than 300 mm from a window in such other building, where the “opposite” window is less than 2 400 mm from the opposite new opening, and |
|  |  | (b) except relocation of units, to be restricted to the same fire compartment and shall conform to the requirements of Articles 3.2.3.13. or 9.10.12.4. where applicable, or |
|  |  | (c) where a building does not satisfy the requirements of Subsection 3.2.3. for the amount of openings facing a yard or space that does not have sufficient limiting distance, such existing openings are allowed to be relocated provided: |
|  |  | (i) such openings are not increased in size and they are protected with wired glass in steel frames conforming to Sentence 3.1.8.14.(2), or |
|  |  | (ii) the building is sprinklered. |
| C157 | 9.10.14.7.; 9.10.14.8. | Where an addition to an existing residential building has its exposing building face further distant from the line than the existing exposing building face and the limiting distance is at least 1 200 mm, the total area of allowable unprotected openings may be determined under Article 9.10.14.8. for the combined new and existing exposing building faces, and |
|  |  | (a) where the existing exposing building face has no unprotected openings, or the existing unprotected openings are to be filled in, the total allowable area of unprotected openings may be installed in the new exposing building face, or |
|  |  | (b) where the existing unprotected openings are to remain, their area shall be deducted from the total allowable area of unprotected openings, and the balance may be installed in the new exposing building face, and |
|  |  | (c) Article 9.10.14.7. applies only to the new exposing building face. |
| C158 | 9.10.15.2.(1) | Where balloon framing is exposed during renovation, fire stopping shall be provided. |
| C159 | 9.10.17. | (a) Subject to approval by the chief building official, existing fire alarm system may remain where the Fire Safety Plan for the building addresses the intent of Subsection 3.2.4. (i.e. “stage” system, electrical supervision, detection as required, Fire Department connection, and emergency power supply), and |
|  |  | (b) extension of an existing system must ensure continuity and compatibility, and integrity of the system. |
| C160 | 9.10.19. | Existing access acceptable. |
| C161 | 9.10.18.3. | Smoke alarms may be battery operated. |
| C162 | 9.14.2.1.(2) | Existing acceptable. |
| C163 | 9.18.2. | Existing access acceptable. |
| C164 | 9.18.3. | Existing vents and ventilation acceptable. |
| C165 | 9.19. | Existing acceptable. |
| C166 | 9.20.2.2. | Used masonry may be reused for patching and filling openings to match adjacent work. Used interior brick may not be used for exterior applications. |
| C167 | 9.20.3. | Archaic mortars may be used to match existing jointing. |
| C168 | 9.20.4.1. | Sound jointing techniques may be employed to match existing archaic joints. |
| C169 | 9.20.12.1. | Corbelling may be constructed to match existing or original details, provided that it is structurally adequate for the proposed use. |
| C170 | 9.21. | Existing acceptable, provided the products of combustion are safely vented, and provided no fire hazard is created. |
| C171 | 9.22.1. to 9.22.7. | Sound period materials, designs and techniques may be employed in recreated fireplaces, provided no fire hazard is created. Article 9.22.1.4. need not comply. |
| C172 | 9.23. | Existing acceptable. |
| C173 | 9.24. | Existing acceptable. |
| C174 | 9.25. | (a) Where the framing systems are being altered to match the existing framing, lesser amounts and extent of insulation and vapour barrier will be permitted. A vapour barrier may consist of paint or other coating with specified perm rating such as two coats of leafing aluminum pigmented paint. |
|  |  | (b) Existing acceptable for Sentences 9.25.2.1.(5) to (7). |
|  |  | (c) Existing previously occupied log houses that are dismantled and reconstructed are exempt from Sentences 9.25.2.1.(13) and (14). |
| C175 | 9.26. | Existing acceptable, except when removing and replacing shingles, comply with the eave protection requirements of Subsection 9.26.5. |
| C176 | 9.27. | Existing acceptable. |
| C177 | 9.28. | All replacement or recreation of existing stucco may be compatible with the existing materials and application. |
| C178 | 9.29.4. | Existing acceptable. All replacement or recreation of existing plaster may be compatible with the existing materials and application. |
| C179 | 9.32. | In detached houses, semi-detached houses, townhouses and row houses containing not more than two dwelling units, rooms or spaces in dwelling units to be ventilated by natural means in accordance with Subsection 9.32.2. or by providing adequate mechanical ventilation. |
| C180 | 9.33.1.1. | In a building containing not more than four dwelling units, the existing heating or air conditioning system may be altered to serve more than one dwelling unit provided smoke alarms are installed in each dwelling unit and provided a smoke detector is installed in the supply or return air duct system serving the entire building which would turn off the fuel supply and electrical power to the heating system upon activation of such detectors. |
| C181 | 9.33.1.2. | Sound, used or antique appliances are acceptable, provided that: |
|  |  | (a) visual examination shows no excessive weakening by corrosion or other damage, |
|  |  | (b) no structural parts are missing, |
|  |  | (c) no cracks are present in the components intended to support the appliance or enclose the fire, and |
|  |  | (d) loading and ash removal door latches and hinges hold the door closed. |
| C181.1 | 9.33.4.3.(1) | Carbon monoxide detectors may be battery operated or plugged into an electrical outlet. |
| C182 | 9.34.4.1. | Existing meter mounting devices need not be relocated to these requirements during renovations. |
| C183 | 9.34.4.3. | Existing overhead and underground supply need not be relocated to these requirements during renovation. |
| C184 | 9.34.4.4.; 9.34.4.5. | Existing acceptable. |
| C185 | 9.37. | Sound used materials shall be acceptable for reuse, subject to the following limitations: |
|  |  | (a) visual examination shows no excessive weakening by holes, notches, nail splits or other damage, and |
|  |  | (b) logs have not been subjected to termite infestation. |
| Col. 1 | 2 | 3 |

Table 11.5.1.1.D/E.

Compliance Alternatives for Business/Mercantile Occupancies

Forming Part of Article 11.5.1.1.

| NUMBER | PART 3 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| DE1 | 3.1.4.6. | Existing heavy timber construction acceptable where construction is within 90% of member sizes listed in Part 3. |
| DE2 | 3.1.5.2.; 3.1.5.3.; 3.1.5.4.; 3.1.5.6. | Existing acceptable. |
| DE3 | 3.1.5.7.; 3.1.5.8.; 3.1.5.9.; 3.1.5.10. | Except for exposed foamed plastics, existing acceptable. To match existing, materials may be added from on or off site. |
| DE4 | 3.1.5.14.; 3.1.5.15.; 3.1.5.20.; 3.1.4.22. | Existing acceptable. |
| DE5 | 3.1.7.1. | Fire-resistance ratings may also be used where they are based on: |
|  |  | 1. HUD No. 8 Guideline on Fire Ratings of Archaic Materials and Assemblies. |
|  |  | 2. Fire Endurance of Protected Steel Columns and Beams, DBR Technical Paper No. 194. |
|  |  | 3. Fire Endurance of Unit Masonry Walls, DBR Technical Paper No. 207. |
|  |  | 4. Fire Endurance of Light-Framed and Miscellaneous Assemblies, DBR Technical Paper No. 222. |
| DE6 | 3.1.7.5.(3) | Existing assemblies required to be of noncombustible construction may be supported by combustible construction having at least the same fire-resistance rating as that supported. |
| DE7 | 3.1.8.1.(2); 3.1.8.6. | Existing functional closures are acceptable and may be relocated within the same existing fire separation. |
| DE8 | 3.1.8.5.(2) | (a) Existing functional and sound doors in existing buildings that are either hollow metal or kalamein and containing wired glass at least 6 mm thick and conforming to Sentence 3.1.8.14.(2) are permitted in lieu of doors not required to exceed 45 min, |
|  |  | (b) all existing functional and sound hollow doors which carry existing 1.5 h labels are acceptable in lieu of current 1.5 h labels and may contain wired glass panels not exceeding 0.0645 m2, at least 6 mm thick and conforming to Sentence 3.1.8.14.(2), and |
|  |  | (c) every fire door, window assembly or glass block used as a closure in a required fire separation shall be installed in conformance with good engineering practice. |
| DE9 | 3.1.8.7.; 3.1.8.9. | Fire dampers or fire stop flaps are not required to be installed in existing ducts at penetrations of existing fire separations. |
| DE10 | 3.1.8.10.(1) | For existing unlabelled doors in existing buildings, at least 45 mm solid core wood or metal clad are acceptable. |
| DE11 | 3.1.8.13. | Existing functionally operable latching devices, excluding draw bolts, are acceptable. |
| DE12 | 3.1.8.14. | Existing transoms or sidelights located in required fire separations may be retained if wired glass, at least 6 mm thick, is securely fixed to a wood frame of at least 50 mm thickness with steel stops. Operable transoms shall be fixed closed. |
| DE13 | 3.1.8.15.; 3.1.8.16.; 3.1.8.17. | Existing acceptable. |
| DE14 | 3.1.11. | Where the concealed space is being materially altered, smoke or heat detection in that space in lieu of firestops and tied into fire alarm system is acceptable. |
| DE15 | 3.2.2.17.(1)(b) and (c) | Existing sprinkler systems in 1 storey buildings need not comply. |
| DE16 | 3.2.3. | Existing windows |
|  |  | (a) Existing windows in walls may be relocated to another part of the wall, provided the existing opening is blocked up to provide the same fire rating for the wall, and the projection of the new opening, at a right angle to the property line onto another building, lies not closer than 300 mm from a window in such other building, where the “opposite” window is less than 2 400 mm from the opposite new opening, and |
|  |  | (b) Except relocation of units, shall be restricted to the same fire compartment and shall conform to the requirements of Articles 3.2.3.13. or 9.10.12.4. where applicable, or |
|  |  | (c) Where a building does not satisfy the requirements of Subsection 3.2.3. for the amount of openings facing a yard or space that does not have sufficient limiting distance, such existing openings are allowed to be relocated provided: |
|  |  | (i) such openings are not increased in size and they are protected with wired glass in steel frames conforming to Sentence 3.1.8.14.(2), or |
|  |  | (ii) the building is sprinklered. |
| DE17 | 3.2.4.1.(1)(d) | (a) Existing fire alarm system may remain except that Article 3.2.4.5. does not apply where the “Fire Safety Plan” (as described in Subsection 2.8.2. of the Ontario Fire Code) for the building addresses the intent of Subsection 3.2.4. (i.e. “stage” system, electrical supervision, detection as required, Fire Department connection, and emergency power supply), and |
|  |  | (b) Extension of an existing system must ensure continuity and compatibility, and integrity of the system. |
| DE18 | 3.2.5.1.; 3.2.5.2. | Existing acceptable. |
| DE19 | 3.2.5.3. | Existing access acceptable. |
| DE20 | 3.2.5.4.; 3.2.5.5.; 3.2.5.6. | Existing acceptable provided the building is sprinklered. |
| DE21 | 3.2.5.7. | Does not apply, except where a change in major occupancy occurs from a lesser hazard index. |
| DE22 | 3.2.5.13. | Existing sprinkler systems in existing buildings that do not conform to NFPA 13 may be altered, added to, or extended from the existing system without complying with NFPA 13, provided the system is operational and adequate with respect to coverage, water supply and controls, and provided the system is evaluated by a qualified designer. |
| DE23 | 3.2.6. Additional requirements for high buildings | Reserved |
| DE24 | 3.2.9. | Does not apply to buildings 6 storeys and less. Does not apply to sprinklered buildings. |
| DE25 | 3.3.1.5.(1)(c); Table 3.3.1.5. | In Column 2, maximum area of room or suite to be unlimited. |
| DE26 | 3.3.1.9.(1) | Existing width of public corridors of not less than 914 mm is acceptable. |
| DE27 | 3.3.1.10.; 3.3.1.11. | Existing door swings may remain in heritage buildings, existing or being restored, with no change in major occupancy and with occupant load no greater than 100. |
| DE28 | 3.3.1.12. | Existing doors acceptable, provided not less than 600 mm wide. |
| DE29 | 3.3.1.15. | Existing curved or spiral stairs acceptable. |
| DE30 | 3.3.1.16. | Existing non-conforming capacities of access to exits are acceptable, provided that: |
|  |  | (a) the increase in occupant load is not greater than 15%, |
|  |  | (b) the corridor fire separations are rated to Code, and |
|  |  | (c) early warning systems are provided, or |
|  |  | (d) there are sprinklers, plus smoke alarms in suites. |
| DE31 | 3.3.1.17. | Does not apply to heritage buildings. |
| DE32 | 3.3.1.18. | Existing stained, etched, bevelled, leaded or figured glass acceptable. |
| DE33 | 3.2.3.16. | Need not comply for “E” occupancy. |
| DE34 | 3.3.5.4.; 3.3.5.7.(3) | Need not comply where a gasketed door and self closer are provided in the existing fire separation. |
| DE35 | 3.4.1.4. | The following types of exits may also be used for buildings not over 6 storeys in building height: |
|  |  | (a) Connected balconies, which connect across firewalls, or connect to another exit, or with access to grade. |
|  |  | (b) Areas of refuge where fire service rescue is possible and that comply with Measure L of Sentences (4) to (10), (18), and 20(a), (b) and (d) in the Supplementary Guidelines. |
| DE36 | 3.4.1.8. | Existing stained, etched, bevelled, leaded or figured glass acceptable. |
| DE37 | 3.4.2.5.(1) | Existing travel distance acceptable where floor area is sprinklered. |
| DE38 | 3.4.3.1.(2) | Existing width of exits acceptable provided the occupant load in not more than 15% above the exit capacity. |
| DE39 | 3.4.3.5. | Existing acceptable. |
| DE40 | 3.4.3.6. | Existing headroom clearance of not less than 1 980 mm is acceptable. |
| DE41 | 3.4.4.1. | Fire separations of exits permitted in buildings: |
|  |  | — 30 min, up to 3 storeys in building height; |
|  |  | — 45 min, up to 6 storeys in building height; |
|  |  | — 1 h, over 6 storeys in building height. |
| DE42 | 3.4.4.4.(7) | Existing washrooms opening directly into exit stairwell shall be separated from exit stairwell by a 45 min closure. |
| DE43 | 3.4.5.1.(2) and (7) | Existing illuminated legible exit signs are acceptable. |
| DE44 | 3.4.6.1. | Existing acceptable. |
| DE45 | 3.4.6.2. | Existing acceptable, if visually apparent. |
| DE46 | 3.4.6.3.(1) and (2) | Existing acceptable with rise no greater than 3.7 m. |
| DE47 | 3.4.6.3.(3) and (4) | Existing acceptable. |
| DE48 | 3.4.6.4.(2) to (8) | Existing acceptable. |
| DE49 | 3.4.6.5.(1) to (5) | Existing acceptable. |
| DE50 | 3.4.6.6.(1) | Existing acceptable. |
| DE51 | 3.4.6.7.; 3.4.6.8. | Existing acceptable. |
| DE52 | 3.4.6.9.(2) to (6) | Existing acceptable. |
| DE53 | 3.4.6.10.(1) and (2) | Existing acceptable. |
| DE54 | 3.4.6.11. | Existing acceptable in public heritage buildings or a change in occupancy with no increase in occupant load. |
| DE55 | 3.4.6.12.; 3.4.6.13. | Existing acceptable. |
| DE56 | 3.4.6.15. | Existing functionally operable panic hardware acceptable. |
| DE57 | 3.4.7.2. | Combustible fire escapes which are protected from fire in accordance with Sentence 3.2.3.13.(2) are permitted or may be reconstructed or recreated (as in the case of a heritage building.) |
| DE58 | 3.5.1. | Existing acceptable except where building is classified under Subsection 3.2.6. |
| DE59 | 3.6.2.1.(5) | Existing fire separation of not less than 30 min is acceptable |
| DE60 | 3.6.2.3. | Existing acceptable where explosion-resistant construction or venting is provided. |
| DE61 | 3.6.2.7. | Existing acceptable. |
| DE62 | 3.6.2.8.(1) | 2 h fire separation acceptable. |
| DE63 | 3.6.3.1.(1) to (5) | 45 min fire separation acceptable up to 6 storeys. |
| DE64 | 3.6.3.3. | (a) Where 2 h fire separation is required, 1 h is acceptable. |
|  |  | (b) Where 1 h fire separation is required, 45 min is acceptable. |
|  |  | (c) Existing need not comply with Sentence 3.5.3.3.(5). |
| DE65 | 3.6.4.2. | Ceiling fire separation need not be fire-resistance rated where sprinklering, subject to C.A. DE24, of fire compartments on both sides of vertical fire separation is provided and where such fire separation is not required to exceed 1 h. |
| DE66 | 3.6.4.3.(1) | Existing to meet flame-spread rating of 25 or to be sprinklered. |
| DE67 | 3.6.4.4.; 3.6.4.5.; 3.6.4.6. | Existing access acceptable. |
| DE68 | 3.7.4.2. | Where the occupant load is increased by more than 15% above the capacity of the existing facilities, facilities to be added to accommodate the increase. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 4 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| DE69 | 4.1.9. | The requirements under this Subsection do not apply. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 6 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| DE70 | 6.2.3.2.; 6.2.3.5.; 6.2.3.6.; 6.2.3.12. | Existing acceptable. |
| DE71 | 6.2.3.17. | Existing openings, grilles and diffusers acceptable, subject to approval of chief building official. |
| DE72 | 6.2.4.2.(1); 6.2.4.5.(1) to (3) | Existing acceptable. |
| DE73 | 6.2.4.5.(10) | Where the duct system is being altered, lesser amounts and extent of insulation will be permitted. |
| DE74 | 6.2.9.2. | Existing acceptable. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 8 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| DE74.1 | 8.2.1.4. | Existing clearances acceptable where: a sewage system is replaced with another sewage system within the same class; and, the capacity of the replacement sewage system does not exceed the capacity of the existing sewage system. |
| DE74.2 | 8.2.1.4. | Existing clearances are acceptable where a replacement sewage system requires lesser clearances than those required in Part 8 for the existing sewage system. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 9 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| DE75 | 9.3.2.1. | Sound used lumber may be acceptable for reuse without a grade stamp provided that: |
|  |  | (a) visual examination shows no excessive weakening by holes, notches, nail splits or other damage, |
|  |  | (b) where the grade or species is unknown, the minimum grade shall apply for span table use, and |
|  |  | (c) lumber has not been subjected to termite infestation. |
| DE76 | 9.6.3.2. | Except where required in Article 9.9.2.7. existing acceptable, provided not less than 600 mm. |
| DE77 | 9.6.5. | Existing acceptable. |
| DE78 | 9.6.6.2.; 9.6.6.3. | Existing doors and sidelights being reused or relocated need not conform if identified or protected. |
| DE79 | 9.7.1.7. | Existing acceptable. |
| DE80 | 9.7.5. | Existing acceptable. |
| DE81 | 9.8.1. to 9.8.4. | Replacement or extension of existing stair systems shall be exempt from the provisions of these Articles, except that they shall have: |
|  |  | (a) a minimum width between wall faces of 700 mm, and |
|  |  | (b) a minimum clear height over tread nosing or landing of 1 800 mm. |
| DE82 | 9.8.2.2. | Existing acceptable. |
| DE83 | 9.8.5.2. | Existing curved or spiral stairs acceptable. |
| DE84 | 9.8.6. | Existing ramps acceptable, where practical. |
| DE85 | 9.8.7. | Existing handrails acceptable, unless considered unsafe by chief building official. |
| DE86 | 9.8.8. | Existing guards acceptable, unless considered unsafe by chief building official. |
| DE87 | 9.9.1.1. | Existing acceptable. |
| DE88 | 9.9.2.2. | The following types of exits may also be used: |
|  |  | (a) connected balconies, which connect across firewalls, or connect to another exit, or with access to grade, |
|  |  | (b) areas of refuge, approved by the chief building official, where fire service rescue is possible, or |
|  |  | (c) combustible or noncombustible exterior stairways or fire escapes which are protected in accordance with Sentence 3.2.3.12.(2). These may be reconstructed or recreated (as in the case of a heritage building). |
| DE89 | 9.9.2.6. | Existing acceptable, provided that the enclosure has a 45 min fire-resistance rating. |
| DE90 | 9.9.2.7. | Existing acceptable. |
| DE91 | 9.9.3.2. | Existing width of exits acceptable. |
| DE92 | 9.9.3.3. | Existing width of public corridors of not less than 965 mm is acceptable. |
| DE93 | 9.9.3.4. | Existing headroom clearance of not less than 1 950 mm is acceptable. |
| DE94 | 9.9.4.2. | 30 min fire separation acceptable. |
| DE95 | 9.9.5.4.; 9.9.5.5. | Existing acceptable. |
| DE96 | 9.9.5.8. | Existing acceptable provided minimum 45 min fire separation and where explosion-resistant construction or venting is provided. |
| DE97 | 9.9.6.2. | Existing acceptable. |
| DE98 | 9.9.6.3. | Existing headroom clearance of not less than 1 950 mm is acceptable, with existing door heights to be acceptable. |
| DE99 | 9.9.6.4. | Existing door widths and heights are acceptable, provided exit widths and heights comply with C.A.’s DE92 and DE93. |
| DE100 | 9.9.6.5. | Existing door swings are acceptable. Existing acceptable in public heritage buildings, where approved by chief building official. |
| DE101 | 9.9.6.6.(1) | Where exit doors open onto a landing, they shall not extend beyond the face of the first riser. |
| DE102 | 9.9.6.10. | Existing functionally operable passage or panic hardware acceptable. |
| DE103 | 9.9.7.3. | Maximum area of existing room or suite to be unlimited. |
| DE104 | 9.9.8.2.(1) | Existing travel distance acceptable where floor area is sprinklered and provided fire separations comply with Part 9 of the Code. |
| DE105 | 9.9.10.6. | Existing illuminated legible signs are acceptable for exit signs, if approved by chief building official. |
| DE106 | 9.10.1.1. | Assemblies required to be of noncombustible construction may be supported by combustible construction having at least the same fire-resistance rating as that supported. |
| DE107 | 9.10.1.3.(8) | Existing installations acceptable subject to C.A.’s DE22 and DE24. |
| DE108 | 9.10.3. | Fire-resistance ratings may also be used where they are based on: |
|  |  | 1. HUD No. 8 Guideline on Fire Ratings of Archaic Materials and Assemblies. |
|  |  | 2. Fire Endurance of Protected Steel Columns and Beams, DBR Technical Paper No. 194. |
|  |  | 3. Fire Endurance of Unit Masonry Walls, DBR Technical Paper No. 207. |
|  |  | 4. Fire Endurance of Light-Framed and Miscellaneous Assemblies, DBR Technical Paper No. 222. |
| DE109 | 9.10.5.1. | (a) Existing openings in existing wall or ceiling membranes to remain. |
|  |  | (b) Existing openings may be moved to another location in the same wall or ceiling, provided the aggregate area of openings does not increase and are not cumulative, and the existing opening is blocked up to provide the same rating as the existing wall or ceiling assembly. |
| DE110 | 9.10.6.2. | Existing heavy timber construction acceptable where construction is within 90% of the member sizes listed in Part 3. |
| DE111 | 9.10.7. | Existing acceptable for heritage buildings, subject to approval of chief building official. |
| DE112 | 9.10.8.1. | Existing 30 min rating acceptable. |
| DE113 | 9.10.8.2. | Existing sprinkler systems complying with C.A. DE24 and Sentence 3.2.2.17.(1) are acceptable. |
| DE114 | 9.10.8.3. | Existing acceptable, subject to approval of the chief building official. |
| DE115 | 9.10.8.7. | 30 min rating acceptable. |
| DE116 | 9.10.9.7.; 9.10.9.9. | Existing acceptable in existing fire separations. |
| DE117 | 9.10.9.10.(1) | Ceiling fire separation need not be fire-resistance rated where sprinklering of fire compartments on both sides of vertical fire separation is provided and where such fire separation is not required to exceed 1 h. |
| DE118 | 9.10.9.11.(2) | In lieu of the 2 h fire separation, sprinklers may be used in the mercantile occupancy with a 1 h fire separation. |
| DE119 | 9.10.9.13. | 30 min fire separation acceptable. |
| DE120 | 9.10.9.15.(1) | 30 min fire separation acceptable. |
| DE121 | 9.10.9.15.(3) | Need not comply for mercantile occupancy. |
| DE122 | 9.10.10.3.(1) | 45 min fire separation acceptable. |
| DE123 | 9.10.12.1. | Need not comply for mercantile occupancy. |
| DE124 | 9.10.13.1. | Existing functional closures are acceptable subject to C.A. DE8. |
| DE125 | 9.10.13.2. | Existing acceptable. |
| DE126 | 9.10.13.3. | Existing acceptable, provided that wood door frames are secured with hinge screws going through frame into the stud. |
| DE127 | 9.10.13.5. | Existing acceptable. Existing transoms or sidelights located in required fire separations may be retained if wired glass, at least 6 mm thick, is securely fixed to a wood frame of at least 50 mm thickness with steel stops. Operable transoms shall be fixed closed. |
| DE128 | 9.10.13.6. | Existing steel door frames acceptable. |
| DE129 | 9.10.13.7. | Existing glass block acceptable. |
| DE130 | 9.10.13.8. | Existing sizes acceptable. |
| DE131 | 9.10.13.9. | Existing operable latches acceptable. |
| DE132 | 9.10.13.10.(1) | Existing functionally operable self-closing device acceptable. |
| DE133 | 9.10.13.10.(2) | Existing functionally operable self-closing devices acceptable in “E” occupancy. |
| DE134 | 9.10.13.11. | Existing operable self-releasing electromagnetic and fusible link hold-open devices acceptable. |
| DE135 | 9.10.13.12. | Existing swings acceptable. |
| DE136 | 9.10.14.1. | Existing windows |
|  |  | (a) existing windows in walls may be relocated to another part of the wall, provided the existing opening is blocked up to provide the same fire rating for the wall, and the projection of the new opening, at a right angle to the property line onto another building, lies no closer than 300 mm from a window in such other building, where the “opposite” window is less than 2 400 mm from the opposite new opening, and |
|  |  | (b) except relocation of units, to be restricted to the same fire compartment and shall conform to the requirements of Articles 3.2.3.14. or 9.10.12.4. where applicable, or |
|  |  | (c) where a building does not satisfy the requirements of Subsection 3.2.3. for the amount of openings facing a yard or space that does not have sufficient limiting distance, such existing openings are allowed to be relocated provided: |
|  |  | (i) such openings are not increased in size and they are protected with wired glass in steel frames conforming to Sentence 3.1.8.14.(2), or |
|  |  | (ii) the building is sprinklered. |
| DE137 | 9.10.15.2.(1) | Where balloon framing is exposed during renovation, fire stopping shall be provided. |
| DE138 | 9.10.17. | (a) subject to approval by the chief building official, existing fire alarm system may remain where the Fire Safety Plan for the building addresses the intent of 3.2.4. (i.e. “stage” system, electrical supervision, detection as required, Fire Department connection, and emergency power supply), and |
|  |  | (b) extension of an existing system must ensure continuity and compatibility. |
| DE139 | 9.10.19. | Existing access acceptable. |
| DE140 | 9.18.2. | Existing access acceptable. |
| DE141 | 9.18.3. | Existing vents and ventilation acceptable. |
| DE142 | 9.19. | Existing acceptable. |
| DE143 | 9.20.2.2. | Used masonry may be reused for patching and filling openings to match adjacent work. Used interior brick may not be used for exterior applications. |
| DE144 | 9.20.3. | Archaic mortars may be used to match existing jointing. |
| DE145 | 9.20.4.1. | Sound jointing techniques may be employed to match existing archaic joints. |
| DE146 | 9.20.12.1. | Corbelling may be constructed to match existing or original details, provided that it is structurally adequate for the proposed use. |
| DE147 | 9.21. | Existing acceptable, provided the products of combustion are safely vented and provided no fire hazard is created. |
| DE148 | 9.22.1. to 9.22.7. | Sound period materials, designs and techniques may be employed in recreated fireplaces, provided no fire hazard is created. Existing need not comply with Article 9.22.1.4. |
| DE149 | 9.23. | Existing acceptable. |
| DE150 | 9.24. | Existing acceptable. |
| DE151 | 9.25.2.1.(5) to (7) | Existing acceptable. |
| DE152 | 9.26. | Existing acceptable, except when removing and replacing shingles, comply with eave protection requirements in Subsection 9.26.5. |
| DE153 | 9.27. | Existing acceptable. |
| DE154 | 9.28. | All replacement or recreation of existing stucco may be compatible with the existing materials and application. |
| DE155 | 9.29.4. | Existing acceptable. All replacement or recreation of existing plaster may be compatible with the existing materials and application. |
| DE156 | 9.33.1.2. | Sound, used or antique appliances are acceptable, provided that: |
|  |  | (a) visual examination shows no excessive weakening by corrosion or other damage, |
|  |  | (b) no structural parts are missing, |
|  |  | (c) no cracks are present in the components intended to support the appliance or enclose the fire, and |
|  |  | (d) loading and ash removal door latches and hinges hold the door closed. |
| DE157 | 9.34.4.1.; 9.34.4.3. | Existing meter mounting devices and overhead and underground supply need not be relocated to these requirements during renovations. |
| DE158 | 9.34.4.4.; 9.34.4.5. | Existing acceptable. |
| DE159 | 9.37. | Sound used materials shall be acceptable for reuse, subject to the following limitations: |
|  |  | (a) visual examination shows no excessive weakening by holes, notches, nail splits or other damage, and |
|  |  | (b) logs have not be subjected to termite infestation. |
| Col. 1 | 2 | 3 |

Table 11.5.1.1.F.

Compliance Alternatives for Industrial Occupancies

Forming Part of Article 11.5.1.1.

| NUMBER | PART 3 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| F1 | 3.1.4.6. | Existing heavy timber construction acceptable where construction is within 90% of member sizes listed in Part 3. |
| F2 | 3.1.5.2.; 3.1.5.3.; 3.1.5.4.; 3.1.5.6. | Existing acceptable. |
| F3 | 3.1.5.7.; 3.1.5.8.; 3.1.5.9.; 3.1.5.10. | Except for exposed foamed plastics, existing acceptable for “F2” and “F3” occupancies. To match existing, materials may be added from on or off site. |
| F4 | 3.1.5.14.; 3.1.5.15.; 3.1.5.16.; 3.1.5.20.; 3.1.5.22. | Existing acceptable. |
| F5 | 3.1.7.1. | Fire-resistance ratings may also be used where they are based on: |
|  |  | 1. HUD No. 8 Guideline on Fire Ratings of Archaic Materials and Assemblies. |
|  |  | 2. Fire Endurance of Protected Steel Columns and Beams, DBR Technical Paper No. 194. |
|  |  | 3. Fire Endurance of Unit Masonry Walls, DBR Technical Paper No. 207. |
|  |  | 4. Fire Endurance of Light-Framed and Miscellaneous Assemblies, DBR Technical Paper No. 222. |
| F6 | 3.1.7.5.(3) | Existing assemblies required to be of noncombustible construction may be supported by combustible construction having at least the same fire-resistance rating as that supported. |
| F7 | 3.1.8.1.(2); 3.1.8.6. | Existing functional closures are acceptable and may be relocated within the same fire separation. |
| F8 | 3.1.8.5.(2) | (a) existing functional and sound doors in existing buildings that are either hollow metal or kalamein and containing wired glass at least 6 mm thick and conforming to Sentence 3.1.8.14.(2) are permitted in lieu of doors not required to exceed 45 min, |
|  |  | (b) all existing functional and sound hollow metal or kalamein doors which carry existing 1.5 h labels are acceptable in lieu of current 1.5 h labels and may contain wired glass panels not exceeding 0.0645 m2, at least 6 mm thick and conforming to Sentence 3.1.8.14.(2), and |
|  |  | (c) every fire door, window assembly or glass block used as a closure in a required fire separation shall be installed in conformance with good engineering practice. |
| F9 | 3.1.8.7.; 3.1.8.9. | Fire dampers or fire stop flaps are not required to be installed in existing ducts at penetrations of existing fire separations. |
| F10 | 3.1.8.10.(1) | For existing unlabelled doors in existing buildings, at least 45 mm solid core wood or metal clad are acceptable. |
| F11 | 3.1.8.11.(1) | Existing functionally operable devices acceptable for “F2” and “F3” occupancies. |
| F12 | 3.1.8.13. | Existing functionally operable latching devices, excluding draw bolts, are acceptable. |
| F13 | 3.1.8.14. | Existing transoms or sidelights located in required fire separations may be retained if wired glass, at least 6 mm thick, is securely fixed to a wood frame of at least 50 mm thickness with steel stops. Operable transoms shall be fixed closed. |
| F14 | 3.1.8.15.; 3.1.5.16.; 3.1.8.17. | Existing acceptable. |
| F15 | 3.1.11. | Where the concealed space is being materially altered, smoke or heat detection in that space in lieu of firestops and tied into fire alarm system is acceptable. |
| F16 | 3.2.2.17.(1)(b) and (c) | Existing sprinkler systems in 1 storey buildings need not comply. |
| F17 | 3.2.3. | Existing need not comply with Article 3.2.3.17. For “F2” occupancy. Existing windows |
|  |  | (a) existing windows in walls may be relocated to another part of the wall, provided the existing opening is blocked up to provide the same fire rating for the wall, and the projection of the new opening, at a right angle to the property line onto another building, lies not closer than 300 mm from a window in such other building, where the “opposite” window is less than 2 400 mm from the opposite new opening, and |
|  |  | (b) except relocation of units, shall be restricted to the same fire compartment and shall conform to the requirements of Articles 3.2.3.13. or 9.10.12.4. where applicable, or |
|  |  | (c) where a building does not satisfy the requirements of Subsection 3.2.3. for the amount of openings facing a yard or space that does not have sufficient limiting distance, such existing openings are allowed to be relocated provided: |
|  |  | (i) such openings are not increased in size and they are protected with wired glass in steel frames conforming to Sentence 3.1.8.14.(2), or |
|  |  | (ii) the building is sprinklered. |
| F18 | 3.2.3.16. | Need not comply for “F2” occupancy. |
| F19 | 3.2.4. | (a) existing fire alarm system may remain except that Article 3.2.4.5. does not apply where the “Fire Safety Plan” (as described in Subsection 2.8.2. of the Ontario Fire Code) for the building addresses the intent of Subsection 3.2.4. (i.e. “stage” system, electrical supervision, detection as required, Fire Department connection, and emergency power supply), and |
|  |  | (b) extension of an existing system must ensure continuity and compatibility, and integrity of the system. |
| F20 | 3.2.5.1; 3.2.5.2. | Existing acceptable. |
| F21 | 3.2.5.3. | Existing access acceptable. |
| F22 | 3.2.5.4.; 3.2.5.5.;3.2.5.6. | Existing acceptable provided the building is sprinklered. |
| F23 | 3.2.5.7. | Does not apply, except where a change in major occupancy occurs from a lesser hazard index. |
| F24 | 3.2.5.13. | Existing sprinkler systems in existing buildings that do not conform to NFPA 13 may be altered, added to, or extended from the existing system without complying with NFPA 13, provided the system is operational and adequate with respect to coverage, water supply and controls, and provided the system is evaluated by a qualified designer. |
| F25 | 3.2.6. Additional requirements for high buildings. | Reserved |
| F26 | 3.2.9. | May not apply to buildings 6 storeys and less of “F2” and “F3” occupancies. Does not apply to sprinklered buildings. |
| F27 | 3.3.1.4.(1) | 30 min is acceptable to separate public corridors or exits in buildings not exceeding 6 storeys in building height, except that 45 min is required for exits in buildings exceeding 3 storeys in building height. Except for exits, no rating required where floor areas are sprinklered. |
| F28 | 3.3.1.5.(1)(c); Table 3.3.1.5. | For “F2” and “F3” occupancies in Column 2, maximum area of room or suite to be unlimited. |
| F29 | 3.3.1.9. | Existing width of public corridors of not less than 914 mm is acceptable. |
| F30 | 3.3.1.9.(13) and (14) | Need not comply where connected balcony or area of refuge is provided complying with C.A. F37. |
| F31 | 3.3.1.10.; 3.3.1.11. | Existing door swings may remain in heritage buildings, existing or being restored, with no change in major occupancy and with occupant load no greater than 100. |
| F32 | 3.3.1.12. | Existing doors acceptable, provided not less than 600 mm wide. |
| F33 | 3.3.1.15. | Existing curved or spiral staircase acceptable. |
| F34 | 3.3.1.18. | Existing stained, etched, bevelled, leaded or figured glass acceptable. |
| F35 | 3.3.5.4.(2), (3), and (5) | Existing acceptable. |
| F36 | 3.3.5.6.; 3.3.5.7. | Need not comply where a gasketed door and self closer are provided in the existing fire separation. |
| F37 | 3.4.1.4. | For “F2” and “F3” occupancies, the following types of exits may also be used for buildings not over 6 storeys in building height: |
|  |  | (a) connected balconies, which connect across firewalls, or connect to another exit, or with access to grade. |
|  |  | (b) areas of refuge where fire service rescue is possible and that comply with Measure L in Sentences (4) to (10) and (20)(a), (b) and (d) in the Supplementary Guidelines. |
| F38 | 3.4.1.8. | Existing stained, etched, bevelled, leaded or figured glass acceptable. |
| F39 | 3.4.2.5.(1) | For “F2” and “F3” occupancies, existing travel distance acceptable where the floor area is sprinklered. |
| F40 | 3.4.3.1.(2) | For “F2“ and “F3” existing width of exits acceptable provided the occupant load in not more than 15% above the exit capacity. |
| F41 | 3.4.3.5. | Existing acceptable. |
| F42 | 3.4.3.6. | Existing headroom clearance of not less than 1 980 mm is acceptable. |
| F43 | 3.4.4.1. | Fire separations of exits permitted in buildings: |
|  |  | — 30 min, up to 3 storeys in building height; |
|  |  | — 45 min, up to 6 storeys in building height; |
|  |  | — 1 h, over 6 storeys in building height. |
| F44 | 3.4.4.4.(7) | Existing washrooms opening directly into exit stairwell shall be separated from exit stairwell by 45 min closure. |
| F45 | 3.4.5.1.(2) and (7) | Existing illuminated legible exit signs are acceptable. |
| F46 | 3.4.6.1. | Existing acceptable. |
| F47 | 3.4.6.2. | Existing acceptable, if visually apparent. |
| F48 | 3.4.6.3.(1) and (2) | Existing acceptable with rise no greater than 3.7 m. |
| F49 | 3.4.6.3.(3) and (4) | Existing acceptable. |
| F50 | 3.4.6.4.(2) to (8) | Existing acceptable. |
| F51 | 3.4.6.5.(1) to (5) | Existing acceptable. |
| F52 | 3.4.6.6.(1) | Existing acceptable. |
| F53 | 3.4.6.7.; 3.4.6.8. | Existing acceptable. |
| F54 | 3.4.6.9.(2) to (6) | Existing acceptable. |
| F55 | 3.4.6.10.(1) and (2) | Existing acceptable. |
| F56 | 3.4.6.11. | For “F2“ and “F3” existing acceptable in public heritage buildings or a change in occupancy with no increase in occupant load. |
| F57 | 3.4.6.12.; 3.4.6.13. | Existing acceptable. |
| F58 | 3.4.6.15. | Existing functionally operable panic hardware acceptable. |
| F59 | 3.4.7.2. | Combustible fire escapes which are protected from fire in accordance with Sentence 3.2.3.13.(2) are permitted or may be reconstructed or recreated (as in the case of a heritage building). |
| F60 | 3.5.1. | Existing acceptable, except where building classified under Subsection 3.2.6. and except where existing elevators are “open” type. |
| F61 | 3.6.2.1.(5) | 45 min fire separation acceptable. |
| F62 | 3.6.2.3. | Existing acceptable where explosion-resistant construction or venting is provided. |
| F63 | 3.6.2.7. | Existing acceptable. |
| F64 | 3.6.2.8.(1) | 2 h fire separation acceptable. |
| F65 | 3.6.3.1.(1) to (5) | 45 min fire separation acceptable up to 6 storeys. |
| F66 | 3.6.3.3. | (a) where 2 h fire separation is required, 1 h is acceptable. |
|  |  | (b) where 1 h fire separation is required, 45 min is acceptable. |
|  |  | (c) existing need not comply with Sentences 3.5.3.3.(4) and (5). |
| F67 | 3.6.4.2. | Ceiling fire separation need not be fire-resistance rated where sprinklering, subject to C.A. F24, of fire compartments on both sides of vertical fire separation is provided and where such fire separation is not required to exceed 1 h. |
| F68 | 3.6.4.3.(1) | Existing to meet flame-spread rating of 25 or to be sprinklered. |
| F69 | 3.6.4.4.; 3.6.4.5.; 3.6.4.6. | Existing access acceptable. |
| F70 | 3.7.4.2. | Where the occupant load is increased by more than 15% above the capacity of the existing facilities, facilities to be added to accommodate the increase. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 4 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| F71 | 4.1.9. | The requirements under this Subsection do not apply. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 6 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| F72 | 6.2.2.3.(1), (3), and (4) | Storage garages with a total capacity of less than 20 motor vehicles need not have mechanical ventilating systems if the downward slope of the floor to the outside door is 1 in 120 and the garage floor is above outside ground level. |
| F73 | 6.2.3.2.; 6.2.3.5.; 6.2.3.6.; 6.2.3.12. | Existing acceptable for “F2” and “F3” occupancies. |
| F74 | 6.2.3.17. | Existing openings, grilles and diffusers acceptable. |
| F75 | 6.2.4.2.(1); 6.2.4.5.(1) to (3) | Existing acceptable. |
| F76 | 6.2.4.5.(10) | Where the duct system is being altered, lesser amounts and extent of insulation will be permitted. |
| F77 | 6.2.9.2. | Existing acceptable for “F2” and “F3” occupancies. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 8 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| F77.1 | 8.2.1.4. | Existing clearances acceptable where: a sewage system is replaced with another sewage system within the same class; and, the capacity of the replacement sewage system does not exceed the capacity of the existing sewage system. |
| F77.2 | 8.2.1.4. | Existing clearances are acceptable where a replacement sewage system requires lesser clearances than those required in Part 8 for the existing sewage system. |
| Col. 1 | 2 | 3 |

| NUMBER | PART 9 REQUIREMENTS | PART 11 COMPLIANCE ALTERNATIVE |
| --- | --- | --- |
| F78 | 9.3.2.1. | Sound used lumber may be acceptable for reuse without a grade stamp provided that: |
|  |  | (a) visual examination shows no excessive weakening by holes, notches, nail splits or other damage, |
|  |  | (b) where the grade or species is unknown, the minimum grade shall apply for span table use, and |
|  |  | (c) lumber has not been subjected to termite infestation. |
| F79 | 9.6.3.2. | Except where required in Article 9.9.2.7. existing acceptable, provided not less than 600 mm. |
| F80 | 9.6.5. | Existing acceptable. |
| F81 | 9.6.6.2.; 9.6.6.3. | Existing doors and sidelights being reused or relocated need not conform if identified or protected. |
| F82 | 9.7.1.7. | Existing acceptable. |
| F83 | 9.7.5. | Existing barriers acceptable. |
| F84 | 9.8.1. to 9.8.4. | Replacement or extension of existing stair systems shall be exempt from the provisions of these Articles, except that they shall have: |
|  |  | (a) a minimum width between wall faces of 700 mm, and |
|  |  | (b) a minimum clear height over tread nosing or landing of 1 800 mm. |
| F85 | 9.8.5.2. | Existing curved or spiral stairs acceptable. |
| F86 | 9.8.6. | Existing ramps acceptable, where practical. |
| F87 | 9.8.7. | Existing handrails acceptable, unless considered unsafe by chief building official. |
| F88 | 9.8.8. | Existing guards acceptable, unless considered unsafe by chief building official. |
| F89 | 9.8.9.5.(2) | Existing acceptable. |
| F90 | 9.9.1.1. | Existing acceptable. |
| F91 | 9.9.2.2. | The following types of exits may also be used: |
|  |  | (a) connected balconies, which connect across firewalls, or connect to another exit, or with access to grade, |
|  |  | (b) areas of refuge approved by the chief building official where fire service rescue is possible, or |
|  |  | (c) combustible or noncombustible exterior stairways or fire escapes which are protected in accordance with Sentence 3.2.3.13.(2). These may be reconstructed or recreated (as in the case of a heritage building). |
| F92 | 9.9.2.6. | Existing acceptable, provided that the enclosure has a 45 min fire-resistance rating. |
| F93 | 9.9.2.7. | Existing acceptable. |
| F94 | 9.9.3.2. | Existing width of exits acceptable. |
| F95 | 9.9.3.3. | Existing width of public corridors of not less than 965 mm is acceptable. |
| F96 | 9.9.3.4. | Existing headroom clearance of not less than 1 950 mm is acceptable. |
| F97 | 9.9.4.2.(1) | 30 min fire separation acceptable. |
| F98 | 9.9.5.4.; 9.9.6.2. | Existing acceptable. |
| F99 | 9.9.5.8. | Existing acceptable provided minimum 45 min fire separation and where explosion-resistant construction or venting is provided. |
| F100 | 9.9.6.3. | Existing headroom clearance of not less than 1 950 mm is acceptable, with existing door heights to be acceptable. |
| F101 | 9.9.6.4. | Existing door widths and heights are acceptable, provided exit widths and heights comply with C.A.’s F95 and F96. |
| F102 | 9.9.6.5. | Existing door swings acceptable. Existing acceptable in public heritage buildings, where approved by chief building official. |
| F103 | 9.9.6.6.(1) | Where exit doors open onto a landing, such doors shall not extend beyond the face of the first riser. |
| F104 | 9.9.6.10. | Existing functionally operable passage or panic hardware acceptable. |
| F105 | 9.9.7.3. | Maximum area of existing room or suite does not apply. |
| F106 | 9.9.8.2.(1) | Existing travel distance acceptable where floor area is sprinklered and provided fire separations comply with Part 9 of the Code. |
| F107 | 9.9.10.6. | Existing illuminated legible signs are acceptable for exit signs, if approved by chief building official. |
| F108 | 9.10.1.1. | Assemblies required to be of combustible construction may be supported by combustible construction having at least the same fire-resistance rating as that supported. |
| F109 | 9.10.1.3.(8) | Existing acceptable subject to C.A.’s F24 and F26. |
| F110 | 9.10.3. | Fire-resistance ratings may also be used where they are based on: |
|  |  | 1. HUD No. 8 Guideline on Fire Ratings of Archaic Materials and Assemblies. |
|  |  | 2. Fire Endurance of Protected Steel Columns and Beams, DBR Technical Paper No. 194. |
|  |  | 3. Fire Endurance of Unit Masonry Walls, DBR Technical Paper No. 207. |
|  |  | 4. Fire Endurance of Light-Framed and Miscellaneous Assemblies, DBR Technical Paper No. 222. |
| F111 | 9.10.5.1. | Existing openings in existing wall or ceiling membranes to remain. Existing openings may be moved to another location in the same wall or ceiling, provided the aggregate area of openings does not increase and are not cumulative, and the existing opening is blocked up to provide the same rating as the existing wall or ceiling assembly. |
| F112 | 9.10.6.2. | Existing heavy timber construction acceptable where construction is within 90% of the member sizes listed in Part 3. |
| F113 | 9.10.7. | Existing acceptable for heritage buildings, subject to approval of chief building official. |
| F114 | 9.10.8.1. | Existing 30 min rating acceptable. |
| F115 | 9.10.8.2. | Existing sprinkler systems complying with C.A. F24 and Sentence 3.2.2.17.(1) are acceptable. |
| F116 | 9.10.8.3. | Existing acceptable, subject to approval of chief building official. |
| F117 | 9.10.8.7. | 30 min rating acceptable. |
| F118 | 9.10.9.7.; 9.10.9.9. | Existing acceptable in existing fire separations. |
| F119 | 9.10.9.10.(1) | Ceiling fire separation need not be fire-resistance rated where sprinklering of fire compartments on both sides of vertical fire separation is provided and where such fire separation is not required to exceed 1 h. |
| F120 | 9.10.9.11.(2) | In lieu of the 2 h fire separation, sprinklers may be used in the medium hazard industrial occupancy with a 1 h fire separation. |
| F121 | 9.10.9.13.; 9.10.9.15.(1) | 30 min fire separation acceptable. |
| F122 | 9.10.10.3.(1) | 45 min fire separation acceptable. |
| F123 | 9.10.12.1. | Need not comply for medium hazard industrial occupancy. |
| F124 | 9.10.13.1. | Existing functional closures are acceptable subject to C.A. F8. |
| F125 | 9.10.13.2. | Existing acceptable. |
| F126 | 9.10.13.3. | Existing acceptable, provided that wood door frames are secured with hinge screws going through frame into the stud. |
| F127 | 9.10.13.5. | Existing wired glass acceptable. Existing transoms or sidelights located in required fire separations may be retained if wired glass, at least 6 mm thick, is securely fixed to a wood frame of at least 50 mm thickness with steel stops. Operable transoms shall be fixed closed. |
| F128 | 9.10.13.6. | Existing steel door frames acceptable. |
| F129 | 9.10.13.7. | Existing glass block acceptable. |
| F130 | 9.10.13.8. | Existing sizes acceptable. |
| F131 | 9.10.13.9. | Existing operable latches acceptable. |
| F132 | 9.10.13.10.(1) | Existing operable self-closing devices acceptable. |
| F133 | 9.10.13.11. | Existing operable self-releasing electromagnetic and fusible link hold-open devices acceptable. |
| F134 | 9.10.13.12. | Existing swings acceptable. |
| F135 | 9.10.14.1. | Existing windows |
|  |  | (a) existing windows in walls may be relocated to another part of the wall, provided the existing opening is blocked up to provide the same fire rating for the wall, and the projection of the new opening, at a right angle to the property line onto another building, lies no closer than 300 mm from a window in such other building, where the “opposite” window is less than 2 400 mm from the opposite new opening, and |
|  |  | (b) except relocation of units, to be restricted to the same fire compartment and shall conform to the requirements of Articles 3.2.3.13. or 9.10.12.4. where applicable, or |
|  |  | (c) where a building does not satisfy the requirements of Subsection 3.2.3. for the amount of openings facing a yard or space that does not have sufficient limiting distance, such existing openings are allowed to be relocated provided: |
|  |  | (i) such openings are not increased in size and they are protected with wired glass in steel frames conforming to Sentence 3.1.8.14.(2), or |
|  |  | (ii) the building is sprinklered. |
| F136 | 9.10.15.2.(1) | Where balloon framing is exposed during renovation, fire stopping shall be provided. |
| F137 | 9.10.17. | (a) subject to approval by the chief building official, existing fire alarm system may remain where the Fire Safety Plan for the building addresses the intent of Subsection 3.2.4. (i.e. “stage” system, electrical supervision, detection as required, Fire Department connection, and emergency power supply), and |
|  |  | (b) extension of an existing system must ensure continuity and compatibility, and integrity of the system. |
| F138 | 9.10.19. | Existing access acceptable. |
| F139 | 9.18.2. | Existing access acceptable. |
| F140 | 9.18.3. | Existing vents and ventilation acceptable. |
| F141 | 9.19.2.1. | Existing access acceptable. |
| F142 | 9.20.2.2. | Used masonry may be reused for patching and filling openings to match adjacent work. Used interior brick may not be used for exterior applications. |
| F143 | 9.20.3. | Archaic mortars may be used to match existing jointing. |
| F144 | 9.20.4.1. | Sound jointing techniques may be employed to match existing archaic joints. |
| F145 | 9.20.12.1. | Corbelling may be constructed to match existing or original details, provided that it is structurally adequate for the proposed use. |
| F146 | 9.21. | Existing acceptable, provided the products of combustion are safely vented and provided no fire hazard is created. |
| F147 | 9.22.1. to 9.22.7. | Sound period materials, designs and techniques may be employed in recreated fireplaces provided no fire hazard is created. Existing need not comply with Article 9.22.1.4. |
| F148 | 9.23. | Existing acceptable. |
| F149 | 9.24. | Existing acceptable. |
| F150 | 9.25.2.1.(5) to (7) | Existing acceptable. |
| F151 | 9.26. | Existing acceptable. |
| F152 | 9.27. | Existing acceptable. |
| F153 | 9.28. | All replacement or recreation of existing stucco may be compatible with the existing materials and application. |
| F154 | 9.29.4. | Existing acceptable. All replacement or recreation of existing plaster may be compatible with the existing materials and application. |
| F155 | 9.33.1.2. | Sound, used or antique appliances are acceptable, provided that: |
|  |  | (a) visual examination shows no excessive weakening by corrosion or other damage, |
|  |  | (b) no structural parts are missing, |
|  |  | (c) no cracks are present in the components intended to support the appliance or enclose the fire, and |
|  |  | (d) loading and ash removal door latches and hinges hold the door closed. |
| F156 | 9.34.4.1.; 9.34.4.3. | Existing meter mounting devices and overhead and underground supply need not be relocated to these requirements during renovations. |
| F157 | 9.34.4.4.; 9.34.4.5. | Existing acceptable. |
| F158 | 9.37. | Sound used materials shall be acceptable for reuse, subject to the following limitations: |
|  |  | (a) visual examination shows no excessive weakening by holes, notches, nail splits or other damage, and |
|  |  | (b) logs have not been subjected to termite infestation. |
| Col. 1 | 2 | 3 |

O. Reg. 403/97, Part 11: O. Reg. 22/98, ss. 33-36; O. Reg. 278/99, s. 27; O. Reg. 205/00, ss. 7-9; O. Reg. 283/01, s. 6.

Part 12
Transition, Revocation and Commencement

| Section | 12.1. | Transition Rule |
| --- | --- | --- |
|  | 12.1.1. | Transition Rule |
|  | 12.1.2. | Sewage Systems, Transition Rules |
|  | 12.1.3. | Transition, July 2001 |
|  | 12.1.4. | Transition, August 2002 |
|  | 12.1.5. | Transition, September 2004 |

Part 12
Transition, Revocation and Commencement

Section 12.1. Transition Rule

12.1.1. Transition Rule

12.1.1.1.  Continuation of Regulation 61 of R.R.O. 1990

(1)  Notwithstanding the revocation of Regulation 61 of the Revised Regulations of Ontario, 1990, that Regulation continues in force in respect of construction

(a)	for which a permit has been issued before April 6, 1998, or

(b)	for which the working drawings, plans and specifications are substantially completed before April 6 , 1998, and for which an application for a permit under Regulation 61 of the Revised Regulations of Ontario, 1990 is made before July 6, 1998

on condition that the construction is commenced within six months after the permit is issued.

12.1.2. Sewage Systems, Transition Rules

12.1.2.1.  Construction of Sewage Systems

(1)  Sections 74 to 79, 81, 82.1, 83 and 176 (6) of the Environmental Protection Act, as they read on April 5, 1998, continue to apply in respect of construction of a sewage system

(a)	for which a certificate of approval was issued under section 77 of the Environmental Protection Act before April 6, 1998, and

(b)	for which a permit under section 78 of the Environmental Protection Act was not issued before April 6, 1998

provided the construction of the sewage system has commenced by October 5, 1998.

(2)  Where an agreement under clause 4(1)(j) or section 81 of the Environmental Protection Act was in force on April 5, 1998 and a certificate of approval for a sewage system referred to in clause (1)(a) was issued by the party administering Part VIII of the Environmental Protection Act under the agreement, the agreement shall continue in force, and shall not be terminated, until such time as a permit under section 78 of the Environmental Protection Act is issued in respect of the sewage system.

12.1.2.2.  Orders

(1)  Where an order issued under section 79 of the Environmental Protection Act has not been complied with before April 6, 1998, sections 74 to 79, 81, 82.1, 83 and 176(6) of the Environmental Protection Act, as they read on April 5, 1998, continue to apply to the sewage system until the order has been complied with.

(2)  Where an agreement under clause 4(1)(j) or section 81 of the Environmental Protection Act was in force on April 5, 1998 and an order referred to in Sentence (1) was issued by the party administering Part VIII of the Environmental Protection Act under the agreement, the agreement shall continue in force according to its terms, and shall not be terminated, until such time as the order referred to in Sentence (1) has been complied with.

12.1.2.3.  Appeals

(1)  Where an appeal has been made under section 139 of the Environmental Protection Act to the Environmental Appeal Board before April 6, 1998 in respect of a decision of a director made under Part VIII of that Act, that Act, as it read on April 5, 1998, continues to apply in respect of all proceedings related to the appeal.

(2)  Where an agreement under clause 4(1)(j) or section 81 of the Environmental Protection Act was in force on April 5, 1998 and the party administering Part VIII of the Environmental Protection Act under the agreement is a party to an appeal referred to in sentence (1), the agreement shall continue in force according to its terms, and shall not be terminated, until such time as the appeal referred to in Sentence (1) has been determined.

12.1.2.4.  Records

(1)  In this Article

Enforcement entity means the municipality, county, board of health, conservation authority or Ontario, as the case may be, that has responsibility under sections 3 or 3.1 of the Act or, where an agreement under sections 3, 5 or 32.1 of the Act is in place under such agreement, for the enforcement of the provisions of the Act or this Code related to sewage systems.

(2)  The Ministry of the Environment or, if an agreement under clause 4(1)(j) or section 81 of the Environmental Protection Act was in force on April 5, 1998, the party that was administering Part VIII of the Environmental Protection Act under the agreement, shall

(a)	keep all records in their possession or under their control with respect to sewage systems for a period of six years or as otherwise directed by the director,

(b)	on the written request of the chief building official of the enforcement entity, deliver to the enforcement entity a certified copy of a record relating to Part VIII of the Environmental Protection Act with respect to sewage systems as specified in the request,

(c)	on the written request of the chief building official of the enforcement entity, deliver to the enforcement entity a certificate as to the service of any document relating to Part VIII of the Environmental Protection Act with respect to sewage systems as specified in the request,

(d)	on the written request of the chief building official of the enforcement entity, deliver to the enforcement entity, a certificate as to the custody of any document relating to Part VIII of the Environmental Protection Act with respect to sewage systems as specified in the request, and

(e)	on the written request of the chief building official of the enforcement entity, deliver to the enforcement entity, a certificate as to whether or not any document relating to Part VIII of the Environmental Protection Act with respect to sewage systems as specified in the request was received or issued.

(3)  Section 37 of the Act applies to

(a)	a direction or order or a certified copy of a direction or order delivered under Clause (2)(b) or (c) that is or relates to a direction or order under Part VIII of the Environmental Protection Act, and

(b)	a statement as to any matter of record in the office of an enforcement entity concerning the enforcement of Part VIII of the Environmental Protection Act that was delivered to the enforcement entity under clauses 2(b) or (c), or a certificate that was delivered to the enforcement entity under clauses (2)(d) or (e).

(4)  If an agreement under clause 4(1)(j) or section 81 of the Environmental Protection Act was in force on April 5, 1998 and the party that was administering Part VIII of the Environmental Protection Act under the agreement is an enforcement entity, then directions, orders or statements as to any matter of record in the office of the enforcement entity relating to the enforcement of Part VIII of the Environmental Protection Act with respect to sewage systems shall be deemed to have been made under this Act for the purposes of section 37 of the Act.

12.1.3. Transition, July 2001

12.1.3.1.  Transition Rule

(1)  Subject to Sentence (2), this Code as it reads on August 5, 2001 is deemed to continue in force with respect to construction

(a)	for which a permit is issued before August 6, 2001, or

(b)	for which the working drawings, plans and specifications are substantially completed before August 6, 2001 and for which an application for a permit is made before November 5, 2001 under this Code as it reads on August 5, 2001.

(2)  Sentence (1) does not apply unless the construction is commenced within six months after the permit is issued.

12.1.4.  Transition August, 2002

12.1.4.1.  Transitional Rule

(1)  Subject to Sentence (2), the row of Table 2.6.3.2. that refers to Document CAN/CSA B66-M90, “Prefabricated Septic Tanks and Sewage Holding Tanks”, and Articles 8.2.2.2. and 8.2.2.3. as they read on August 3, 2002 shall be deemed to continue in force with respect to construction

(a)	for which a permit is issued before August 4, 2002, or

(b)	for which the working drawings, plans and specifications are substantially completed before August 4, 2002, and for which an application for a permit is made before November 3, 2002.

(2)  Sentence (1) does not apply unless the construction is commenced within six months after the permit is issued.

(3)  The row of Table 2.6.3.2. that refers to Document CSA B66-00, “Prefabricated Septic Tanks and Sewage Holding Tanks”, does not apply to construction to which Sentence (1) applies.

12.1.5.  Transition, September 2004

12.1.5.1.  Transitional Rule

(1)  Subject to Sentence (2), this Code as it reads on August 31, 2004 is deemed to continue in force with respect to construction

(a)	for which a permit is issued before September 1, 2004, or

(b)	for which the working drawings, plans and specifications are substantially completed before September 1, 2004 and for which an application for a permit is made before December 1, 2004 under this Code as it reads on August 31, 2004.

(2)  Sentence (1) does not apply unless the construction is commenced within six months after the permit is issued.

12.2.  Omitted (revokes other Regulations).

12.3.  Omitted (provides for coming into force of provisions of this Regulation).

O. Reg. 403/97, Part 12; O. Reg. 22/98, ss. 37, 38; O. Reg. 283/01, s. 7; O. Reg. 220/02, ss. 12-14; O. Reg. 23/04, s. 6.

Back to top